## Project Structure
METLIFE GULF RISE BLDG 4
89 Symes Drive Red Beach, Auckland, 0932
QA
Level 1 (basement) QA
Underslab drainage
|  |  | Checklist |  |  |  | Underslab Checklist
Waste & Stacks
|  |  | Checklist |  |  |  | Common Waste & Stack QA Check
Main Cold Water Reticulation
Cold Water
|  |  |  | Checklist |  |  | Main Cold Water QA Checklist
Hot Water
|  |  |  | Checklist |  |  | Hot Water Main Checklist
Sump Pump
|  |  | Checklist |  |  |  | Waste Pump Checklist
|  | Apartment #'sB4 101 | Checklist | First Fix
Waste
[6 empty] | Checklist | Apartment Waste QA Checklist
Water
[6 empty] | Checklist | Apartment Waste QA Checklist
Second Fix
[6 empty] | Checklist | Apartment Waste QA Checklist
Hot Water Plant
|  |  | HOT WATER PLANT QA_TEST |  |  |  | HOT WATER PLANT QA_TEST
Level 2 (Ground) QA
Waste & Stacks
|  |  | Checklist |  |  |  | Common Waste & Stack QA Check
Main Water Reticulation
Cold Water
|  |  |  | Checklist |  |  | Main Cold Water QA Checklist
Hot Water
|  |  |  | Checklist |  |  | Hot Water Main Checklist
Apartments
Apartment #'sB4 201 to B4 211
First Fix
Waste
[6 empty] | Checklist | Apartment Waste QA Checklist
Water
[6 empty] | Checklist | Apartment Waste QA Checklist
Second Fix
[6 empty] | Checklist | Apartment Waste QA Checklist
Level 3 QA
Waste & Stacks
|  |  | Checklist |  |  |  | Common Waste & Stack QA Check
Main Water Reticulation
Cold Water
|  |  |  | Checklist |  |  | Main Cold Water QA Checklist
Hot Water
|  |  |  | Checklist |  |  | Hot Water Main Checklist
Apartments
Apartment #'sB4 301 to B4 311
First Fix
Waste
[6 empty] | Checklist | Apartment Waste QA Checklist
Water
[6 empty] | Checklist | Apartment Waste QA Checklist
Second Fix
[6 empty] | Checklist | Apartment Waste QA Checklist
Level 4 QA
Waste & Stacks
|  |  | Checklist |  |  |  | Common Waste & Stack QA Check
Main Water Reticulation
Cold Water
|  |  |  | Checklist |  |  | Main Cold Water QA Checklist
Hot Water
|  |  |  | Checklist |  |  | Hot Water Main Checklist
Apartments
Apartment #'sB4 401 to B4 411
First Fix
Waste
[6 empty] | Checklist | Apartment Waste QA Checklist
Water
[6 empty] | Checklist | Apartment Waste QA Checklist
Second Fix
[6 empty] | Checklist | Apartment Waste QA Checklist
TESTING & COMMISSIONING
Level 1 (basement) TEST
Underslab drainage
Test Sheet
Waste & Stacks
Test Sheet
Main Cold Water Reticulation
Cold Water Test Sheet
Hot Water Test Sheet
Sump Pump
Checklist
|  | Apartment #'sB4 101 | Apartment Water Test Sheet
Hot Water Plant
HOT WATER PLANT QA_TEST
Level 2 (Ground) TEST
Waste & Stacks
Test Sheet
Main Cold Water Reticulation
Cold Water Test Sheet
Hot Water Test Sheet
Apartments
Apartment #'sB4 201 to B4 211
Apartment Waste Test Sheet
Apartment Water Test Sheet
Level 3 TEST
Waste & Stacks
Test Sheet
Main Cold Water Reticulation
Cold Water Test Sheet
Hot Water Test Sheet
Apartments
Apartment #'sB4 301 to B4 311
Apartment Waste Test Sheet
Apartment Water Test Sheet
Level 4 TEST
Waste & Stacks
Test Sheet
Main Cold Water Reticulation
Cold Water Test Sheet
Hot Water Test Sheet
Apartments
Apartment #'sB4 401 to B4 411
Apartment Waste Test Sheet
Apartment Water Test Sheet

## Underslab Checklist
checklist | QA - Basement Underslab | COMENT
section | Area Prestart / Acceptance & Drawings
Text | Zone / Area
checkpoint | Area ready for works (grids setout, area accessible and approval to start)
checkpoint | Current Dimensioned Slab Set Out Drawings numbers and revisions recorded
section | Under Slab Pipe install
checkpoint | Correct pipe laid to specified level and grade (all joints sealed correctly as specified)
text | Start Invert
text | Finish Invert
text | Grade of Pre-Line %
text | Product Type
checkpoint | Pipe supported
checkpoint | Install Tests completed, reviewed & approved
text | Test method used
text | Duration
checkpoint | Local Authority Inspection Passed
text | Witnessed by
SIGN BOX
Text | Representing (Company)
text | Date
checkpoint | All relevant test plugs removed where applicable
checkpoint | Open ends sealed
checkpoint | General photos, comments and observations
checkpoint | Pipe Laying Completed
Text | Laid by
bool | Bedding Sound
bool | Soil Removed
bool | Trench Compacted
bool | Hard Filled
section | Area Completion/Signoff
checkpoint | Specified Protection Around All feeds/pipes penetrating slab
checkpoint | All Measurements Double Checked
checkpoint | As-Built Drawings recorded (drawing & revision number(s)
checkpoint | All relevant under slab works completed, reviewed and approved
text | Completion Date

## Common Waste & Stacks QA Check
checklist | QA - Waste / Stacks | COMENT
section | Area Prestart / Acceptance & Drawings
Text | Zone / Area
checkpoint | Area ready for works
checkpoint | Current Dimensioned Slab Set Out Drawings numbers and revisions recorded
section | Pipe install
checkpoint | IE's - Test points installed corrrect locations (ASNZS 3500)
checkpoint | Pipeout completed
Check point | Correct labels
Checkpoint | Acoustic lagging
text | Product Type
checkpoint | Correct Pipe supports completed
checkpoint | Seismic bracing completed
checkpoint | Vent installed
checkpoint | Correct fall
checkpoint | Flood Test in accordance with ASNZ 3500
text | Witnessed by
SIGN BOX
Text | Representing (Company)
text | Date
checkpoint | All relevant test plugs removed where applicable
checkpoint | Open ends sealed
checkpoint | General photos, comments and observations
checkpoint | Pipe Install Completed
Text | Installed by
section | Area Completion/Signoff
checkpoint | Specified Protection Around All feeds/pipes penetrating slab
checkpoint | All Measurements Double Checked
checkpoint | As-Built Drawings recorded (drawing & revision number(s)
text | Completion Date
Pass,Fail,Partial Pass,N/A
Remove to waste
Remove to waste

## Hot Water Main Checklist
Checklist
checkpoint | Connections welded/crimped correctly
checkpoint | Clip spacing to manufacturer's specs horizontal/ vertical
checkpoint | Lagging installed and neat
checkpoint | Labels installed
checkpoint | Correct valves fitted correctly
checkpoint | Tested

## Main Cold Water QA Checklist
Checklist
checkpoint | Connections welded/crimped correctly
checkpoint | Clip spacing to manufacturer's specs horizontal/ vertical
checkpoint | Lagging installed and neat
checkpoint | Labels installed
checkpoint | Correct valves in correct locations
checkpoint | Tested
Photo&Notes | Add drawing - Highlight completed section. Include channges for As-Builts

## Apartment Water Checklist
Section | Water Supply | Preload apartment #'s
checkpoint | Pipe Work Secured in ceiling
checkpoint | Pipe Work Secured in wall
checkpoint | Pipe Work Siliconed
checkpoint | Check for Cross Overs
checkpoint | Pressure Test 1500 KPA or product/job spec
checkpoint | Visual check & photos attached
checkpoint | Check all joints
Photo | Shower/bath outlet Crimp | Must include photo to pass
Section | Pre-line Inspection
Checkpoint | Nogs in correct Location
Checkpoint | Cylinder siesmic nogs in place
checkpoint | Vanity, shower, toilet nogs
Checkpoint | Shower mixer - Depths allowance for tiles, nogs square to wall
Checkpoint | Mixers straight
checkpoint | Vanity Wingbacks
Checkpoint | Outlets straight
Checkpoint | Outlets correct length
checkpoint | HWC water feeds
checkpoint | Capped Off
checkpoint | Rubbish removed
checkpoint | Protective covers in place
label | Attach photos of completed area
checkpoint | Pre Line Inspection Passed - Foreman
holdpoint | Add Signature
checkpoint | Pre Line Inspection Passed - Witness
holdpoint | Add Signature

## Apartment Waste QA Checklist
Section |  | Preload apartment #'s
checklist | First Fix - P.V.C
checkpoint | Waste Pipeout complete
checkpoint | Vent installed
checkpoint | Correct Fall
checkpoint | Correct Clipping
checkpoint | Flood Test in accordance with ASNZ 3500
checkpoint | Hydrostatic test Plug Removed
checkpoint | Inspection Cover Replaced
checkpoint | All pipe stubs & FWG's covered
checkpoint | Visual check & photos attached
label | Attach photos of completed area
checkpoint | Pre Line Inspection Passed - Foreman
holdpoint | Add Signature
checkpoint | Pre Line Inspection Passed - Witness
holdpoint | Add Signature
Photo&Notes | Add drawing - Highlight completed section. Include channges for As-Builts

## Apartment Waste Test Sheet
Checklist | Testing - Waste / Stacks
Text | Area / Stack
checkpoint | Flood Test in accordance with ASNZ 3500 (15.2)
text | Duration
text | Notes
checkpoint | Install Tests completed, reviewed & approved
checkpoint | Local Authority Inspection Passed
text | Witnessed by
Text | Representing (Company)
Signing box
text | Date

## Apartment Water Test Sheet
checklist | Apartment Water Test Sheet
checkpoint | Connections welded/crimped correctly
checkpoint | Clip Spacing to manufacturer's specs horizontal/ vertical
checkpoint | Valves fitted correctly
checkpoint | Checked for crossovers
checkpoint | Lagging installed and neat
checkpoint | Tidy work areas
checkpoint | Pressure 1500 kpa or as per spec
text | Duration
checkpoint | Visual check (for leeks form valves, tees, saddles, etc)
label | Attach photos of completed area
checkpoint | Pre Line Inspection Passed - Foreman
holdpoint | Add Signature
checkpoint | Pre Line Inspection Passed - Inspector
holdpoint | Add Signature

## Pump Test Sheet
Waste Water Pump Commissioning
name | Pump Model Matches Spec
checklist | Waste Water Pump Commissioning
Checkpoint | Chain connected and secure
Checkpoint | Float Valve operating free of obstruction
checkpoint | Flow test pump
checkpoint | Visual check for leaks
checkpoint | Non return valves fitted
checkpoint | Installers name & date works completed
text | Installers name
text | Date:
checkpoint | Tested by & date
text | Tested by:
text | Date tested:
checkpoint | Council inspector sign off and date

## Apartment 2nd Fix QA Checklist
type | name
checklist | Second Fix Plumbing - Water & Waste
checkpoint | Flush all water pipes before connecting fittings
checkpoint | Correct Taps And Fittings Provided
checkpoint | Silicone Applied To Fixtures Where Required
checkpoint | Check All Tap Connectors For Leaks
checkpoint | Check Screwed Nippling In Walls For Leaks
checkpoint | Check Traps For Leaks
checkpoint | Check Cisterns For Leaks
checkpoint | Check cisterns flushing correctly
checkpoint | Check All Fixtures Function Correctly
checkpoint | Test TPR on HWC and safetray drains away & airgap
checkpoint | Check HWC For Correct Valve Installation
checkpoint | Check Restraints & Timber chooks are installed on HWC
checkpoint | Element Position on HWC Is In A Serviceable Position
checkpoint | Check FWG & Shower wastes are clean & clear
checkpoint | Check Flanges Have Been Installed Where Required
checkpoint | Check All Soll Pipe Connections Are Connected To Drain
checkpoint | Kitchen overflow working and no leaks
checkpoint | Picked Up All Left Over Material & Retumed to Office
checkpoint | All your rubbish removed or in bins provided
checkpoint | Check All Hot/Cold Pipes For Correct Position
checkpoint | Temperature set point
checkpoint | Downpipe & overflow cover installed on balcony
checkpoint | Correct screws on balcony drain
checkpoint | Installers name & date works completed
text | Installers name
text | Date:
checkpoint | Tested by & date
text | Tested by:
text | Date tested:
checkpoint | Council inspector sign off and date

## HOT WATER PLANT QA_TEST
checklist | HOT WATER PLANT
checkpoint | Installation – refer to installation check list for hot and cold water.
checkpoint | Testing – Pressure tested to1500kpa or 1.5 times working pressure whichever is greater.
checkpoint | Temp relief points ran to tundishes.
checkpoint | Temperature probe from control box installed into storage tanks.
checkpoint | Check that an adequate water supply is available to the hot water system.
checkpoint | Water supply pressure shall not exceed the maximum pressure stated by manufacturer.
checkpoint | Open cold water inlet valve, hot water outlet valve
checkpoint | Exercise all valves and ensure correct operation. Ensure all valves are in open position prior turning power on.
checkpoint | Check the system is fully charged & all air is bled from the system & no leaks are evident
checkpoint | Ensure hot water heaters and storage tanks are full of water and all valves are open.
checkpoint | Ensure pressures are not greater then 750Kpa to the heaters or storage tanks.
checkpoint | Open all individual gas isolation valves & purge gas lines.
checkpoint | Test gas pipe work for leaks.
checkpoint | Check the gas supply pressure at the inlet to the water heater with the water heater and all
checkpoint | other burning appliances in the premises operating. The minimum gas supply pressure
checkpoint | range is NG: 1.13Kpa - 3.5Kpa & LPG: 2.75Kpa - 3.5Kpa
checkpoint | Clean filters and strainers once after 4 hours of use.
checkpoint | Set temperature to 65 degrees.
checkpoint | For further detailed applications refer to owners/installation manual from manufacturer