## res
type | name | values | prefix | postfix | usage count | user addable | template name
checklist | NEL-CNT-SDC-2990-PQA-ITP-0042 Rev 0 - Conduits (Trenching and Install) | itp |  |  |  |  | NEL-CNT-SDC-2990-PQA-ITP-0042 Rev 0 - Conduits (Trenching and Install)
section | 1.0 Preliminaries (Include all aspects of Materials, Approvals, IFC Drawings, etc. Ensure all required permits have been raised prior to commencing works)
checkpoint | 1.1 - IFC Drawings issued
label | Resp. Person - PE
label | Specification Reference - IFC Drawing Number: PSDR Part 6 Section 2(h)
label | Acceptance Criteria - IFC Drawings, approved plans, technical specification issued for construction
label | • Construction of any Construction Package must not commence until at least 5 Business days after the later of when:
label | i). the Construction Documentation has been submitted to the State, the IREA and any Returned Asset Owner (if applicable) in accordance with section 2(f) and
label | ii). Any requirements of the IREA under section 2(g) have been complied with.
label | Test Method - V
label | Test Frequency - PW
label | Inspection/Verification (Name, signature & date): Sub-Contractor - NR
label | Inspection/Verification (Name, signature & date): Spark NEL Engineer - HP
label | Inspection/Verification (Name, signature & date): Nominated Authority - NR
label | Inspection/Verification (Name, signature & date): IREA - NR
label | Records/Documents - IFC Drawings
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 1.2 - Survey Set Out
label | Resp. Person - PE
label | Specification Reference - QMP IFC Drawings
label | Acceptance Criteria - Confirmation and visually inspect survey set out as per the IFC Drawing
label | Test Method - V
label | Test Frequency - PW
label | Inspection/Verification (Name, signature & date): Sub-Contractor - HP
label | Inspection/Verification (Name, signature & date): Spark NEL Engineer - HP
label | Inspection/Verification (Name, signature & date): Nominated Authority - NR
label | Inspection/Verification (Name, signature & date): IREA - NR
label | Records/Documents -
textbox | • InEight Document References:
label | • Lot Map
holdpoint | AUTHORITY HOLDPOINT
section | 2.0 Operations (Include Work Execution – Installation / Manufacturing Process step-by-step)
checkpoint | 2.1 - Material Conformance - Pits and Lids
label | Resp. Person - SE
label | Specification Reference - VR 733.07 IFC drawings, VicRoads TC-1220 PSDR Section 14
label | Acceptance Criteria - Pits and Lids are correct type & approved notations.
label | • Where the conduits enter the cable pit, a neat hole shall be cut in the pit using a hole cutter or similar tools. Pits with holes knocked in with a hammer or similar tool will be rejected.
label | • The conduit shall be sealed to the box with silicone sealant or a cementitious grout / mortar where the pit is of HDPE construction.
label | • Light duty pits to be used for non-trafficable areas. Heavy duty (Class D) pits shall be used in trafficable areas.
label | • All conduit entry and exit points into pit walls to be sealed to provide watertight seal.
label | Test Method - R
label | Test Frequency - PL + PW
label | Inspection/Verification (Name, signature & date): Sub-Contractor - NR
label | Inspection/Verification (Name, signature & date): Spark NEL Engineer - WP
label | Inspection/Verification (Name, signature & date): Nominated Authority - NR
label | Inspection/Verification (Name, signature & date): IREA - NR
label | Records/Documents - Delivery Dockets (Pit Detail)
checkpoint | 2.2 - Material Conformance - Conduit
label | Resp. Person - SE
label | Specification Reference - VR 733.02 AS 1345 AS 2053.2 IFC Drawings PSDR Section 10.3
label | Acceptance Criteria - All conduits installed underground shall be rigid heavy- duty grade UPVC in accordance with AS 2053.2.
label | • Electrical – Heavy Duty Grade, Rigid orange UPVC conduit to AS/NZS 2053.2; Profile wall- smooth bore HD UPVC conduit to AS/NZS 2053.6
label | • Communications – Heavy Duty Grade, Rigid White UPVC communication conduit to AS/NZS 2053.2;
label | • Profile wall - smooth bore HD UPVC conduit to AS/NZS 2053.6 Review Certificate of Compliance.
label | Test Method - R
label | Test Frequency - PL + PW
label | Inspection/Verification (Name, signature & date): Sub-Contractor - NR
label | Inspection/Verification (Name, signature & date): Spark NEL Engineer - WP
label | Inspection/Verification (Name, signature & date): Nominated Authority - NR
label | Inspection/Verification (Name, signature & date): IREA - NR
label | Records/Documents - Delivery Docket (Conduit Detail)
checkpoint | 2.3 - Material Conformance - Concrete Mix
label | Resp. Person - SE
label | Specification Reference - VR 703
label | Acceptance Criteria - Application of concrete to comply to VR703.
label | Test Method - R
label | Test Frequency - PL + PW
label | Inspection/Verification (Name, signature & date): Sub-Contractor - NR
label | Inspection/Verification (Name, signature & date): Spark NEL Engineer - WP
label | Inspection/Verification (Name, signature & date): Nominated Authority - NR
label | Inspection/Verification (Name, signature & date): IREA - NR
label | Records/Documents - Delivery Docket
label | • Mix Design
checkpoint | 2.4 - Pit Lid Inscription
label | Resp. Person - SE
label | Specification Reference - VicRoads TC-1220
label | Acceptance Criteria - Inscription A:
label | • “A1=VICROADS” or “A2=OTHER INSCRIPTION AS SPECIFIED”
label | ○ Inscription B: “B1=ELECTRICAL” or “ELEC” “B2=COMMUNICATIONS” or “COMMS”
label | • “B3=TRAFFIC SIGNALS” or “TRAFF SIG”
label | • “B4=OTHER INSCRIPTION AS SPECIFIED
label | Test Method - IP
label | Test Frequency - F
label | Inspection/Verification (Name, signature & date): Sub-Contractor - NR
label | Inspection/Verification (Name, signature & date): Spark NEL Engineer - WP
label | Inspection/Verification (Name, signature & date): Nominated Authority - NR
label | Inspection/Verification (Name, signature & date): IREA - NR
label | Records/Documents - Signed ITP
checkpoint | 2.5 - Excavation & Boring
label | Resp. Person - Nominated Authority
label | Specification Reference - VR 733.03 & Drawings
label | Acceptance Criteria - Detailed proposals for boring under carriageways shall be submitted to the Superintendent for review two weeks prior to the programmed commencement of work.
label | • Excavation center-line aligns with the design center-line of the conduit run, to the dimensions specified.
label | ○ Note: Boring by water jet not permitted.
label | • Excavation floor provides a suitable foundation with all debris removed prior to the placement of Embedment Material
label | • Excavation kept free of water until the conduit has been installed and embedment and fill material(s) placed and compacted to a sufficient height, to prevent flotation of the pipeline.
label | Test Method - V
label | Test Frequency - PL + PW
label | Inspection/Verification (Name, signature & date): Sub-Contractor - NR
label | Inspection/Verification (Name, signature & date): Spark NEL Engineer - WP
label | Inspection/Verification (Name, signature & date): Nominated Authority - HP
label | Inspection/Verification (Name, signature & date): IREA - WP
label | Records/Documents - Signed ITP
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 2.6 - Cover Requirements
label | Resp. Person - SE
label | Specification Reference - VR Table 733.031 IFC Drawings: NEL-CNT- SMEC-2102- IEI-DRG-0031
label | Acceptance Criteria - Minimum Cover for underground conduits shall be 600mm.
label | • Note: where minimum depth cover is not possible, a request for an exemption to Superintendent is to be considered (VR 733.03).
label | Test Method - V
label | Test Frequency - PL
label | Inspection/Verification (Name, signature & date): Sub-Contractor - NR
label | Inspection/Verification (Name, signature & date): Spark NEL Engineer - WP
label | Inspection/Verification (Name, signature & date): Nominated Authority - NR
label | Inspection/Verification (Name, signature & date): IREA - NR
label | Records/Documents - Signed ITP
checkpoint | 2.7 - Material conformance - Bedding and Backfill material
label | Resp. Person - SE
label | Specification Reference - Table VR 733.061 IFC drawings
label | Acceptance Criteria - Material shall be free from perishable matter.
label | • Material shall comply with requirements as set-out in table VR 733.061
label | Test Method - IP
label | Test Frequency - PL + PW
label | Inspection/Verification (Name, signature & date): Sub-Contractor - NR
label | Inspection/Verification (Name, signature & date): Spark NEL Engineer - WP
label | Inspection/Verification (Name, signature & date): Nominated Authority - NR
label | Inspection/Verification (Name, signature & date): IREA - NR
label | Records/Documents - Delivery Dockets for: Bedding and Backfilling Material
checkpoint | 2.8 - Bedding Placement and Compaction
label | Resp. Person - SE
label | Specification Reference - VR 733.06 IFC drawings AS 2566
label | Acceptance Criteria - Minimum 80mm bedding below conduits on earth foundation
label | • Minimum 200mm bedding below conduits on rock foundation
label | • Bedding placed to full width of trench, and between conduits
label | • Minimum 150mm bedding above top conduit prior to backfill
label | • Embedment material shall be placed to ensure uniformity of density with no distortion, dislodgment, or damage to the pipeline. Where required to be compacted, embedment material shall be placed in layers of thickness in accordance with design IFC to achieve the density specified uniformly through the depth of each layer.
label | Test Method - IP
label | Test Frequency - PL
label | Inspection/Verification (Name, signature & date): Sub-Contractor - NR
label | Inspection/Verification (Name, signature & date): Spark NEL Engineer - WP
label | Inspection/Verification (Name, signature & date): Nominated Authority - NR
label | Inspection/Verification (Name, signature & date): IREA - NR
label | Records/Documents - Signed ITP
checkpoint | 2.9 - Conduit installation
label | Resp. Person - SE
label | Specification Reference - VR 733.04, IFC Drawings VR 733.01 AS 3000 VR 733.11
label | Acceptance Criteria - All conduits laid with the alignments, levels, gradients and clearances as per the latest revision of IFC drawings
label | • Number of conduits, type spacing and specified colour conduits are installed as per the latest revision IFC drawings.
label | • All conduit and cable pit installation works for electrical wiring shall be carried out by, or under the direct site supervision of a registered electrical contractor and hold appropriate VicRoads prequalification.
label | • An underground conduit warning sign shall be installed in accordance with VicRoads Drawing TC-1208.
label | • Conduit Installation to comply to VR 733.04
label | • Each conduit for electrical wiring and communication cables shall be provided with one synthetic draw cord not less than 3mm diameter and minimum breaking strain of 1.6kN (VR 733.05).
label | ○ Note: Draw strings shall be installed in each conduit where there is no cable installed and removed when there is an existing cable(s) in conduit.
label | Test Method - IP
label | Test Frequency - F/ Pit
label | Inspection/Verification (Name, signature & date): Sub-Contractor - NR
label | Inspection/Verification (Name, signature & date): Spark NEL Engineer - WP
label | Inspection/Verification (Name, signature & date): Nominated Authority - HP
label | Inspection/Verification (Name, signature & date): IREA - WP
label | Records/Documents - Certificates of Electrical Safety
label | • Installation Records
label | • Signed ITP
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 2.10 - Post Bedding (Backfill)
label | Resp. Person - Nominated Authority
label | Specification Reference - VR 733.06
label | Acceptance Criteria - Once the bedding material has been laid and the conduits put in place, works shall not proceed prior to inspection by Superintendent or Representative.
label | ○ Note: Bedding material must not be the same material excavated for the trench, it shall be clearly identifiable as introduced material.
label | Test Method - IP
label | Test Frequency - F
label | Inspection/Verification (Name, signature & date): Sub-Contractor - NR
label | Inspection/Verification (Name, signature & date): Spark NEL Engineer - WP
label | Inspection/Verification (Name, signature & date): Nominated Authority - HP
label | Inspection/Verification (Name, signature & date): IREA - WP
label | Records/Documents - Signed ITP
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 2.11 - Pit installation
label | Resp. Person - SE
label | Specification Reference - VR 733.07 VicRoads Drawings TC-1230, TC-2203 IFC Drawings
label | • Acceptance Criteria - Pits to be installed on crushed rock base thickness as per IFC Drawings.
label | • Access pits shall be installed in accordance with VicRoads drawings TC-2200 to TC-2219.
label | ○ Note: Larger communication pits may be used where deemed appropriate due to splicing or other cable requirements as agreed with the Superintendent.
label | • Pits to be constructed such that the Finished Surface Level to the top of the pit lid matches the surrounding FSL.
label | Test Method - V
label | Test Frequency - F/ Pit
label | Inspection/Verification (Name, signature & date): Sub-Contractor - NR
label | Inspection/Verification (Name, signature & date): Spark NEL Engineer - WP
label | Inspection/Verification (Name, signature & date): Nominated Authority - NR
label | Inspection/Verification (Name, signature & date): IREA - NR
label | Records/Documents - Certificates of Electrical Safety
label | • Installation Records
checkpoint | 2.12 - Pit Lid Surrounds
label | Resp. Person - SE
label | Specification Reference - VR 733.07 (c)
label | Acceptance Criteria - Before the pit lid surround or pre- formed collar is cemented into position, an inspection by a Superintendent (Nominated Authority Representative) must be carried out.
label | Test Method - IP
label | Test Frequency - F
label | Inspection/Verification (Name, signature & date): Sub-Contractor - NR
label | Inspection/Verification (Name, signature & date): Spark NEL Engineer - WP
label | Inspection/Verification (Name, signature & date): Nominated Authority - HP
label | Inspection/Verification (Name, signature & date): IREA - WP
label | Records/Documents - Signed ITP
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 2.13 - Warning Tape
label | Resp. Person - SS
label | Specification Reference - VR 733.05
label | Acceptance Criteria - Marker tape to be installed 300mm below ground level.
label | • Marker tape to be installed 75mm from the trench wall.
label | • Where both electrical and communication conduits are provided in a trench two marker tapes shall be provided one for electrical and the other for communication conduits.
label | Test Method - V
label | Test Frequency - PL
label | Inspection/Verification (Name, signature & date): Sub-Contractor - NR
label | Inspection/Verification (Name, signature & date): Spark NEL Engineer - WP
label | Inspection/Verification (Name, signature & date): Nominated Authority - NR
label | Inspection/Verification (Name, signature & date): IREA - NR
label | Records/Documents - Photos
checkpoint | 2.14 - Detector Pits
label | Resp. Person - SE
label | Specification Reference - VR 733.08
label | Acceptance Criteria - Detector pits and detector pit covers shall be constructed and installed in accordance with VR Standard Drawings TC-1310 and TC-1320.
label | Test Method - V
label | Test Frequency - F
label | Inspection/Verification (Name, signature & date): Sub-Contractor - NR
label | Inspection/Verification (Name, signature & date): Spark NEL Engineer - WP
label | Inspection/Verification (Name, signature & date): Nominated Authority - NR
label | Inspection/Verification (Name, signature & date): IREA - NR
label | Records/Documents - Signed ITP
checkpoint | 2.15 - Test Records - Compaction (Backfill) - Concrete
label | Resp. Person - SE
label | Specification Reference - VR 733.06(d) VR 703
label | Acceptance Criteria - Backfill Compaction
label | • Bedding and backfill materials shall have compacted in layers to a density ratio >95%,
label | • Moisture content within the range 85% to 115% where backfill material contains material retained on a 37.5mm AS sieve.
label | ○ Note (Backfill):
label | • Detailed proposals for compaction of backfill materials of nominal size >40mm shall be submitted to Superintendent for review before commencing works.
label | ○ Note (Concrete):
label | • Minimum test requirements to comply to VR 703.11 (2021).
label | Test Method - V
label | Test Frequency - PL
label | Inspection/Verification (Name, signature & date): Sub-Contractor - NR
label | Inspection/Verification (Name, signature & date): Spark NEL Engineer - WP
label | Inspection/Verification (Name, signature & date): Nominated Authority - NR
label | Inspection/Verification (Name, signature & date): IREA - NR
label | Records/Documents - NATA Test Records
section | 3.0 Post Operations (Include Inspection and Testing)
checkpoint | 3.1 - Certification of installation
label | Resp. Person - SE
label | Specification Reference - VR 733.04, VR 733.07 AS 3000
label | Acceptance Criteria - All conduit installation works for electrical wiring and communications cabling shall be carried out by, or under the direct supervision of, appropriately registered and licensed personnel provided by the Contractor.
label | Test Method - V
label | Test Frequency - PL
label | Inspection/Verification (Name, signature & date): Sub-Contractor - NR
label | Inspection/Verification (Name, signature & date): Spark NEL Engineer - HP
label | Inspection/Verification (Name, signature & date): Nominated Authority - NR
label | Inspection/Verification (Name, signature & date): IREA - NR
label | Records/Documents - Certificate of Electrical Safety
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 3.2 - Redline Drawings
label | Resp. Person - SE
label | Specification Reference - VR 733.11 IFC Drawings
label | Acceptance Criteria - a). ‘As-Constructed drawings showing complete conduit network including conduit types, sizes and depths.
label | b). the above “as constructed’ drawings shall also show all pits, pit types and pit sizes.
label | c). certificates of electrical safety for all conduits and pits installed
label | d). documentation demonstrating that all pits and conduits have been installed in accordance with requirements of this specification.
label | Test Method - V
label | Test Frequency - F
label | Inspection/Verification (Name, signature & date): Sub-Contractor - NR
label | Inspection/Verification (Name, signature & date): Spark NEL Engineer - WP
label | Inspection/Verification (Name, signature & date): Nominated Authority - NR
label | Inspection/Verification (Name, signature & date): IREA - NR
label | Records/Documents - Redline Mark-Up Records
section | 4.0 Quality
checkpoint | 4.1 - Identification and control of non- conforming products or services (if applicable)
label | Resp. Person - QSR
label | Specification Reference - CQMP
label | Acceptance Criteria - Review and confirm closure of NCR’s and associated RFI’s prior to closing of construction lot
label | Test Method - R
label | Test Frequency - PL
label | Inspection/Verification (Name, signature & date): Spark NEL Engineer - WP
label | Records/Documents - NCR closed with related documentation
label | Field Notes / Comments - InEight Form Reference Numbers (NCRs, RFIs etc)
checkpoint | 4.2 - Check all quality records for lot closure
label | Resp. Person - QSR
label | Specification Reference - CQMP
label | Acceptance Criteria - All applicable quality records are complete
label | Test Method - R
label | Test Frequency - PL
label | Inspection/Verification (Name, signature & date): Spark NEL Engineer - WP
label | Records/Documents - Compiled documents (all data reports and records)