## Project Structure
Folder Structure |  |  |  | Checklists
Site QA
Rough In
West Tower
|  |  | Basement | Fire Sprinkler System Installation - Rough In
|  |  | Level 1 | Fire Sprinkler System Installation - Rough In
|  |  | Level 2 | Fire Sprinkler System Installation - Rough In
|  |  | Level 3 | Fire Sprinkler System Installation - Rough In
|  |  | Level 4 | Fire Sprinkler System Installation - Rough In
|  |  | Level 5 | Fire Sprinkler System Installation - Rough In
|  |  | Level 6 | Fire Sprinkler System Installation - Rough In
|  |  | Level 7 | Fire Sprinkler System Installation - Rough In
|  |  | Roof | Fire Sprinkler System Installation - Rough In
East Tower
|  |  | Basement | Fire Sprinkler System Installation - Rough In
|  |  | Level 1 | Fire Sprinkler System Installation - Rough In
|  |  | Level 2 | Fire Sprinkler System Installation - Rough In
|  |  | Level 3 | Fire Sprinkler System Installation - Rough In
|  |  | Level 4 | Fire Sprinkler System Installation - Rough In
|  |  | Level 5 | Fire Sprinkler System Installation - Rough In
|  |  | Level 6 | Fire Sprinkler System Installation - Rough In
|  |  | Level 7 | Fire Sprinkler System Installation - Rough In
|  |  | Roof | Fire Sprinkler System Installation - Rough In
Fit Off
West Tower
|  |  | Basement | Fire Sprinkler System Installation - Fit Off
|  |  | Level 1 | Fire Sprinkler System Installation - Fit Off
|  |  | Level 2 | Fire Sprinkler System Installation - Fit Off
|  |  | Level 3 | Fire Sprinkler System Installation - Fit Off
|  |  | Level 4 | Fire Sprinkler System Installation - Fit Off
|  |  | Level 5 | Fire Sprinkler System Installation - Fit Off
|  |  | Level 6 | Fire Sprinkler System Installation - Fit Off
|  |  | Level 7 | Fire Sprinkler System Installation - Fit Off
|  |  | Roof | Fire Sprinkler System Installation - Fit Off
East Tower
|  |  | Basement | Fire Sprinkler System Installation - Fit Off
|  |  | Level 1 | Fire Sprinkler System Installation - Fit Off
|  |  | Level 2 | Fire Sprinkler System Installation - Fit Off
|  |  | Level 3 | Fire Sprinkler System Installation - Fit Off
|  |  | Level 4 | Fire Sprinkler System Installation - Fit Off
|  |  | Level 5 | Fire Sprinkler System Installation - Fit Off
|  |  | Level 6 | Fire Sprinkler System Installation - Fit Off
|  |  | Level 7 | Fire Sprinkler System Installation - Fit Off
|  |  | Roof | Fire Sprinkler System Installation - Fit Off
Pump Room
Fire Pump Room
SCV Cupboard
SCV Cupboard
Variations
West Tower
|  |  | Basement | Ability to add Variations Checklist
|  |  | Level 1 | Ability to add Variations Checklist
|  |  | Level 2 | Ability to add Variations Checklist
|  |  | Level 3 | Ability to add Variations Checklist
|  |  | Level 4 | Ability to add Variations Checklist
|  |  | Level 5 | Ability to add Variations Checklist
|  |  | Level 6 | Ability to add Variations Checklist
|  |  | Level 7 | Ability to add Variations Checklist
|  |  | Roof | Ability to add Variations Checklist
East Tower
|  |  | Basement | Ability to add Variations Checklist
|  |  | Level 1 | Ability to add Variations Checklist
|  |  | Level 2 | Ability to add Variations Checklist
|  |  | Level 3 | Ability to add Variations Checklist
|  |  | Level 4 | Ability to add Variations Checklist
|  |  | Level 5 | Ability to add Variations Checklist
|  |  | Level 6 | Ability to add Variations Checklist
|  |  | Level 7 | Ability to add Variations Checklist
|  |  | Roof | Ability to add Variations Checklist

## Checklists
type | name | values
checklist | Fire Sprinkler System Installation - Rough In
checkpoint | Fire Sprinkler System Installation
checkpoint | All sprinkler mains/range pipes are installed in the correct position, elevation and alignment in accordance with the approved plan
checkpoint | All supports/brackets/hangers are correctly installed and spaced
checkpoint | All Roll Grooved couplings are tightened correctly
checkpoint | No mains/range pipe is clashing with other services
checkpoint | All Ceiling Space sprinkler heads are installed
checkpoint | All flexible droppers are installed with sprinkler head and inner escutcheon plate and in correct locations
checkpoint | Floor Isolation valve & test drain installed and connected inc chain/padlocked
checkpoint | Installation pipe works ready for hydrostatic pressure testing
checkpoint | Floor tested to 1200kPa for a period of 4 Hrs and witnessed
checkpoint | Work complete (photo required)
checklist | Fire Sprinkler System Installation - Fit Off
checkpoint | Fire Sprinkler System Installation
checkpoint | Below Ceiling heads set to correct height
checkpoint | Hallway/common heads complete
checkpoint | Escutcheon plates installed
checkpoint | Sprinkler heads defect free
checklist | Fire Pump Room
checkpoint | Plinth setout and fixed in position
checkpoint | Pump secured to plinth
checkpoint | Water supply connected
checkpoint | Discharge supply connected
checkpoint | Annubar discharge plumbed to waste
checkpoint | Heat exchanger plumbed to waste
checkpoint | Gland drain plumbed to waste
checkpoint | Exhaust plumbed to mech exhaust
checkpoint | Exhaust heat wrapped to 2.1m AFFL
checkpoint | All M/V's chained/padlocked/tagged
checkpoint | 240V power supplied to control panel
checkpoint | Back up batteries installed and secure
checkpoint | 93* Heads installed within pump room
checkpoint | Signage & Block Plan/s installed
checklist | SCV Cupboard
checkpoint | Water supply connected
checkpoint | Discharge Mains connected
checkpoint | Annubar discharge plumbed to waste
checkpoint | Waste/Test drains plumbed to waste
checkpoint | Alarm Pressure Switch installed
checkpoint | Water Motor Gong mounted/ connected
checkpoint | Towns Main Gauge/s run from tapping
checkpoint | Jacking Pump connected & set correctly
checkpoint | All valves chained/padlocked/tagged
checkpoint | 240V power available for J/Pump
checkpoint | SCV's correctly labelled
checkpoint | Block Plan/s installed
checkpoint | Spares box mounted & stocked inc s/key
checkpoint | Test Book supplied within spares box
checkpoint | 003 barrel & external signage supplied
checklist | Variations
checkpoint | Ensure all variation details are completed
text | Name
text | Company
text | Day
text | Date
select | Shift | Day, Night
text | Start AM / PM
text | Finish AM / PM
text | Site Address
text | Description of work performed
text | Names of persons performing work
text | Materials used
text | Hours per man
checkpoint | Fireline Employee/s signatures
checkpoint | Builders representative signature
type | name | values
checklist | Fire Penetration
checkpoint | Fire Penetration labelled & caulked in accordance with AS 4072.1 Drawing Reference No AO101