## Inspection and Test Plan
General Details | Project details
Project Name | Bluff Hill Watermain Stage 2 Inspection
Project Number | 561281
Customer | Invercargill City Council
Contract Number | 1073
Area/ Sub-System | Southland Water
Lot ID Number | 56126
ITP Number | 2
Version | A
ITP Description | Watermain Construction Stage 2
Discipline | Water
Specification | Section C ICC Project Specifications and Section D ICC Standard Specifications
Drawings | Drawings provided by ICC ESG
Prepared By | Engineering Services Group
Date | 12/07/23
Quality Specified
Section | Item No. | Activity/Task Description | Inspection Point: Quality Control Activity | Acceptance Criteria | Verifying Document | Reference: Contract Specs/Standards | Inspection Point/ Signature & Date
Preliminary Works | 3.1 | Pre-construction Photos | Photos of worksite including vehicle access points. Photos of any existing defects/damage. | Coverage of whole site | Photos saved | D1.4 | PM
Preliminary Works | 3.2 | Verify Construction Drawings | Verify Construction Drawings that are in the site folder are the latest revision. | Latest drawings approved | Drawings Register |  | PM
Preliminary Works | 3.3 | Road Authority Notifications | Corridor access Permit. Block by block Temporary Traffic Management Plans. | Permit & Traffic Plan approved | Work Access Permit & TMP | C1.09, D1.4 | PM
Preliminary Works | 3.4 | Management Plan | H&S Plan Environmental Plan Quality Assurances | Plans & Safety Measures in place | H&S Plan, Method Statement | D1.3 | PM, CR
Preliminary Works | 3.5 | Public Notification | Notice of works to properties in the construction zone in each block Notification to Rubbish collection contractor. Project Signage | 48 hours prior notification | Letter to residents | D1.10 | PM
Preliminary Works | 3.6 | Shutdown/Isolation | Shutdown/Isolation process verified in each block closure | Shutdown process verified | Notification letters | C1.16, D2.7.8 | PS
Preliminary Works | 3.7 | Construction Set Out | Correctly mark out the position of the new pipelines for construction. | Construction Plans checked | Construction Plans | D2.7.1 | PS, CR
Preliminary Works | 3.8 | Pre-Excavation Permits | Permit to excavate for the location has been endorsed by an authorised person. • Existing service plans & locates • Close approach permits • Notifiable works | Permit to excavate endorsed | Ground Disturbance Permit | D1.7 | PS
Incoming Goods Inspections | 4.1 | Pipe & Fitting Inspections | Visual check of materials delivered: • Correct Material & dimensions • Condition & Quantity • Free of defects – surface abrasion, ovality, not kinked or crushed • Batch/serial numbers present | Correct material & no defects | Packing Slips | D2.4,D3.3, D4.3, D5.3, D8.3 | PS
Incoming Goods Inspections | 4.2 | Pipe & Fitting Storage | Stored as per manufacturers specifications including maximum height limits and safely chocked in place. • All pipes are end capped. • No scoring of pipe more than 10% of thickness. • No damage to epoxy coating on Ductile fittings. | Stored as per manufacturer | Manufacturer’s Storage Instructions |  | PS, CR
Construction Inspections | 5.1 | Trench Excavation | Trench width to be sufficient to safely lay the pipe (including shoring if required) and compact the side support of the new pipe. Bedding details below; Sufficient room to enable the pipe, joint, bed, haunch or surround shown in the drawings to be accommodated. Trench depth to enable pipe to be laid with the designed cover as shown on construction plans. If trench bottom to be suitable to compact pipe bedding as support pipe. | Trench dimensions correct | Daily Site Diary | D2.6, D2.7 | PS
Construction Inspections | 5.2 | Encountered Services | Block by block ensure existing live services are not unnecessarily damaged by works. Repair any services that are temporarily removed during construction. Record any services found. | Existing services not damaged | Encountered Services Record | D1.7, D2.7.7 | PS
Construction Inspections | 5.3 | Pipe Installation | Interior of each pipe visually inspected to ensure free of debris. Re-cap end of pipe after installation. Check pipe installed at correct depth. Ensure all collars are free from contamination in McDougall St berm | Pipes free of debris & correctly installed | Daily Site Diary | D2.5, D2.7, D8.4.2 | PS
Construction Inspections | 5.4 | Concrete Pre-Pour Inspection | Check dimensions of formwork match details in the Construction Drawings. Check pipe fitting joints are clear of concrete pour. Thrust blocks to be poured against good solid natural ground. | Thrust blocks against solid ground | Daily Site Diary & Photos | D5.1, D5.3.2, D5.7 | PS, CR
Construction Inspections | 5.5 | Hydrant Depth | Confirm depth requirements have been met; Hydrant outlet: 200mm min. to 400mm max. | Hydrant depth verified | Daily Site Diary | D5.5 | PS
Construction Inspections | 5.6 | Compaction Testing | Confirm trenches in paved areas are compacted to standard block by block. | Compaction confirmed | Clegg Record Sheet | D2.7.10 | PS
Construction Inspections | 5.7 | Watermain Pressure Testing | Hydrostatic pressure test on new pipeline and fittings block by block. | Pressure test passed | Pressure Test Record Sheet | D2.9.1, AS/NSZ 2566.2:2002 Section 6 | PS, CR
Construction Inspections | 5.8 | Watermain Sterilization | Flushing and sterilizing full length of new pipeline and fittings block by block. | Sterilization completed | Sterilization Record Sheet | D2.9.1, AS/NSZ 2566.2:2002 Section 6 | PS, CR
Construction Inspections | 5.9 | As-built Information | Capture data for all new construction work. | Redline mark-up plan submitted | Redline Mark-up Plan | C1.22 | PM
Final Inspection and Handover | 6.1 | Final Inspection of Works | Work is inspected by the authorised person and complies with the nominated specification/standards | Work inspected & complies with standards | Practical Completion Certificate |  | PM

## General_Details
SECTION 1 – GENERAL DETAILS
Project Name
Project Number
Customer | Invercargill City Council
Contract Number
Area/ Sub-System | [Location/ Water, Stormwater, Wastewater]
Lot ID Number
ITP Number
Version | A
ITP Description | [Watermain/ Stormwater Main/ Wastewater Main - Construction]
Discipline | [Water, Stormwater, Wastewater]
Specifications | Section C and D - ICC Project Specifications Invercargill City Council District Plan Code of Land Development (current version) NZS 4404:2010 (including ICC Addendum) New Zealand Handbook – National Code of Practice for Utility Operators Access to Transport Corridors Health and Safety at Work Act 2015 Relevant Work Safe guidelines NZTA/TNZ AS/NZS Standards Relevant ISO Standards Manufacturers specifications for all materials [Additional Specification reference]
Drawings | Drawings provided by: [ICC ESG] [External Consultant]
Prepared By | Engineering Services Group
Date
Quality Specified
Responsabilities
Inspection Key | Description | Role Key | Role | Name | Signature/Initial
A | Action | CM | Contract Manager
B | Report by Breach | ER | Engineer's Representative
C | Check | IP | Inspection Personnel
D | Dimension Inspection | MC | Material Controller
E | Examine | OP | Operations Manager
H | Hold Point | PM | Project Manager
I | Inspection | PS | Project Supervisor
M | Monitor on Random Basis | QE | Quality Engineer
O | Operation | QM | QA Manager
R | Review | SP | Supervisor
S | Subcontractor | ST | Superintendent
V | Visual Verification | SV | Surveyor
W | Witness Point | WS | Welding Supervisor
|  | FM | Foreman
SECTION 2 – SIGNATURES - CLOSE-OUT & APPROVAL
ITP Close-Out by Downer | Name: | Signature: | Date:
Downer Approval | Name: | Signature: | Date:
Customer Approval | Name: | Signature: | Date:

## ITP_Items
INSPECTION TEST PLAN | [7 empty] | [Zone/Location for Inspection] : From CH__________ to CH___________
[CONTRACT NAME/CONTRACT NUMBER]
Role | Key Role | Name/Company | Action | A | Action | O | Operation | Inspection Date:
Foreman | FM |  |  | B | Report by Breach | R | Review | [Add sketch detail / location / clarification / etc]
Supervisor | SP |  |  | C | Check | S | Subcontractor
QA Manager | QM |  |  | D | Dimension Inspection | V | Visual Verification
Contract Manager | CM |  |  | E | Examine | W | Witness Point
Project Manager | PM |  |  | H | Hold Point
Engineer's Representative | ER | [Salomon/ICC] |  | I | Inspection
[Add relevant role from list] |  |  |  | M | Monitor on Random Basis
Section | Preliminary Works
[ITP subject to Quality - Specifications D1.3.3, AS/NZS 2566.2:2002, ICC CoP, NZS 4404] | [10 empty] | Inspection Point/ Signature
Item No. | Activity/Task Description | Inspection Point: Quality Control Activity | Inspection Method / Test Point | Acceptance Criteria | Frequency | Verifying Records | Reference: Contract Specs/Standards | ACTION | PASS / FAIL | Comments | [Contractor] | [Engineer]
[SoQ ref.] | Pre-construction Photos | Photos of worksite including vehicle access points. Photos of any existing defects/damage. | Photos/videos | Coverage of whole site | Pre-construction | Photos saved Records submitted to the Engineer | D1.5
| Pre-construction walkover | Contractor and Engineer | Photos/videos |  | Pre-construction |  | D1.5
| Verify Construction Drawings | Verify Construction Drawings that are in the site folder are the latest revision. | Confirm latest version | Latest drawings approved | Pre-construction | Drawings Register | D1.22
| Traffic Management Plan and Work Access Permit | Corridor access Permit. Block by block Temporary Traffic Management Plans. | CAR Number WAP number | Permit & Traffic Plan approved | Pre-construction | Work Access Permit & TMP | D1.3.2
| Management Plan | Site-Specific Safety Plan | Plan submittied to the Engineer | Engineer to approve plan based on NZ Standards and Contract requirments | Pre-construction | Site Management Plan | D1.3
| Management Plan | Quality Management Plan | Plan submittied to the Engineer | Engineer to approve plan based on NZ Standards and Contract requirments | Pre-construction | Site Management Plan | D1.3
| Management Plan | Environmental Management Plan | Plan submittied to the Engineer | Engineer to approve plan based on NZ Standards and Contract requirments | Pre-construction | Site Management Plan | D1.3
| Public Notification and Stakeholders | Notice of works to properties in the construction zone in each block Notification to Rubbish collection contractor. Project Signage Notification to stakeholders via letter drop, Antenno and Great South comms | Draft Letter submitted for approval. | Engineer to approve letter | 48 hours prior notification | Letter to residents List:- letter dropping by adress | D1.11
| Shutdown/Isolation | Shutdown/Isolation process verified in each block closure | Verify with Council staff | Shutdown process verified (Protocols inluded in Appendix) | Pre-construction | Council staff confirmation Notification letters | D5.4 and Appendix - Valve shutdown procedure
| Construction Set Out | - Mark out chainages on site(road or K&C) - Mark out alignment as per design drawings - Verify ground levels and exiting structres by using coordinates and land surveying equipment. - Install temporary pins (nails) RLs to verify levels during inspections. | Verification by comparison: Drawings vs Site set out | Construction Plans checked Levels verified and reported to the Engineer | Pre-Construction and During Construction | Construction Plans Set out mark-ups List of RLs Daily diary Sheets | D2.7.1 C Specs
| Pre-Excavation Permits | Permit to excavate for the location has been endorsed by an authorised person. • Existing service plans & locates • Close approach permits • Notifiable works | Visual verififcation | Permit to excavate endorsed | Daily, and/or Depending on risk assessment | Ground Disturbance Permit Site inspection Sheets Daily diary Sheets | D1.7
| Materials to comply with contract and NZTA M/4 specification | Laboratory test certificates: MDD and Grading Results: Bedding Material (AP20) AP65 AP40 | Lab report Visual inspection | Contract Document and Specifications | Pre-construction During Construction | Grading curves Site Inspection records | D2.7 Section 3 - AS/NZS 2566.2:2002
| Existing asset condition | Recorded via video by Contract Manager | Existing or new CCTV | Reporting to the Engineer Video recordings | Pre-construction | CCTV records and report | D1.32.4
Incoming Goods
| Pipe and fittings inspection | Visual check of materials delivered: • Correct Material & dimensions • Condition & Quantity • Free of defects – surface abrasion, ovality, not kinked or crushed • Batch/serial numbers present Stored as per manufacturers specifications • All pipes are end capped. • No scoring of pipe more than 10% of thickness. • No damage to epoxy coating on Ductile fittings. | Visual verififcation | Contract Document and Specifications Manufacturers specifications | Pre-construction During Construction | Site Inspection records Reporting to the Engineer Daily diary Sheets
| Protection of other services | Service locates done on other assets, and workers familiar with BeforeUDig and GIS plans | Service locate Mark-up on site | Contract Document and Specifications | Prior Excavation works | Drawings Asbuilt - Mark-ups | D1.8
Construction inspections
| Trench Excavation | Trench dimensions, stability, dewatering, falls from heights, confined spaces | Trench dimensions correct: - Width for providing safety, shoring and side support for haunching. - Depth for pipe installation at designed levels, including structures and bedding support | Trench Design Drawings Contract Document and Specifications | Pre-Construction and During construction | Site Inspection Daily diary sheets Drawings | D2.6 AS/NZS 2566.2:2002 Section 4
| Encountered Services | Existing services to be protected Repair any services that are temporarily removed during construction. Record any services found. | Service locate Visual inspection Dye Testing Historical records Inspection holes | Confirmation of live services and abandonded services | During Construction | Encountered services record sheets. Daily Diary Sheets | D2.7.4
| Pipe Installation | Visual inspection of interior of pipe. Re-cap end of pipe after installation. Check pipe installed at correct depth and levels Ensure all collars are free from contamination | - Accurate location of the pipe crown and invert levels every 10m. - Inlet and outlet invert level at structures. - Road sump levels. - Road surface levels, kerb and channel every 20m | Levels confirmed as per designs Levels verified using land surveying equipmnet Bedding depth confirmed on site Pipes debris free and protected at ends | During Construction | Site Inspection records Photos Daily Diary Sheets Leveling Sheet | D Specs AS/NZS 2566.2:2002 Section 5
| Concrete Pre-Pour Inspection | Check dimensions of formwork match details in the Construction Drawings. Check pipe fitting joints are clear of concrete pour. Thrust blocks to be poured against good solid natural ground. | Thrust blocks and Anchor blocks against solid ground | Thrust block dimensions as per design CoP and standard details | During Construction | Site Inspection records Photos Daily Diary Sheets Delivery dockets | D 5.3, D5.7 CoP standard details
| Hydrant Depth | Confirm depth requirements have been met; Hydrant outlet: 200mm min. to 400mm max. | Site Inspection Hydrant depth verified Installation and fittings as per design and standards | Compliance with drawings. Compliance with Specifications | During Construction | Drawings Site Inspection records Photos Daily Diary Sheets Manufacturers guide | D 5.3, D5.7 CoP standard details W2
| Compaction Testing | Confirming each layer is 200mm maximum to be compacted. Controling segregation of aggregates Controling oversize course aggregates Ensuring the right material is used for each layer Initial Compaction Test to calibrate NDM and Clegg Testing. Moisture exceedance to be controlled on Site | Site Inspection: Depth of each layer Subgrade appears to be free from roots and organic material Bedding material installed meeting specification requirement (ICC D2.7 & AS/NZS 2566.2:2002 5.4 & 5.6) Clegg testing NDM testing No water saturated areas. Degree of saturation is in accordance with TNZ B/2 and is an absolute maximum of 80% (check if water content is likely to have changed significantly since testing i.e. sustained period of rain, and if so further testing may be necessary). | Surface must not show any aggregate segregation. Compaction lab results | During Construction Clegg Testing every 6m NDM Testing every 120m As per agreement on site | Initial Clegg Testing results for calibration. Clegg Test Calibration results Lab results for NDM: AP65 >=95% AP40 >=98% Daily diary Sheets | D2.7
| Surface Reinstatement | Initial inspection done by Contractor Mix design / Chip seal design copy supplied to the Engineer 48 hours in advanced Spray rate - Tack Coat / membrane seal (Spray sheets submitted) Spray rate - Chip seal (emulsion /binder) – Spray sheets submitted Check favourable Weather Conditions CCTV submitted in advanced (if applicable) Pre-seal Inspection requested 24 hrs in advanced. | Site pre-seal inspection Tightly compacted, non-glazed, clean stone mosaic surface that remains bound when swept. Surface swept and clean of fines and running course or areas available to allow the inspection to occur (optional as the inspector will sweep as required) Tack coat / membrane seal visual inspection done. Coverage achieved with no gaps, no bubbles, or blisters etc Overcuts as per specification / chip seal overlap as per specification and utility code requirements K&C / islands etc protected from bitumen spray Asphalt temp - At loading Asphalt temp - At Placing / Compaction | Free of bumps, surface shape and finish in accordance with TNZ B/2, variation over a 3m straight edge < 10mm. (Note : Roads longer than 150m will require NAASRA roughness testing) Compaction testing for wearing course done as per NZTA M10 specs. Or in case of lots involving less than 30 Ton contractor to provide documents in proof to ensure required compaction is achieved. |  |  | D2.8 NZTA M10
| Watermain Pressure Testing | Hydrostatic pressure test on new pipeline and fittings block by block. | Pressure test to be determined by the Engineer | Testing pass | To be agree with Contractor | Test result sheets Tests Result Report Daily diary Sheets | AS/NZS 2566.2:2002 Section 6
| Watermain Sterilization | Flushing and sterilizing full length of new pipeline and fittings block by block. | Sterilization coordinated with ICC lab | Confirmation by ICC lab | To be agree with Contractor | Test result report from ICC lab Daily diary Sheets | D2.9 NZS4404:200 AS/NZS 2566.2:2002 Section 7
| As-built Information | Capture data for all new construction work Submitting recording sheets as per Appendixes | Red pen mark-up plan submitted CAD file submitted | Clear and well records on the red pen mark-ups, including long sections. Excel sheet with coordinates and levels CAD drawings including structure locations, coordinates, details of link-ins and connections. ICC Vertical Datum | Red pen mark-ups: by commissioned block CAD drawing: to achieve practical completion | Recording sheets provided in Appendixes Photos Survey Data: Pipe Levels, lengths, locations, etc | D17, D1.31.2
| Final Inspection of Works | Work is inspected by the authorised person and complies with the nominated specification/standards | Walkover with the Engineer Defects list verification Recording defects to be rectified | Defects list recorded/rectified Works complying with designs and standard specifications | At end of works | Defects list Weekly and Monthly Reports As-builts and QA information