## res
type | name | values | prefix | postfix | usage count | user addable | template name | Resource Id
checklist | ITP-002 - Watermain Construction Stage 2 | itp |  |  |  |  | ITP-002 - Watermain Construction Stage 2 - Rev A
section | Preliminary Works
checkpoint | 3.1 - Pre-construction Photos
label | Inspection Point: Quality Control Activity - Photos of worksite including vehicle access points.
label | ○ Photos of any existing defects/damage.
label | Acceptance Criteria - Coverage of whole site
label | Verifying Document - Photos saved
label | Reference: Contract Specs/Standards - D1.4
label | Inspection Point/Signature & Date - PM
checkpoint | 3.2 - Verify Construction Drawings
label | Inspection Point: Quality Control Activity - Verify Construction Drawings that are in the site folder are the latest revision.
label | Acceptance Criteria - Latest drawings approved
label | Verifying Document - Drawings Register
label | Reference: Contract Specs/Standards -
label | Inspection Point/Signature & Date - PM
checkpoint | 3.3 - Road Authority Notifications
label | Inspection Point: Quality Control Activity - Corridor access Permit.
label | ○ Block by block Temporary Traffic Management Plans.
label | Acceptance Criteria - Permit & Traffic Plan approved
label | Verifying Document - Work Access Permit & TMP
label | Reference: Contract Specs/Standards - C1.09, D1.4
label | Inspection Point/Signature & Date - PM
checkpoint | 3.4 - Management Plan
label | Inspection Point: Quality Control Activity - H&S Plan
label | ○ Environmental Plan
label | ○ Quality Assurances
label | Acceptance Criteria - Plans & Safety Measures in place
label | Verifying Document - H&S Plan, Method Statement
label | Reference: Contract Specs/Standards - D1.3
label | Inspection Point/Signature & Date - PM, CR
checkpoint | 3.5 - Public Notification
label | Inspection Point: Quality Control Activity - Notice of works to properties in the construction zone in each block
label | ○ Notification to Rubbish collection contractor.
label | ○ Project Signage
label | Acceptance Criteria - 48 hours prior notification
label | Verifying Document - Letter to residents
label | Reference: Contract Specs/Standards - D1.10
label | Inspection Point/Signature & Date - PM
checkpoint | 3.6 - Shutdown/Isolation
label | Inspection Point: Quality Control Activity - Shutdown/Isolation process verified in each block closure
label | Acceptance Criteria - Shutdown process verified
label | Verifying Document - Notification letters
label | Reference: Contract Specs/Standards - C1.16, D2.7.8
label | Inspection Point/Signature & Date - PS
checkpoint | 3.7 - Construction Set Out
label | Inspection Point: Quality Control Activity - Correctly mark out the position of the new pipelines for construction.
label | Acceptance Criteria - Construction Plans checked
label | Verifying Document - Construction Plans
label | Reference: Contract Specs/Standards - D2.7.1
label | Inspection Point/Signature & Date - PS, CR
checkpoint | 3.8 - Pre-Excavation Permits
label | Inspection Point: Quality Control Activity - Permit to excavate for the location has been endorsed by an authorised person.
label | ○ Existing service plans & locates
label | ○ Close approach permits
label | ○ Notifiable works
label | Acceptance Criteria - Permit to excavate endorsed
label | Verifying Document - Ground Disturbance Permit
label | Reference: Contract Specs/Standards - D1.7
label | Inspection Point/Signature & Date - PS
section | Incoming Goods Inspections
checkpoint | 4.1 - Pipe & Fitting Inspections
label | Inspection Point: Quality Control Activity - Visual check of materials delivered:
label | ○ Correct Material & dimensions
label | ○ Condition & Quantity
label | ○ Free of defects – surface abrasion, ovality, not kinked or crushed
label | ○ Batch/serial numbers present
label | Acceptance Criteria - Correct material & no defects
label | Verifying Document - Packing Slips
label | Reference: Contract Specs/Standards - D2.4,D3.3, D4.3, D5.3, D8.3
label | Inspection Point/Signature & Date - PS
checkpoint | 4.2 - Pipe & Fitting Storage
label | Inspection Point: Quality Control Activity - Stored as per manufacturers specifications including maximum height limits and safely chocked in place.
label | ○ All pipes are end capped.
label | ○ No scoring of pipe more than 10% of thickness.
label | ○ No damage to epoxy coating on Ductile fittings.
label | Acceptance Criteria - Stored as per manufacturer
label | Verifying Document - Manufacturer’s Storage Instructions
label | Reference: Contract Specs/Standards -
label | Inspection Point/Signature & Date - PS, CR
section | Construction Inspections
checkpoint | 5.1 - Trench Excavation
label | Inspection Point: Quality Control Activity - Trench width to be sufficient to safely lay the pipe (including shoring if required) and compact the side support of the new pipe. Bedding details below;
label | ○ Sufficient room to enable the pipe, joint, bed, haunch or surround shown in the drawings to be accommodated.
label | ○ Trench depth to enable pipe to be laid with the designed cover as shown on construction plans.
label | ○ If trench bottom to be suitable to compact pipe bedding as support pipe.
label | Acceptance Criteria - Trench dimensions correct
label | Verifying Document - Daily Site Diary
label | Reference: Contract Specs/Standards - D2.6, D2.7
label | Inspection Point/Signature & Date - PS
checkpoint | 5.2 - Encountered Services
label | Inspection Point: Quality Control Activity - Block by block ensure existing live services are not unnecessarily damaged by works.
label | ○ Repair any services that are temporarily removed during construction.
label | ○ Record any services found.
label | Acceptance Criteria - Existing services not damaged
label | Verifying Document - Encountered Services Record
label | Reference: Contract Specs/Standards - D1.7, D2.7.7
label | Inspection Point/Signature & Date - PS
checkpoint | 5.3 - Pipe Installation
label | Inspection Point: Quality Control Activity - Interior of each pipe visually inspected to ensure free of debris.
label | ○ Re-cap end of pipe after installation.
label | ○ Check pipe installed at correct depth.
label | ○ Ensure all collars are free from contamination in McDougall St berm
label | Acceptance Criteria - Pipes free of debris & correctly installed
label | Verifying Document - Daily Site Diary
label | Reference: Contract Specs/Standards - D2.5, D2.7, D8.4.2
label | Inspection Point/Signature & Date - PS
checkpoint | 5.4 - Concrete Pre-Pour Inspection
label | Inspection Point: Quality Control Activity - Check dimensions of formwork match details in the Construction Drawings.
label | ○ Check pipe fitting joints are clear of concrete pour.
label | ○ Thrust blocks to be poured against good solid natural ground.
label | Acceptance Criteria - Thrust blocks against solid ground
label | Verifying Document - Daily Site Diary & Photos
label | Reference: Contract Specs/Standards - D5.1, D5.3.2, D5.7
label | Inspection Point/Signature & Date - PS, CR
checkpoint | 5.5 - Hydrant Depth
label | Inspection Point: Quality Control Activity - Confirm depth requirements have been met;
label | ○ Hydrant outlet: 200mm min. to 400mm max.
label | Acceptance Criteria - Hydrant depth verified
label | Verifying Document - Daily Site Diary
label | Reference: Contract Specs/Standards - D5.5
label | Inspection Point/Signature & Date - PS
checkpoint | 5.6 - Compaction Testing
label | Inspection Point: Quality Control Activity - Confirm trenches in paved areas are compacted to standard block by block.
label | Acceptance Criteria - Compaction confirmed
label | Verifying Document - Clegg Record Sheet
label | Reference: Contract Specs/Standards - D2.7.10
label | Inspection Point/Signature & Date - PS
checkpoint | 5.7 - Watermain Pressure Testing
label | Inspection Point: Quality Control Activity - Hydrostatic pressure test on new pipeline and fittings block by block.
label | Acceptance Criteria - Pressure test passed
label | Verifying Document - Pressure Test Record Sheet
label | Reference: Contract Specs/Standards - D2.9.1, AS/NSZ 2566.2:2002 Section 6
label | Inspection Point/Signature & Date - PS, CR
checkpoint | 5.8 - Watermain Sterilization
label | Inspection Point: Quality Control Activity - Flushing and sterilizing full length of new pipeline and fittings block by block.
label | Acceptance Criteria - Sterilization completed
label | Verifying Document - Sterilization Record Sheet
label | Reference: Contract Specs/Standards - D2.9.1, AS/NSZ 2566.2:2002 Section 6
label | Inspection Point/Signature & Date - PS, CR
checkpoint | 5.9 - As-built Information
label | Inspection Point: Quality Control Activity - Capture data for all new construction work.
label | Acceptance Criteria - Redline mark-up plan submitted
label | Verifying Document - Redline Mark-up Plan
label | Reference: Contract Specs/Standards - C1.22
label | Inspection Point/Signature & Date - PM
section | Final Inspection and Handover
checkpoint | 6.1 - Final Inspection of Works
label | Inspection Point: Quality Control Activity - Work is inspected by the authorised person and complies with the nominated specification/standards
label | Acceptance Criteria - Work inspected & complies with standards
label | Verifying Document - Practical Completion Certificate
label | Reference: Contract Specs/Standards -
label | Inspection Point/Signature & Date - PM