## zres_siteapp_NEW
Id | Type | Name | Values | Prompting Name | Postfix | Resource Id
71311430-12af-4de5-b2e1-320343a3d7c5 | checklist | ITP-002 - Watermain Construction Stage 2 - Rev A | itp | ITP-002 - Watermain Construction Stage 2
20380797-825e-43d5-b636-1e28953acadd | section | Preliminary Works
107e3d9c-f945-48ad-a893-382139576ad3 | checkpoint | 3.1 Pre-construction Photos
955645e1-125c-52ac-a36d-9f7aaf64fd68 | note | Inspection Point: Quality Control Activity - Photos of worksite including vehicle access points.
de815be8-ff5b-5bbf-8fcf-b6a74f875d15 | note | ○ Photos of any existing defects/damage.
f629ba35-c6c9-5e84-afb6-f12afe19ba50 | note | Acceptance Criteria - Coverage of whole site
b343e756-6236-534e-a04c-adde741f9cf9 | note | Verifying Document - Photos saved
487d2c77-26c6-574d-9f8c-69197b900e60 | note | Reference: Contract Specs/Standards - D1.4
aa7dcc23-975c-5d3e-90f1-e46ecef13a8e | note | Inspection Point/Signature & Date - PM
441f8f47-9e59-4e93-af48-52ea9db74b4f | checkpoint | 3.2 Verify Construction Drawings
5979cb19-48d2-5a0f-8a4a-18a2495e019b | note | Inspection Point: Quality Control Activity - Verify Construction Drawings that are in the site folder are the latest revision.
77adfc3c-637c-5532-a2de-de99b4eb0801 | note | Acceptance Criteria - Latest drawings approved
2e7272cf-1b67-5992-8aea-1c720473b1e1 | note | Verifying Document - Drawings Register
91384230-7de8-55b8-b9f0-cf3094b4e632 | note | Reference: Contract Specs/Standards -
53f92b21-b0f6-50b0-9a66-65c339b74caa | note | Inspection Point/Signature & Date - PM
92a4d361-6a90-4261-aacc-b17a70c5ba02 | checkpoint | 3.3 Road Authority Notifications
a5905a4b-3c67-5ea9-9f5c-3f49ad93a559 | note | Inspection Point: Quality Control Activity - Corridor access Permit.
0158a33e-7ce3-58a8-babd-2c00a85ada9b | note | ○ Block by block Temporary Traffic Management Plans.
c980e384-1324-5a31-ad80-c5f42c7f2909 | note | Acceptance Criteria - Permit & Traffic Plan approved
670802ca-5daf-518d-ba40-b11f61b8bba8 | note | Verifying Document - Work Access Permit & TMP
ae04fd1d-8285-5e71-9dc0-6c451b22a24a | note | Reference: Contract Specs/Standards - C1.09, D1.4
afbe1801-0461-5ff9-9968-d71d709c4667 | note | Inspection Point/Signature & Date - PM
d39f31d1-9f41-49b3-8e2e-f1d32ae48a60 | checkpoint | 3.4 Management Plan
dacc70c9-2410-5db2-bd45-66d975547e52 | note | Inspection Point: Quality Control Activity - H&S Plan
c98cf114-7fba-5cd7-9f75-05f14d1dc0c4 | note | ○ Environmental Plan
ff8ca60d-7b07-570e-837e-2ea6f5924d22 | note | ○ Quality Assurances
6ad36c2d-187f-596a-87f1-b024ccfeeffd | note | Acceptance Criteria - Plans & Safety Measures in place
d5f70aa4-3aed-5da0-b07e-f5410907778d | note | Verifying Document - H&S Plan, Method Statement
79d6f9d4-a271-5202-907c-58e7835bcb83 | note | Reference: Contract Specs/Standards - D1.3
7f636cf1-81e6-5b8d-8b3a-e415c151f5d7 | note | Inspection Point/Signature & Date - PM, CR
5d595464-2779-423b-add8-0d8127f9cada | checkpoint | 3.5 Public Notification
3a84e0b1-0335-5dc4-bb53-a8236469f1e8 | note | Inspection Point: Quality Control Activity - Notice of works to properties in the construction zone in each block
111ac031-f06c-52e2-8d36-657040eef63d | note | ○ Notification to Rubbish collection contractor.
6425c7b3-a4a7-5fc9-b4d2-348fb03ae6aa | note | ○ Project Signage
1fb132d3-92db-5038-aa91-124209dd7f89 | note | Acceptance Criteria - 48 hours prior notification
6a28c857-a4f5-59ec-8a55-c083caf0c3a7 | note | Verifying Document - Letter to residents
c926fb82-add6-5d96-9893-e1996f955a14 | note | Reference: Contract Specs/Standards - D1.10
bdbcb526-3a1e-5e5d-86ef-0a808ab8369e | note | Inspection Point/Signature & Date - PM
83d17dff-2396-439e-955c-8f1f727f65ed | checkpoint | 3.6 Shutdown/Isolation
6ea865c2-ca78-5854-8fa3-2264bf699993 | note | Inspection Point: Quality Control Activity - Shutdown/Isolation process verified in each block closure
1555c1d5-29de-5a42-a7d4-8b3739287984 | note | Acceptance Criteria - Shutdown process verified
cd7f89f3-8fdf-5085-8c83-7bb9094c8b0a | note | Verifying Document - Notification letters
ef26b893-83e8-5557-854d-c80eb7263938 | note | Reference: Contract Specs/Standards - C1.16, D2.7.8
28d7be85-39af-58e3-9302-9376a974da67 | note | Inspection Point/Signature & Date - PS
d167c212-b415-420c-a15c-45c677294de6 | checkpoint | 3.7 Construction Set Out
742868c8-23f0-5452-9b92-ba186649d8d7 | note | Inspection Point: Quality Control Activity - Correctly mark out the position of the new pipelines for construction.
9e97b2cc-ba1a-5815-b8f9-fbfc1eb1d305 | note | Acceptance Criteria - Construction Plans checked
5b2e22e1-e5ff-5dc0-99bf-61f23b16df05 | note | Verifying Document - Construction Plans
62386f7d-45bf-5fb2-8ee5-5645b5fb6848 | note | Reference: Contract Specs/Standards - D2.7.1
d58502cb-242d-55dc-b860-3551207f6eba | note | Inspection Point/Signature & Date - PS, CR
a5600e25-383f-46d4-8512-0c264c1e449f | checkpoint | 3.8 Pre-Excavation Permits
dae1eccc-c23e-53c5-a82d-0efd94bccfeb | note | Inspection Point: Quality Control Activity - Permit to excavate for the location has been endorsed by an authorised person.
4086823b-a3b0-5514-bed4-f7f9e3b60915 | note | ○ Existing service plans & locates
c1e5fd2a-aef6-51bf-8cd0-bb993a96c4c9 | note | ○ Close approach permits
e9ebe2eb-6bb3-5920-af4f-3e5f51dc6ced | note | ○ Notifiable works
c0184131-3963-58e5-89ee-4c85ee5a746b | note | Acceptance Criteria - Permit to excavate endorsed
ef5bff12-f195-5b6f-aa81-cb8850c90580 | note | Verifying Document - Ground Disturbance Permit
64acb508-1d91-553b-8bd2-2bec3032ca97 | note | Reference: Contract Specs/Standards - D1.7
7835cccc-5334-5c60-a2d5-886aa9e0b519 | note | Inspection Point/Signature & Date - PS
| signoff | HOLD POINT
abbb431d-e004-44ec-b738-fab1868140b8 | section | Incoming Goods Inspections
2aa07f2e-4aed-4158-88a0-e6abf1872ee1 | checkpoint | 4.1 Pipe & Fitting Inspections
335e2b85-3765-5d7c-823f-1a30f4f4c2cd | note | Inspection Point: Quality Control Activity - Visual check of materials delivered:
3c2f6b16-25d4-518b-a78c-50cd0381e2b9 | note | ○ Correct Material & dimensions
38ce9bbf-d35b-56d0-9094-6888dbbe0772 | note | ○ Condition & Quantity
e0aca729-1137-5fa6-a9c4-e65d8d4be14e | note | ○ Free of defects – surface abrasion, ovality, not kinked or crushed
c7813b84-576f-505d-b003-53fb30070daf | note | ○ Batch/serial numbers present
e60eb730-8b8d-5bbe-9001-2c575dd38607 | note | Acceptance Criteria - Correct material & no defects
775a2f60-1a0d-5a61-a840-33859f5f5380 | note | Verifying Document - Packing Slips
5523d66d-7eb8-57b7-8130-17f63b83eb86 | note | Reference: Contract Specs/Standards - D2.4,D3.3, D4.3, D5.3, D8.3
4815886f-d85b-584d-a8bf-54bb43596b4d | note | Inspection Point/Signature & Date - PS
18a89c7a-07fc-4278-9ab2-46bbdeed02f3 | checkpoint | 4.2 Pipe & Fitting Storage
736fc6ca-0587-58a7-aa66-1e6006900b05 | note | Inspection Point: Quality Control Activity - Stored as per manufacturers specifications including maximum height limits and safely chocked in place.
88679b02-09b0-5f6d-85d2-86abe8c910f1 | note | ○ All pipes are end capped.
ace5e548-9b68-55f8-acb6-13682245a6d3 | note | ○ No scoring of pipe more than 10% of thickness.
0f1df64d-4495-5578-a941-f201cb9bd702 | note | ○ No damage to epoxy coating on Ductile fittings.
1dbf0fff-4157-5283-af1b-f1fa245cb0fd | note | Acceptance Criteria - Stored as per manufacturer
c2c2afc7-5301-5e5c-ba67-ba552d116bc1 | note | Verifying Document - Manufacturer’s Storage Instructions
99bbba7a-beec-5223-939d-15034191d36d | note | Reference: Contract Specs/Standards -
1dbd7e86-bf3c-5e32-8b08-073e38069992 | note | Inspection Point/Signature & Date - PS, CR
| signoff | HOLD POINT
1f6a3545-531a-431b-8950-db0056c6a96e | section | Construction Inspections
5b9fc0f7-1004-4407-be8c-24b464b7f09e | checkpoint | 5.1 Trench Excavation
02e391fc-3a18-522d-9c19-e2a03e270cfb | note | Inspection Point: Quality Control Activity - Trench width to be sufficient to safely lay the pipe (including shoring if required) and compact the side support of the new pipe. Bedding details below;
a6f490ee-48df-5ce7-ad7c-e1ea3aa3e379 | note | ○ Sufficient room to enable the pipe, joint, bed, haunch or surround shown in the drawings to be accommodated.
eec54b15-5ecd-5436-96af-7f3f1ec2feb7 | note | ○ Trench depth to enable pipe to be laid with the designed cover as shown on construction plans.
8fd021a9-e8d2-5b4c-8b4b-5843892fc6d1 | note | ○ If trench bottom to be suitable to compact pipe bedding as support pipe.
fc3f41ae-94b6-572c-ac89-2a9ef6fb22bf | note | Acceptance Criteria - Trench dimensions correct
e3b19d68-be79-52b1-b552-b4069f08f057 | note | Verifying Document - Daily Site Diary
84a404dc-63b4-5583-b4db-f3add2e91694 | note | Reference: Contract Specs/Standards - D2.6, D2.7
5aa888e2-14d6-582f-9a52-d9c849c2397e | note | Inspection Point/Signature & Date - PS
27edf7a6-5c6f-40e4-b0c0-9ab61a806878 | checkpoint | 5.2 Encountered Services
da1255de-facf-5b78-9de0-40b88d5693d6 | note | Inspection Point: Quality Control Activity - Block by block ensure existing live services are not unnecessarily damaged by works.
5fc0b366-4852-5bfe-a581-cba57122ba03 | note | ○ Repair any services that are temporarily removed during construction.
c6c5167f-c5f2-5998-b8d3-01f5f3e9341c | note | ○ Record any services found.
0631e0d3-22a9-5d7c-8b37-c6cbd46c7c91 | note | Acceptance Criteria - Existing services not damaged
81f412b2-a38d-50f2-a598-84775c34f384 | note | Verifying Document - Encountered Services Record
90c9acea-6aa9-5d0a-b22b-e74a722eebd8 | note | Reference: Contract Specs/Standards - D1.7, D2.7.7
7d0df532-6775-5e02-87ef-5933b5113c19 | note | Inspection Point/Signature & Date - PS
0bb6eb81-7e4a-451f-830e-1b4ed2ca3ea2 | checkpoint | 5.3 Pipe Installation
e9a5264d-e34d-57c2-b251-70577ea28002 | note | Inspection Point: Quality Control Activity - Interior of each pipe visually inspected to ensure free of debris.
4de7eba6-7a52-508a-8f6f-3da7ba17c6ad | note | ○ Re-cap end of pipe after installation.
9fcd0740-534d-500d-8189-e0970be0fe0f | note | ○ Check pipe installed at correct depth.
97372ff6-7a61-5b54-b317-dc368cef403b | note | ○ Ensure all collars are free from contamination in McDougall St berm
d141a6e9-ce08-571e-8cfd-8a4080f2f31b | note | Acceptance Criteria - Pipes free of debris & correctly installed
6c48859f-43ee-519f-b185-e2757b35f5ef | note | Verifying Document - Daily Site Diary
d6e34e20-3287-5bb8-accf-914843f1e5ed | note | Reference: Contract Specs/Standards - D2.5, D2.7, D8.4.2
c344ad27-9a7c-5088-8578-ce9de1f06115 | note | Inspection Point/Signature & Date - PS
315ca360-db4e-4b0f-b047-bcd13a88803d | checkpoint | 5.4 Concrete Pre-Pour Inspection
a0c3ca9d-7c53-5f00-a910-1efc9d53070f | note | Inspection Point: Quality Control Activity - Check dimensions of formwork match details in the Construction Drawings.
63a3685f-631f-50f2-b45b-5b550dd42985 | note | ○ Check pipe fitting joints are clear of concrete pour.
23788df5-5f26-5f32-a93c-2b6f87bf050f | note | ○ Thrust blocks to be poured against good solid natural ground.
2e389bbc-ca69-56cc-991e-0c7ae5298cfb | note | Acceptance Criteria - Thrust blocks against solid ground
4630ea02-6452-5ef8-9df0-b7baf484a9ae | note | Verifying Document - Daily Site Diary & Photos
2a52135d-b44a-5d64-8c2f-594fcb8d9444 | note | Reference: Contract Specs/Standards - D5.1, D5.3.2, D5.7
270f8374-94d2-5ff4-afe3-a9f4d98bb457 | note | Inspection Point/Signature & Date - PS, CR
02e5fe15-a3d0-4117-9c59-df286de87b71 | checkpoint | 5.5 Hydrant Depth
c166f8ac-68a4-56d5-a714-45a77c232876 | note | Inspection Point: Quality Control Activity - Confirm depth requirements have been met;
2f2ace55-1dbf-557c-880b-7b6a3dd25264 | note | ○ Hydrant outlet: 200mm min. to 400mm max.
285e10aa-95d7-51d9-ab64-3b2072cdb2d5 | note | Acceptance Criteria - Hydrant depth verified
9803aeb2-9d90-54ba-9e49-df36b5629658 | note | Verifying Document - Daily Site Diary
f8c94654-15c9-51e9-8452-342e59ecae6e | note | Reference: Contract Specs/Standards - D5.5
cc256614-c42e-5f6e-a39f-f68a89b87155 | note | Inspection Point/Signature & Date - PS
a0e3fce6-d131-4d47-b2fa-1afd64dedf22 | checkpoint | 5.6 Compaction Testing
ba0f25db-c515-54bf-af10-241ef05a2184 | note | Inspection Point: Quality Control Activity - Confirm trenches in paved areas are compacted to standard block by block.
49e7f8fd-7c6b-5d23-b61b-854926d2d227 | note | Acceptance Criteria - Compaction confirmed
22f4308c-0c3d-5079-b554-738af731d09f | note | Verifying Document - Clegg Record Sheet
ea3ff20d-d289-5332-88c3-7d7ac37a937a | note | Reference: Contract Specs/Standards - D2.7.10
bb591b35-fe0b-530a-8cb7-36e77516390e | note | Inspection Point/Signature & Date - PS
cdecfdb6-ad87-453e-b692-8fb65eb5cbe7 | checkpoint | 5.7 Watermain Pressure Testing
1da5f833-284a-5b18-99a9-331354fad608 | note | Inspection Point: Quality Control Activity - Hydrostatic pressure test on new pipeline and fittings block by block.
2f9a2668-68c2-5f33-8c5e-ec33a157d16e | note | Acceptance Criteria - Pressure test passed
36849462-809a-58b1-a71f-40568e648c95 | note | Verifying Document - Pressure Test Record Sheet
a57df2e3-9168-58b3-8e23-04a24658c806 | note | Reference: Contract Specs/Standards - D2.9.1, AS/NSZ 2566.2:2002 Section 6
2d130f10-37f0-55a1-8d72-a460b1f28c32 | note | Inspection Point/Signature & Date - PS, CR
a1e1175c-838a-44d4-97e2-105d86a88295 | checkpoint | 5.8 Watermain Sterilization
ce10429c-a3e0-5c3c-b478-43bc65ee371b | note | Inspection Point: Quality Control Activity - Flushing and sterilizing full length of new pipeline and fittings block by block.
14828d25-390c-5376-8cc6-48d3ee750694 | note | Acceptance Criteria - Sterilization completed
72845af4-3a77-57b0-bfd3-8c8b00ad194a | note | Verifying Document - Sterilization Record Sheet
c67f69b9-5827-576d-aa4b-e05ef53cf735 | note | Reference: Contract Specs/Standards - D2.9.1, AS/NSZ 2566.2:2002 Section 6
99631707-3d31-5b31-aff4-efb8e8c21979 | note | Inspection Point/Signature & Date - PS, CR
ddf7462a-b76e-41eb-a36d-0de8b8dd2a87 | checkpoint | 5.9 As-built Information
517e67db-4033-58c1-a6ca-d3362f98ca30 | note | Inspection Point: Quality Control Activity - Capture data for all new construction work.
ba450391-5c8a-5c55-b1c4-c22f0833b96c | note | Acceptance Criteria - Redline mark-up plan submitted
3eb797e2-7275-5590-8fac-676aa04c793f | note | Verifying Document - Redline Mark-up Plan
b2cc15a1-1e88-5f06-9c50-d2d2827d97a5 | note | Reference: Contract Specs/Standards - C1.22
3c06f156-3b4e-51b2-91ab-48d5a7624304 | note | Inspection Point/Signature & Date - PM
| signoff | HOLD POINT
8b2fb51e-3dea-4864-85cf-ea6c1f2099ae | section | Final Inspection and Handover
e1185f06-97ee-41c3-ba68-9fa87ec8f197 | checkpoint | 6.1 Final Inspection of Works
937e6486-743d-5157-8e7e-d97207a69798 | note | Inspection Point: Quality Control Activity - Work is inspected by the authorised person and complies with the nominated specification/standards
17149ea4-e39d-5a08-9b34-a5a55b8544b8 | note | Acceptance Criteria - Work inspected & complies with standards
69020570-efe6-5843-a2ad-9a102698555a | note | Verifying Document - Practical Completion Certificate
b28f2ad8-0f63-5340-9f55-310a0e29c35a | note | Reference: Contract Specs/Standards -
5422ff6f-c5f8-5de4-8a22-f168bf4f557c | note | Inspection Point/Signature & Date - PM
| signoff | HOLD POINT