## matrix
Matrix Name | Dimension | Name | Type / Data Field | Tag 1 | Tag 2
Overall Progress
| Scope |  |  | qa
Rows
|  | Civil | dynamic | qa | civil
|  | Hydraulics - New | dynamic | qa | new | hydraulics
|  | Hydraulics - Thermostatic Mixing Valves | dynamic | qa | hydraulics | thermostatic mixing valves
|  | Decommissioning / Demolition | dynamic | qa | decommissioning / demolition
Columns
|  | QA |  | qa
Cold Water BG
| Scope |  |  | qa
Rows
|  | Hydraulics - New | grouping | hydraulics - new
|  | Level 01 - Zone 5 - Pump Line BG (PL) - Pump Line from Sump Pit 1 |  | QA | Hydraulics | New | Level 01 | Zone 5 | Pump Line BG (PL) | Pump Line from Sump Pit 1
|  | Level 01 - Zone 5 - Pump Line BG (PL) - Pump Line from Sump Pit 2 |  | QA | Hydraulics | New | Level 01 | Zone 5 | Pump Line BG (PL) | Pump Line from Sump Pit 2
|  | Level 01 - Zone 5 - Pump Line BG (PL) - Pump Line from Sump Pit 3 |  | QA | Hydraulics | New | Level 01 | Zone 5 | Pump Line BG (PL) | Pump Line from Sump Pit 3
|  | Level 01 - Zone 5 - Cold Water BG (CW) |  | QA | Hydraulics | New | Level 01 | Zone 5 | Cold Water BG (CW)
|  | Level 05 - Zone 4 - Cold Water BG (CW) - Grid (ZB-ZC, Z3-Z6) |  | QA | Hydraulics | New | Level 05 | Zone 4 | Cold Water BG (CW) | Grid (ZB-ZC, Z3-Z6)
|  | Level 05 - Zone 4 - Cold Water BG (CW) - Grid (AB-ZB, Z3-Z6) |  | QA | Hydraulics | New | Level 05 | Zone 4 | Cold Water BG (CW) | Grid (AB-ZB, Z3-Z6)
|  | Level 05 - Zone 4 - Non-Potable Cold Water BG (NPCW) |  | QA | Hydraulics | New | Level 05 | Zone 4 | Non-Potable Cold Water BG (NPCW)
|  | Level 05 - Zone 5 - Pump Line AG (PL) |  | QA | Hydraulics | New | Level 05 | Zone 5 | Pump Line AG (PL)
|  | Level 05 - Zone 5 - 150mm Cold Water BG (CW) - Grid (ZB-ZC, Z3-Z1) |  | QA | Hydraulics | New | Level 05 | Zone 5 | 150mm Cold Water BG (CW) | Grid (ZB-ZC, Z3-Z1)
|  | Level 05 - Zone 5 - 150mm Cold Water BG (CW) - Grid (ZB-ZC, Z1-02) |  | QA | Hydraulics | New | Level 05 | Zone 5 | 150mm Cold Water BG (CW) | Grid (ZB-ZC, Z1-02)
|  | Level 05 - Zone 5 - 150mm Cold Water BG (CW) - Grid (ZB-ZC, 02-04) |  | QA | Hydraulics | New | Level 05 | Zone 5 | 150mm Cold Water BG (CW) | Grid (ZB-ZC, 02-04)
|  | Level 05 - Zone 5 - 150mm Cold Water BG (CW) - Grid (ZB-ZC, 04-06) |  | QA | Hydraulics | New | Level 05 | Zone 5 | 150mm Cold Water BG (CW) | Grid (ZB-ZC, 04-06)
|  | Level 05 - Zone 5 - 150mm Cold Water BG (CW) - Grid (ZB-ZC, 06-08) |  | QA | Hydraulics | New | Level 05 | Zone 5 | 150mm Cold Water BG (CW) | Grid (ZB-ZC, 06-08)
|  | Level 05 - Zone 5 - 150mm Cold Water BG (CW) - Grid (ZB-ZD, 08-09) |  | QA | Hydraulics | New | Level 05 | Zone 5 | 150mm Cold Water BG (CW) | Grid (ZB-ZD, 08-09)
|  | Level 05 - Zone 5 - 150mm Cold Water BG (CW) - Grid (ZB-ZC, 02-04) |  | QA | Hydraulics | New | Level 05 | Zone 5 | 150mm Cold Water BG (CW) | Grid (ZB-ZC, 02-04)
|  | Level 05 - Zone 5 - 150mm Cold Water BG (CW) - Grid (AA-ZA, Z3-Z1) |  | QA | Hydraulics | New | Level 05 | Zone 5 | 150mm Cold Water BG (CW) | Grid (AA-ZA, Z3-Z1)
|  | Level 05 - Zone 5 - 150mm Cold Water BG (CW) - Grid (AA-ZA, Z1-02) |  | QA | Hydraulics | New | Level 05 | Zone 5 | 150mm Cold Water BG (CW) | Grid (AA-ZA, Z1-02)
|  | Level 05 - Zone 5 - 150mm Cold Water BG (CW) - Grid (AA-ZA, 02-03) |  | QA | Hydraulics | New | Level 05 | Zone 5 | 150mm Cold Water BG (CW) | Grid (AA-ZA, 02-03)
|  | Level 05 - Zone 5 - 150mm Cold Water BG (CW) - Grid (ZA-ZB, 02-03) |  | QA | Hydraulics | New | Level 05 | Zone 5 | 150mm Cold Water BG (CW) | Grid (ZA-ZB, 02-03)
|  | Level 05 - Zone 5 - 150mm Cold Water BG (CW) - Grid (ZB-ZC, 02-04) |  | QA | Hydraulics | New | Level 05 | Zone 5 | 150mm Cold Water BG (CW) | Grid (ZB-ZC, 02-04)
|  | Level 05 - Zone 5 - 150mm Cold Water BG (CW) - Grid (ZB-ZC, 04-06) |  | QA | Hydraulics | New | Level 05 | Zone 5 | 150mm Cold Water BG (CW) | Grid (ZB-ZC, 04-06)
|  | Level 05 - Zone 5 - 150mm Cold Water BG (CW) - Grid (ZB-ZC, 06-08) |  | QA | Hydraulics | New | Level 05 | Zone 5 | 150mm Cold Water BG (CW) | Grid (ZB-ZC, 06-08)
|  | Level 05 - Zone 5 - 150mm Cold Water BG (CW) - Grid (ZB-ZC, 08-09) |  | QA | Hydraulics | New | Level 05 | Zone 5 | 150mm Cold Water BG (CW) | Grid (ZB-ZC, 08-09)
|  | Level 05 - Zone 5 - 100mm Cold Water BG (CW) - Grid (AA-ZA, 02-04) |  | QA | Hydraulics | New | Level 05 | Zone 5 | 100mm Cold Water BG (CW) | Grid (AA-ZA, 02-04)
|  | Level 05 - Zone 5 - 100mm Cold Water BG (CW) - Grid (AA-ZA, 04-07) |  | QA | Hydraulics | New | Level 05 | Zone 5 | 100mm Cold Water BG (CW) | Grid (AA-ZA, 04-07)
|  | Level 05 - Zone 5 - 50mm Cold Water BG (CW) - Grid (ZB-ZC, 02-03) |  | QA | Hydraulics | New | Level 05 | Zone 5 | 50mm Cold Water BG (CW) | Grid (ZB-ZC, 02-03)
|  | Level 05 - Zone 5 - 50mm Cold Water BG (CW) - Grid (ZA-ZB, 02-03) |  | QA | Hydraulics | New | Level 05 | Zone 5 | 50mm Cold Water BG (CW) | Grid (ZA-ZB, 02-03)
|  | Level 05 - Zone 5 - 50mm Cold Water BG (CW) - Grid (AA-ZA, 02-03) |  | QA | Hydraulics | New | Level 05 | Zone 5 | 50mm Cold Water BG (CW) | Grid (AA-ZA, 02-03)
|  | Level 05 - Zone 5 - 50mm Cold Water BG (CW) - Grid (AA-ZA, 03-05) |  | QA | Hydraulics | New | Level 05 | Zone 5 | 50mm Cold Water BG (CW) | Grid (AA-ZA, 03-05)
|  | Level 05 - Zone 5 - 50mm Cold Water BG (CW) - Grid (AA-ZA, 05-07) |  | QA | Hydraulics | New | Level 05 | Zone 5 | 50mm Cold Water BG (CW) | Grid (AA-ZA, 05-07)
|  | Level 05 - Zone 5 - 20mm Cold Water BG (CW) - Grid (AA-ZA, 06-08) |  | QA | Hydraulics | New | Level 05 | Zone 5 | 20mm Cold Water BG (CW) | Grid (AA-ZA, 06-08)
|  | Level 05 - Zone 5 - 20mm Cold Water BG (CW) - Grid (AA-ZA, 08-09) |  | QA | Hydraulics | New | Level 05 | Zone 5 | 20mm Cold Water BG (CW) | Grid (AA-ZA, 08-09)
|  | Level 05 - Zone 5 - 100mm Non-Potable Cold Water BG (NPCW) - Grid (ZB-ZC, Z3-Z1) |  | QA | Hydraulics | New | Level 05 | Zone 5 | 100mm Non-Potable Cold Water BG (NPCW) | Grid (ZB-ZC, Z3-Z1)
|  | Level 05 - Zone 5 - 100mm Non-Potable Cold Water BG (NPCW) - Grid (ZB-ZC, Z1-02) |  | QA | Hydraulics | New | Level 05 | Zone 5 | 100mm Non-Potable Cold Water BG (NPCW) | Grid (ZB-ZC, Z1-02)
|  | Level 05 - Zone 5 - 100mm Non-Potable Cold Water BG (NPCW) - Grid (ZB-ZC, 02-04) |  | QA | Hydraulics | New | Level 05 | Zone 5 | 100mm Non-Potable Cold Water BG (NPCW) | Grid (ZB-ZC, 02-04)
|  | Level 05 - Zone 5 - 100mm Non-Potable Cold Water BG (NPCW) - Grid (ZB-ZC, 04-06) |  | QA | Hydraulics | New | Level 05 | Zone 5 | 100mm Non-Potable Cold Water BG (NPCW) | Grid (ZB-ZC, 04-06)
|  | Level 05 - Zone 5 - 100mm Non-Potable Cold Water BG (NPCW) - Grid (ZB-ZC, 06-08) |  | QA | Hydraulics | New | Level 05 | Zone 5 | 100mm Non-Potable Cold Water BG (NPCW) | Grid (ZB-ZC, 06-08)
|  | Level 05 - Zone 5 - 100mm Non-Potable Cold Water BG (NPCW) - Grid (ZB-ZC, 08-09) |  | QA | Hydraulics | New | Level 05 | Zone 5 | 100mm Non-Potable Cold Water BG (NPCW) | Grid (ZB-ZC, 08-09)
|  | Level 05 - Zone 5 - 100mm Non-Potable Cold Water BG (NPCW) - Grid (ZA-ZB, 02-03) |  | QA | Hydraulics | New | Level 05 | Zone 5 | 100mm Non-Potable Cold Water BG (NPCW) | Grid (ZA-ZB, 02-03)
|  | Level 05 - Zone 5 - 100mm Non-Potable Cold Water BG (NPCW) - Grid (AA-ZA, 02-03) |  | QA | Hydraulics | New | Level 05 | Zone 5 | 100mm Non-Potable Cold Water BG (NPCW) | Grid (AA-ZA, 02-03)
|  | Level 05 - Zone 5 - 100mm Non-Potable Cold Water BG (NPCW) - Grid (AA-ZA, 02-04) |  | QA | Hydraulics | New | Level 05 | Zone 5 | 100mm Non-Potable Cold Water BG (NPCW) | Grid (AA-ZA, 02-04)
|  | Level 05 - Zone 5 - 100mm Non-Potable Cold Water BG (NPCW) - Grid (AA-ZA, 04-07) |  | QA | Hydraulics | New | Level 05 | Zone 5 | 100mm Non-Potable Cold Water BG (NPCW) | Grid (AA-ZA, 04-07)
Columns
|  | Employee trained for task & reviewed installation instructions |  | employee trained for task and reviewed installation instructions (product qr code / manufacturer's website / instruction manual)
|  | Notify & gain permit from principal contractor/client for inspection |  | notify and gain permit from principal contractor / client for inspection (hold point)
|  | Setout & alignment as per drawing |  | setout & alignment as per drawing (include revision below)
|  | Drawing & revision number(s) | Drawing & revision number(s) | setout & alignment as per drawing (include revision below)
|  | Correct material as per sample register |  | correct material as per sample register
|  | Bedding material installed correctly |  | bedding material installed correctly
|  | Fittings & joints correctly installed to manufacturer's requirements |  | fittings & joints correctly installed to manufacturer's requirements
|  | Satisfactory welding/pressing of copper pipe |  | satisfactory welding/pressing of copper pipe
|  | Witness marks visible |  | witness marks visible
|  | Pipework layed correctly & to AS 3500 |  | pipework layed correctly and to as 3500
|  | Inspection & Testing Prior to Concealment to AS 3500 |  | inspection and testing prior to concealment to as 3500
|  | Seal open ends with caps & high light to avoid damage |  | seal open ends with caps & high light to avoid damage
|  | Identification of services via I.D tape |  | identification of services via i.d tape
|  | Backfill & compaction to specification in 300mm layers |  | backfill & compaction to specification in 300mm layers
|  | Final sign off |  | final sign off - pass when satisfied to proceed (any issues please comment & add photos below)
|  | Area clean | Area clean | final sign off - pass when satisfied to proceed (any issues please comment & add photos below)
Cold Water Checklist
| Scope |  |  | qa
Rows
|  | Hydraulics - New | grouping | hydraulics - new
|  | Level 02 - Zone 5 - Cold Water AG (CW) |  | QA | Hydraulics | New | Level 02 | Zone 5 | Cold Water AG (CW)
|  | Level 02 - Zone 6 - Cold Water AG (CW) |  | QA | Hydraulics | New | Level 02 | Zone 6 | Cold Water AG (CW)
|  | Level 02 - Zone 6 - Pump Line & Vent (PL) |  | QA | Hydraulics | New | Level 02 | Zone 6 | Pump Line & Vent (PL)
|  | Level 03 - Zone 1 - Pump Line (PL) |  | QA | Hydraulics | New | Level 03 | Zone 1 | Pump Line (PL)
|  | Level 03 - Zone 1 - Grid (AD-AE, 6-7) - Cold Water AG (CW) |  | QA | Hydraulics | New | Level 03 | Zone 1 | Grid (AD-AE, 6-7) | Cold Water AG (CW)
|  | Level 03 - Zone 1 - Grid (AD-AE, 7-8) - Cold Water AG (CW) |  | QA | Hydraulics | New | Level 03 | Zone 1 | Grid (AD-AE, 7-8) | Cold Water AG (CW)
|  | Level 03 - Zone 2 - Pump Line (PL) |  | QA | Hydraulics | New | Level 03 | Zone 2 | Pump Line (PL)
|  | Level 04 - Zone 1 - Pump Line (PL) |  | QA | Hydraulics | New | Level 04 | Zone 1 | Pump Line (PL)
|  | Level 04 - Zone 1 - Cold Water AG (CW) |  | QA | Hydraulics | New | Level 04 | Zone 1 | Cold Water AG (CW)
|  | Level 04 - Zone 5 - Grid (AA-ZA, 4-5) - Pump Line 1 (PL) |  | QA | Hydraulics | New | Level 04 | Zone 5 | Grid (AA-ZA, 4-5) | Pump Line 1 (PL)
|  | Level 04 - Zone 5 - Grid (AA-ZA, 4-5) - Pump Line 2 (PL) |  | QA | Hydraulics | New | Level 04 | Zone 5 | Grid (AA-ZA, 4-5) | Pump Line 2 (PL)
|  | Level 04 - Zone 6 - Cold Water AG (CW) |  | QA | Hydraulics | New | Level 04 | Zone 6 | Cold Water AG (CW)
|  | Level 05 - Zone 1 - Grid (AA-AD, 6-7) - Pump Line (PL) |  | QA | Hydraulics | New | Level 05 | Zone 1 | Grid (AA-AD, 6-7) | Pump Line (PL)
|  | Level 05 - Zone 1 - Grid (AC-AD, 7-8) - Pump Line (PL) |  | QA | Hydraulics | New | Level 05 | Zone 1 | Grid (AC-AD, 7-8) | Pump Line (PL)
|  | Level 05 - Zone 2 - Cold Water AG (CW) |  | QA | Hydraulics | New | Level 05 | Zone 2 | Cold Water AG (CW)
|  | Level 05 - Zone 6 - 150mm Cold Water AG (CW) - Grid (ZC-ZD, 09-11) |  | QA | Hydraulics | New | Level 05 | Zone 6 | 150mm Cold Water AG (CW) | Grid (ZC-ZD, 09-11)
|  | Level 05 - Zone 6 - 150mm Cold Water AG (CW) - Grid (ZB-ZD, 11-12) |  | QA | Hydraulics | New | Level 05 | Zone 6 | 150mm Cold Water AG (CW) | Grid (ZB-ZD, 11-12)
|  | Level 05 - Zone 6 - 150mm Cold Water AG (CW) - Grid (ZB-ZC, 09-11) |  | QA | Hydraulics | New | Level 05 | Zone 6 | 150mm Cold Water AG (CW) | Grid (ZB-ZC, 09-11)
|  | Level 05 - Zone 6 - 100mm Non-Potable Cold Water AG (NPCW) - Grid (ZB-ZD, 11-12) |  | QA | Hydraulics | New | Level 05 | Zone 6 | 100mm Non-Potable Cold Water AG (NPCW) | Grid (ZB-ZD, 11-12)
|  | Level 05 - Zone 6 - 100mm Non-Potable Cold Water AG (NPCW) - Grid (ZB-ZC, 09-11) |  | QA | Hydraulics | New | Level 05 | Zone 6 | 100mm Non-Potable Cold Water AG (NPCW) | Grid (ZB-ZC, 09-11)
|  | Level 05A - Zone 1 - Pump Line AG (PL) |  | QA | Hydraulics | New | Level 05A | Zone 1 | Pump Line AG (PL)
|  | Level 05A - Zone 1 - Cold Water AG (CW) |  | QA | Hydraulics | New | Level 05A | Zone 1 | Cold Water AG (CW)
|  | Level 05A - Zone 1 - Non-Potable Cold Water AG (NPCW) |  | QA | Hydraulics | New | Level 05A | Zone 1 | Non-Potable Cold Water AG (NPCW)
|  | Level 05A - Zone 2 - Pump Line AG (PL) |  | QA | Hydraulics | New | Level 05A | Zone 2 | Pump Line AG (PL)
|  | Level 05A - Zone 2 - Cold Water AG (CW) |  | QA | Hydraulics | New | Level 05A | Zone 2 | Cold Water AG (CW)
|  | Level 05A - Zone 6 - Cold Water AG (CW) |  | QA | Hydraulics | New | Level 05A | Zone 6 | Cold Water AG (CW)
|  | Level 05A - Zone 6 - Non-Potable Cold Water AG (NPCW) |  | QA | Hydraulics | New | Level 05A | Zone 6 | Non-Potable Cold Water AG (NPCW)
|  | Level 06 - Zone 2 - Cold Water AG (CW) |  | QA | Hydraulics | New | Level 06 | Zone 2 | Cold Water AG (CW)
|  | Level 06 - Zone 5 - Cold Water AG (CW) |  | QA | Hydraulics | New | Level 06 | Zone 5 | Cold Water AG (CW)
|  | Level 06 - Zone 6 - Cold Water AG (CW) |  | QA | Hydraulics | New | Level 06 | Zone 6 | Cold Water AG (CW)
|  | Level 07 - Zone 2 - Cold Water AG (CW) |  | QA | Hydraulics | New | Level 07 | Zone 2 | Cold Water AG (CW)
|  | Level 10 - Zone 2 - Cold Water AG (CW) |  | QA | Hydraulics | New | Level 10 | Zone 2 | Cold Water AG (CW)
Columns
|  | Employee trained for task & reviewed installation instructions |  | employee trained for task and reviewed installation instructions (product qr code / manufacturer's website / instruction manual)
|  | Notify & gain permit from principal contractor/client for inspection |  | notify and gain permit from principal contractor / client for inspection (hold point)
|  | Setout & alignment as per drawing |  | setout & alignment as per drawing (include revision below)
|  | Drawing & revision number(s) | Drawing & revision number(s) | setout & alignment as per drawing (include revision below)
|  | Material type (as per sample submission) |  | material type (as per sample submission)
|  | Pipework fittings, bends, joints etc (as per AS 3500.1 section 2.6) |  | pipework fittings, bends, joints etc (as per as 3500.1 section 2.6)
|  | Welding/pressfit/push fit (as per AS 3500.1) |  | welding / pressfit / push fit (as per as 3500.1)
|  | Support & fixings (acoustic/seismic/water hammer) |  | support & fixings (acoustic / seismic / water hammer)
|  | Pipework installation (as per AS 3500.1) |  | pipework installation (as per as 3500.1)
|  | Check no cross connection |  | check no cross connection
|  | Pressure test (1500kpa pressure test) |  | pressure test (1500kpa pressure test)
|  | 3rd Party Inspection |  | 3rd party inspection (including the below as applicable)
|  | Name | Name | 3rd party inspection (including the below as applicable)
|  | Company | Company | 3rd party inspection (including the below as applicable)
|  | Final sign off |  | final sign off - pass when satisfied to proceed (any issues please comment & add photos below)
|  | Area clean | Area clean | final sign off - pass when satisfied to proceed (any issues please comment & add photos below)
Commissioning Pump / Macerator Station
| Scope |  |  | qa
Rows
|  | Hydraulics - New | grouping | hydraulics - new
|  | Level 01 - Zone 1 - Pump Station - Commissioning Pump / Macerator Station |  | QA | Hydraulics | New | Level 01 | Zone 1 | Pump Station | Commissioning Pump / Macerator Station
|  | Level 02 - Zone 2 - Grid (AA-AD, 14-16) - Pump Station - Commissioning Pump / Macerator Station |  | QA | Hydraulics | New | Level 02 | Zone 2 | Grid (AA-AD, 14-16) | Pump Station | Commissioning Pump / Macerator Station
|  | Level 02 - Zone 6 - Pump Station (ZA-ZB, 14-15) - Commissioning Pump / Macerator Station |  | QA | Hydraulics | New | Level 02 | Zone 6 | Pump Station (ZA-ZB, 14-15) | Commissioning Pump / Macerator Station
Columns
|  | Employee trained for task & reviewed installation instructions |  | employee trained for task and reviewed installation instructions (product qr code / manufacturer's website / instruction manual)
|  | Condition as when it was installed (report any changes) |  | condition as when it was installed (report any changes)
|  | Control panel installed |  | control panel installed
|  | Electrical wiring connected between pumps, controller & level sensing system installed correctly |  | electrical wiring connected between pumps, controller & level sensing system installed correctly
|  | Connected to BMS |  | connected to bms
|  | Connected to power supply |  | connected to power supply
|  | BMS faults in working order |  | bms faults in working order (specify faults)
|  | High level alarm in working order |  | high level alarm in working order
|  | Supplier commissioning sheet |  | supplier commissioning sheet
|  | Area clean | Area clean | supplier commissioning sheet
Decommissioning / Demolition
| Scope |  |  | qa | decommissioning / demolition
Rows
|  | Level 01 | dynamic | QA | Decommissioning / Demolition | Level 01
|  | Level 02 | dynamic | QA | Decommissioning / Demolition | Level 02
|  | Level 03 | dynamic | QA | Decommissioning / Demolition | Level 03
|  | Level 05 | dynamic | QA | Decommissioning / Demolition | Level 05
|  | Level 07 | dynamic | QA | Decommissioning / Demolition | Level 07
Columns
|  | Employee trained for task |  | employee trained for task
|  | Drawing & revision number(s) | Drawing & revision number(s) | employee trained for task
|  | Notify & gain permit from principal contractor/client for inspection |  | notify and gain permit from principal contractor / client for inspection (hold point)
|  | Service/object to be decommissioned/demolished located |  | service / object to be decommissioned / demolished located
|  | Identify & locate any dependant & affected areas/stakeholders/items |  | identify and locate any dependant and affected areas/stakeholders/items
|  | Locate & identify any hazards that may occur when decommissioning/demolishing |  | locate and identify any hazards that may occur when decommissioning / demolishing
|  | Service/object locked out for decommissioning/demolition |  | service / object locked out for decommissioning / demolition
|  | Service/object isolated & ready for safe decommissioning/demolition |  | service / object isolated and ready for safe decommissioning / demolition
|  | Service/object isolated safely decommissioned/demolished |  | service / object isolated safely decommissioned / demolished (testing if applicable)
|  | Clean |  | clean
|  | Final sign off |  | final sign off - pass when satisfied to proceed (any issues please comment & add photos below)
Fire Collars
| Scope |  |  | qa
Rows
|  | Hydraulics - New | grouping | hydraulics - new
|  | Level 02 - Zone 1 |  | QA | Hydraulics | New | Level 02 | Zone 1 | Fire Collars
|  | Level 02 - Zone 2 |  | QA | Hydraulics | New | Level 02 | Zone 2 | Fire Collars
|  | Level 02 - Zone 3 |  | QA | Hydraulics | New | Level 02 | Zone 3 | Fire Collars
|  | Level 03 - Zone 1 |  | QA | Hydraulics | New | Level 03 | Zone 1 | Fire Collars
|  | Level 03 - Zone 2 |  | QA | Hydraulics | New | Level 03 | Zone 2 | Fire Collars
|  | Level 03 - Zone 5 |  | QA | Hydraulics | New | Level 03 | Zone 5 | Fire Collars
|  | Level 03 - Zone 6 |  | QA | Hydraulics | New | Level 03 | Zone 6 | Fire Collars
|  | Level 04 - Zone 1 |  | QA | Hydraulics | New | Level 04 | Zone 1 | Fire Collars
|  | Level 04 - Zone 2 |  | QA | Hydraulics | New | Level 04 | Zone 2 | Fire Collars
|  | Level 04 - Zone 5 |  | QA | Hydraulics | New | Level 04 | Zone 5 | Fire Collars
|  | Level 05 - Zone 1 |  | QA | Hydraulics | New | Level 05 | Zone 1 | Fire Collars
|  | Level 05 - Zone 2 |  | QA | Hydraulics | New | Level 05 | Zone 2 | Fire Collars
|  | Level 05 - Zone 6 |  | QA | Hydraulics | New | Level 05 | Zone 6 | Fire Collars
|  | Level 05A - Zone 1 |  | QA | Hydraulics | New | Level 05A | Zone 1 | Fire Collars
|  | Level 05A - Zone 2 |  | QA | Hydraulics | New | Level 05A | Zone 2 | Fire Collars
|  | Level 05A - Zone 5 |  | QA | Hydraulics | New | Level 05A | Zone 5 | Fire Collars
|  | Level 05A - Zone 6 |  | QA | Hydraulics | New | Level 05A | Zone 6 | Fire Collars
|  | Level 06 - Zone 1 |  | QA | Hydraulics | New | Level 06 | Zone 1 | Fire Collars
|  | Level 06 - Zone 2 |  | QA | Hydraulics | New | Level 06 | Zone 2 | Fire Collars
|  | Level 06 - Zone 4 |  | QA | Hydraulics | New | Level 06 | Zone 4 | Fire Collars
|  | Level 06 - Zone 5 |  | QA | Hydraulics | New | Level 06 | Zone 5 | Fire Collars
|  | Level 06 - Zone 6 |  | QA | Hydraulics | New | Level 06 | Zone 6 | Fire Collars
|  | Level 07 - Zone 1 |  | QA | Hydraulics | New | Level 07 | Zone 1 | Fire Collars
|  | Level 07 - Zone 2 |  | QA | Hydraulics | New | Level 07 | Zone 2 | Fire Collars
|  | Level 07 - Zone 5 |  | QA | Hydraulics | New | Level 07 | Zone 5 | Fire Collars
|  | Level 07 - Zone 6 |  | QA | Hydraulics | New | Level 07 | Zone 6 | Fire Collars
|  | Level 08 - Zone 1 |  | QA | Hydraulics | New | Level 08 | Zone 1 | Fire Collars
|  | Level 10 - Zone 2 |  | QA | Hydraulics | New | Level 10 | Zone 2 | Fire Collars
Columns
|  | Employee trained for task & reviewed installation instructions |  | employee trained for task and reviewed installation instructions (product qr code / manufacturer's website / instruction manual)
|  | Notify & gain permit from principal contractor/client for inspection |  | notify and gain permit from principal contractor / client for inspection (hold point)
|  | Setout & alignment as per drawing |  | setout & alignment as per drawing (include revision below)
|  | Drawing & revision number(s) | Drawing & revision number(s) | setout & alignment as per drawing (include revision below)
|  | Installation as per manufacturer's requirements |  | installation as per manufacturer's requirements
|  | Correct fire collar location (as per drawing) |  | correct fire collar location (as per drawing)
|  | Location | Location | correct fire collar location (as per drawing)
|  | Fire tags as per fire matrix installed |  | fire tags as per fire matrix installed
|  | Structurally correct (Engineers Approval required) |  | structurally correct (engineers approval required)
|  | Engineers Approval attached | Engineers Approval attached | structurally correct (engineers approval required)
|  | Fire sealant installed correctly |  | fire sealant installed correctly
|  | Final Inspection - 3rd Party |  | final inspection - 3rd party (including the below as applicable)
|  | Name | Name | final inspection - 3rd party (including the below as applicable)
|  | Company | Company | final inspection - 3rd party (including the below as applicable)
|  | Final sign off |  | final sign off - pass when satisfied to proceed (any issues please comment & add photos below)
Fix 1 Checklist
| Scope |  |  | qa
Rows
|  | Hydraulics - New | grouping | hydraulics - new
|  | Level 02 - Zone 1 - Grid (AA-AE, 07-09) - Toilet (02.504) + Cleaner's Sink, Drinking Fountain & Paint Collection Tank |  | QA | Hydraulics | New | Level 02 | Zone 1 | Grid (AA-AE, 07-09) | Toilet (02.504) + Cleaner's Sink, Drinking Fountain & Paint Collection Tank | Fix 1 Checklist
|  | Level 02 - Zone 1 - Grid (AD-AE, 08-09) - Scenery Dock (02.040) |  | QA | Hydraulics | New | Level 02 | Zone 1 | Grid (AD-AE, 08-09) | Scenery Dock (02.040) | Fix 1 Checklist
|  | Level 02 - Zone 2 - Grid (AA-AD, 14-16) - Drinking Fountain (AC-AD, 13-14) drink fountain West |  | QA | Hydraulics | New | Level 02 | Zone 2 | Grid (AA-AD, 14-16) | Drinking Fountain (AC-AD, 13-14) drink fountain West | Fix 1 Checklist
|  | Level 02 - Zone 2 - Grid (AA-AD, 14-16) - UD WC (02.537) |  | QA | Hydraulics | New | Level 02 | Zone 2 | Grid (AA-AD, 14-16) | UD WC (02.537) | Fix 1 Checklist
|  | Level 02 - Zone 2 - Grid (AA-AD, 14-16) - Quick change |  | QA | Hydraulics | New | Level 02 | Zone 2 | Grid (AA-AD, 14-16) | Quick change | Fix 1 Checklist
|  | Level 02 - Zone 2 - Grid (AA-AD, 14-16) - Amenities West |  | QA | Hydraulics | New | Level 02 | Zone 2 | Grid (AA-AD, 14-16) | Amenities West | Fix 1 Checklist
|  | Level 02 - Zone 2 - Grid (AD-AL, 11-12) - Grid (AD-AE, 11-12) cleaners sink West |  | QA | Hydraulics | New | Level 02 | Zone 2 | Grid (AD-AL, 11-12) | Grid (AD-AE, 11-12) cleaners sink West | Fix 1 Checklist
|  | Level 02 - Zone 2 - Grid (AD-AL, 11-12) - Grid (AJ-AL, 11-12) cleaners sink East |  | QA | Hydraulics | New | Level 02 | Zone 2 | Grid (AD-AL, 11-12) | Grid (AJ-AL, 11-12) cleaners sink East | Fix 1 Checklist
|  | Level 02 - Zone 2 - Grid (AD-AL, 11-12) - Waynes World |  | QA | Hydraulics | New | Level 02 | Zone 2 | Grid (AD-AL, 11-12) | Waynes World | Fix 1 Checklist
|  | Level 02 - Zone 2 - Grid (AL-AN, 14-16) - Drinking Fountain (AL-AM, 13-14) |  | QA | Hydraulics | New | Level 02 | Zone 2 | Grid (AL-AN, 14-16) | Drinking Fountain (AL-AM, 13-14) | Fix 1 Checklist
|  | Level 02 - Zone 2 - Grid (AL-AN, 14-16) - Ensuite (02.572) |  | QA | Hydraulics | New | Level 02 | Zone 2 | Grid (AL-AN, 14-16) | Ensuite (02.572) | Fix 1 Checklist
|  | Level 02 - Zone 2 - Grid (AL-AN, 14-16) - UD WC (02.570) |  | QA | Hydraulics | New | Level 02 | Zone 2 | Grid (AL-AN, 14-16) | UD WC (02.570) | Fix 1 Checklist
|  | Level 02 - Zone 3 - Wardrobe Kitchenette (02.582A) |  | QA | Hydraulics | New | Level 02 | Zone 3 | Wardrobe Kitchenette (02.582A) | Fix 1 Checklist
|  | Level 02 - Zone 6 - Corridor & Performer BOH Spaces (Cold Shell) - Dressing Room (02.522) |  | QA | Hydraulics | New | Level 02 | Zone 6 | Corridor & Performer BOH Spaces (Cold Shell) | Dressing Room (02.522)
|  | Level 02 - Zone 6 - Corridor & Performer BOH Spaces (Cold Shell) - WC1 (ZA-ZB, 13-14) |  | QA | Hydraulics | New | Level 02 | Zone 6 | Corridor & Performer BOH Spaces (Cold Shell) | WC1 (ZA-ZB, 13-14)
|  | Level 02 - Zone 6 - Corridor & Performer BOH Spaces (Cold Shell) - Ensuite (02.524) |  | QA | Hydraulics | New | Level 02 | Zone 6 | Corridor & Performer BOH Spaces (Cold Shell) | Ensuite (02.524)
|  | Level 02 - Zone 6 - Corridor & Performer BOH Spaces (Cold Shell) - Ensuite (02.523) |  | QA | Hydraulics | New | Level 02 | Zone 6 | Corridor & Performer BOH Spaces (Cold Shell) | Ensuite (02.523)
|  | Level 02 - Zone 6 - Corridor & Performer BOH Spaces (Cold Shell) - Crew Stand By Room (02.532) |  | QA | Hydraulics | New | Level 02 | Zone 6 | Corridor & Performer BOH Spaces (Cold Shell) | Crew Stand By Room (02.532)
|  | Level 02 - Zone 6 - Corridor & Performer BOH Spaces (Cold Shell) - Room (AA-ZA, 13-14) |  | QA | Hydraulics | New | Level 02 | Zone 6 | Corridor & Performer BOH Spaces (Cold Shell) | Room (AA-ZA, 13-14)
|  | Level 02 - Zone 6 - Corridor & Performer BOH Spaces (Cold Shell) - WC2 (AA-ZA, 14-15) |  | QA | Hydraulics | New | Level 02 | Zone 6 | Corridor & Performer BOH Spaces (Cold Shell) | WC2 (AA-ZA, 14-15)
|  | Level 02 - Zone 6 - Corridor & Performer BOH Spaces (Cold Shell) - Kitchen (AA-ZA, 14-15) |  | QA | Hydraulics | New | Level 02 | Zone 6 | Corridor & Performer BOH Spaces (Cold Shell) | Kitchen (AA-ZA, 14-15)
|  | Level 02 - Zone 6 - Corridor & Performer BOH Spaces (Cold Shell) - Sound Lock (02.526) |  | QA | Hydraulics | New | Level 02 | Zone 6 | Corridor & Performer BOH Spaces (Cold Shell) | Sound Lock (02.526)
|  | Level 03 - Zone 2 - UD WC (03.518) |  | QA | Hydraulics | New | Level 03 | Zone 2 | UD WC (03.518) | Fix 1 Checklist
|  | Level 03 - Zone 2 - Female Amenities (03.517) |  | QA | Hydraulics | New | Level 03 | Zone 2 | Female Amenities (03.517) | Fix 1 Checklist
|  | Level 03 - Zone 2 - UD Ambulant (03.541) |  | QA | Hydraulics | New | Level 03 | Zone 2 | UD Ambulant (03.541) | Fix 1 Checklist
|  | Level 03 - Zone 6 - Male Amenities (03.516) |  | QA | Hydraulics | New | Level 03 | Zone 6 | Male Amenities (03.516) | Fix 1 Checklist
|  | Level 05 - Zone 6 - Female Amenities (05.532) |  | QA | Hydraulics | New | Level 05 | Zone 6 | Female Amenities (05.532) | Fix 1 Checklist
|  | Level 05 - Zone 6 - UD WC (05.533) |  | QA | Hydraulics | New | Level 05 | Zone 6 | UD WC (05.533) | Fix 1 Checklist
|  | Level 05 - Zone 6 - UD Ambulant (05.534) |  | QA | Hydraulics | New | Level 05 | Zone 6 | UD Ambulant (05.534) | Fix 1 Checklist
|  | Level 05 - Zone 6 - All Gender Inclusive (05.537) |  | QA | Hydraulics | New | Level 05 | Zone 6 | All Gender Inclusive (05.537) | Fix 1 Checklist
|  | Level 05 - Zone 6 - Male Amenities (05.535) |  | QA | Hydraulics | New | Level 05 | Zone 6 | Male Amenities (05.535) | Fix 1 Checklist
|  | Level 05A - Zone 1 - WC (05.523) |  | QA | Hydraulics | New | Level 05A | Zone 1 | WC (05.523) | Fix 1 Checklist
|  | Level 05A - Zone 1 - WC (05.544) |  | QA | Hydraulics | New | Level 05A | Zone 1 | WC (05.544) | Fix 1 Checklist
|  | Level 05A - Zone 1 - WC (05.545) |  | QA | Hydraulics | New | Level 05A | Zone 1 | WC (05.545) | Fix 1 Checklist
|  | Level 05A - Zone 2 - Dock Manager's Office (05.515) |  | QA | Hydraulics | New | Level 05A | Zone 2 | Dock Manager's Office (05.515) | Fix 1 Checklist
|  | Level 05A - Zone 6 - Grid (AA-ZA, 15-16) |  | QA | Hydraulics | New | Level 05A | Zone 6 | Grid (AA-ZA, 15-16) | Fix 1 Checklist
|  | Level 06 - Zone 1 - Stage Door Entry (06.501) |  | QA | Hydraulics | New | Level 06 | Zone 1 | Stage Door Entry (06.501) | Fix 1 Checklist
Columns
|  | Sewer AG - Employee trained for task & reviewed installation instructions |  | sewer ag | employee trained for task and reviewed installation instructions (product qr code / manufacturer's website / instruction manual)
|  | Sewer AG - Notify & gain permit from principal contractor/client for inspection |  | sewer ag | notify and gain permit from principal contractor / client for inspection (hold point)
|  | Sewer AG - Setout & alignment as per drawing |  | sewer ag | setout & alignment as per drawing (include revision below)
|  | Sewer AG - Drawing & revision number(s) | Drawing & revision number(s) | sewer ag | setout & alignment as per drawing (include revision below)
|  | Sewer AG - Grades, fittings & joints installed to standards |  | grades, fittings & joints installed to standards | sewer ag
|  | Sewer AG - Fixings & seismic support to standards |  | fixings & seismic support to standards | sewer ag
|  | Sewer AG - Expansion joints per floor installed correctly & clipped |  | sewer ag | expansion joints per floor installed correctly & clipped
|  | Sewer AG - Pipe risers sealed per floor & capped off to prevent damage |  | pipe risers sealed per floor & capped off to prevent damage | sewer ag
|  | Sewer AG - Correct invert level (As per Standards) |  | correct invert level (as per standards) | sewer ag
|  | Sewer AG - Vents & AAV installed (As per Standards) |  | sewer ag | vents and aav installed (as per standards)
|  | Sewer AG - Acoustic lagging installed to acoustic spec. |  | acoustic lagging installed to acoustic specification | sewer ag
|  | Sewer AG - Pipework water tested to 15Kpa |  | pipework water tested to 15kpa | sewer ag
|  | Sewer AG - Identifications of services |  | sewer ag | identifications of services
|  | Sewer AG - Final sign off |  | sewer ag | final sign off - pass when satisfied to proceed (any issues please comment & add photos below)
|  | Sewer AG - Area clean | Area clean | sewer ag | final sign off - pass when satisfied to proceed (any issues please comment & add photos below)
|  | Stormwater AG - Employee trained for task & reviewed installation instructions |  | stormwater ag | employee trained for task and reviewed installation instructions (product qr code / manufacturer's website / instruction manual)
|  | Stormwater AG - Notify & gain permit from principal contractor/client for inspection |  | stormwater ag | notify and gain permit from principal contractor / client for inspection (hold point)
|  | Stormwater AG - Setout & alignment as per drawing |  | setout & alignment as per drawing (include revision below) | stormwater ag
|  | Stormwater AG - Drawing & revision number(s) | Drawing & revision number(s) | setout & alignment as per drawing (include revision below) | stormwater ag
|  | Stormwater AG - Grades (as per AS:3500) |  | grades (as per as:3500) | stormwater ag
|  | Stormwater AG - Location (as per hydraulic drawing) |  | stormwater ag | location (as per hydraulic drawing)
|  | Stormwater AG - Location | Location | stormwater ag | location (as per hydraulic drawing)
|  | Stormwater AG - Fixings - Securely fixed (As per Standards) |  | stormwater ag | fixings - securely fixed (as per standards)
|  | Stormwater AG - Fittings Joints ETC (as per AS 3500) |  | fittings joints etc (as per as 3500) | stormwater ag
|  | Stormwater AG - Inspection prior to closure |  | inspection prior to closure | stormwater ag
|  | Stormwater AG - Operation of pumps (Commissioning report) |  | operation of pumps (commissioning report) if applicable | stormwater ag
|  | Stormwater AG - Test water & discharge requirements are met |  | test water and discharge requirements are met | stormwater ag
|  | Stormwater AG - Correct invert level AS per AS 3500 |  | correct invert level as per as 3500 | stormwater ag
|  | Stormwater AG - Final sign off |  | final sign off - pass when satisfied to proceed (any issues please comment & add photos below) | stormwater ag
|  | Stormwater AG - Area clean | Area clean | final sign off - pass when satisfied to proceed (any issues please comment & add photos below) | stormwater ag
|  | Rough In - Employee trained for task & reviewed installation instructions |  | employee trained for task and reviewed installation instructions (product qr code / manufacturer's website / instruction manual) | rough in
|  | Rough In - Notify & gain permit from principal contractor/client for inspection |  | notify and gain permit from principal contractor / client for inspection (hold point) | rough in
|  | Rough In - Setout & alignment as per drawing |  | setout & alignment as per drawing (include revision below) | rough in
|  | Rough In - Drawing & revision number(s) | Drawing & revision number(s) | setout & alignment as per drawing (include revision below) | rough in
|  | Rough In - Material type (as per sample submission) |  | material type (as per sample submission) | rough in
|  | Rough In - Pipework installation checked against standards (as per AS 3500.1) |  | pipework installation checked against standards (as per as 3500.1) | rough in
|  | Rough In - Welding/pressfit/push fit/witness marks (as per AS 3500.1) |  | welding / pressfit / push fit / witness marks (as per as 3500.1) | rough in
|  | Rough In - Support & fixings checked (acoustic/seismic/water hammer/silicone) |  | support & fixings checked (acoustic / seismic / water hammer/ silicone) | rough in
|  | Rough In - Check for no cross connection |  | check for no cross connection | rough in
|  | Rough In - Heights double checked before room sign off as per sample submission |  | heights double checked before room sign off as per sample submission | rough in
|  | Rough In - Pipe risers water sealed per floor & capped off to prevent damage |  | pipe risers water sealed per floor and capped off to prevent damage | rough in
|  | Rough In - Correct sewer ventilation |  | correct sewer ventilation | rough in
|  | Rough In - Pressure test water lines to (1500kpa) |  | pressure test water lines to (1500kpa) | rough in
|  | Rough In - Identification of services |  | identification of services | rough in
|  | Rough In - Final sign off |  | final sign off - pass when satisfied to proceed (any issues please comment & add photos below) | rough in
|  | Rough In - Area clean | Area clean | final sign off - pass when satisfied to proceed (any issues please comment & add photos below) | rough in
|  | Rainwater - Employee trained for task & reviewed installation instructions |  | rainwater | employee trained for task and reviewed installation instructions (product qr code / manufacturer's website / instruction manual)
|  | Rainwater - Notify & gain permit from principal contractor/client for inspection |  | rainwater | notify and gain permit from principal contractor / client for inspection (hold point)
|  | Rainwater - Setout & alignment as per drawing |  | setout & alignment as per drawing (include revision below) | rainwater
|  | Rainwater - Drawing & revision number(s) | Drawing & revision number(s) | setout & alignment as per drawing (include revision below) | rainwater
|  | Rainwater - Material type as per approved sample submission |  | material type as per approved sample submission | rainwater
|  | Rainwater - Pipework fittings, bends, joints etc (as per AS 3500.1 section 2.6) |  | rainwater | pipework fittings, bends, joints etc (as per as 3500.1 section 2.6)
|  | Rainwater - Welding/pressfit/push fit (as per AS 3500.1) |  | welding / pressfit / push fit (as per as 3500.1) | rainwater
|  | Rainwater - Support & fixings (acoustic/seismic/water hammer) |  | support & fixings (acoustic / seismic / water hammer) | rainwater
|  | Rainwater - Pipework Installation (as per AS 3500.1) |  | pipework installation (as per as 3500.1) | rainwater
|  | Rainwater - Check no cross connection |  | check no cross connection | rainwater
|  | Rainwater - Pressure test (1500kpa pressure test) |  | pressure test (1500kpa pressure test) | rainwater
|  | Rainwater - Identifications of services |  | identifications of services | rainwater
|  | Rainwater - Final sign off |  | final sign off - pass when satisfied to proceed (any issues please comment & add photos below) | rainwater
|  | Rainwater - Area clean | Area clean | final sign off - pass when satisfied to proceed (any issues please comment & add photos below) | rainwater
Fix 2 Checklist
| Scope |  |  | qa
Rows
|  | Hydraulics - New | grouping | hydraulics - new
|  | Level 02 - Zone 1 - Grid (AA-AE, 07-09) - Toilet (02.504) + Cleaner's Sink, Drinking Fountain & Paint Collection Tank |  | QA | Hydraulics | New | Level 02 | Zone 1 | Grid (AA-AE, 07-09) | Toilet (02.504) + Cleaner's Sink, Drinking Fountain & Paint Collection Tank | Fix 2 checklist
|  | Level 02 - Zone 1 - Grid (AD-AE, 08-09) - Scenery Dock (02.040) |  | QA | Hydraulics | New | Level 02 | Zone 1 | Grid (AD-AE, 08-09) | Scenery Dock (02.040) | Fix 2 checklist
|  | Level 02 - Zone 2 - Grid (AA-AD, 14-16) - Drinking Fountain (AC-AD, 13-14) drink fountain West |  | QA | Hydraulics | New | Level 02 | Zone 2 | Grid (AA-AD, 14-16) | Drinking Fountain (AC-AD, 13-14) drink fountain West | Fix 2 checklist
|  | Level 02 - Zone 2 - Grid (AA-AD, 14-16) - UD WC (02.537) |  | QA | Hydraulics | New | Level 02 | Zone 2 | Grid (AA-AD, 14-16) | UD WC (02.537) | Fix 2 checklist
|  | Level 02 - Zone 2 - Grid (AA-AD, 14-16) - Quick change |  | QA | Hydraulics | New | Level 02 | Zone 2 | Grid (AA-AD, 14-16) | Quick change | Fix 2 checklist
|  | Level 02 - Zone 2 - Grid (AA-AD, 14-16) - Amenities West |  | QA | Hydraulics | New | Level 02 | Zone 2 | Grid (AA-AD, 14-16) | Amenities West | Fix 2 checklist
|  | Level 02 - Zone 2 - Grid (AD-AL, 11-12) - Grid (AD-AE, 11-12) cleaners sink West |  | QA | Hydraulics | New | Level 02 | Zone 2 | Grid (AD-AL, 11-12) | Grid (AD-AE, 11-12) cleaners sink West | Fix 2 checklist
|  | Level 02 - Zone 2 - Grid (AD-AL, 11-12) - Grid (AJ-AL, 11-12) cleaners sink East |  | QA | Hydraulics | New | Level 02 | Zone 2 | Grid (AD-AL, 11-12) | Grid (AJ-AL, 11-12) cleaners sink East | Fix 2 checklist
|  | Level 02 - Zone 2 - Grid (AD-AL, 11-12) - Waynes World |  | QA | Hydraulics | New | Level 02 | Zone 2 | Grid (AD-AL, 11-12) | Waynes World | Fix 2 checklist
|  | Level 02 - Zone 2 - Grid (AL-AN, 14-16) - Drinking Fountain (AL-AM, 13-14) |  | QA | Hydraulics | New | Level 02 | Zone 2 | Grid (AL-AN, 14-16) | Drinking Fountain (AL-AM, 13-14) | Fix 2 checklist
|  | Level 02 - Zone 2 - Grid (AL-AN, 14-16) - Ensuite (02.572) |  | QA | Hydraulics | New | Level 02 | Zone 2 | Grid (AL-AN, 14-16) | Ensuite (02.572) | Fix 2 checklist
|  | Level 02 - Zone 2 - Grid (AL-AN, 14-16) - UD WC (02.570) |  | QA | Hydraulics | New | Level 02 | Zone 2 | Grid (AL-AN, 14-16) | UD WC (02.570) | Fix 2 checklist
|  | Level 02 - Zone 3 - Wardrobe Kitchenette (02.582A) |  | QA | Hydraulics | New | Level 02 | Zone 3 | Wardrobe Kitchenette (02.582A) | Fix 2 checklist
|  | Level 03 - Zone 2 - UD WC (03.518) |  | QA | Hydraulics | New | Level 03 | Zone 2 | UD WC (03.518) | Fix 2 checklist
|  | Level 03 - Zone 2 - Female Amenities (03.517) |  | QA | Hydraulics | New | Level 03 | Zone 2 | Female Amenities (03.517) | Fix 2 checklist
|  | Level 03 - Zone 2 - UD Ambulant (03.541) |  | QA | Hydraulics | New | Level 03 | Zone 2 | UD Ambulant (03.541) | Fix 2 checklist
|  | Level 03 - Zone 6 - Male Amenities (03.516) |  | QA | Hydraulics | New | Level 03 | Zone 6 | Male Amenities (03.516) | Fix 2 checklist
|  | Level 05 - Zone 6 - Female Amenities (05.532) |  | QA | Hydraulics | New | Level 05 | Zone 6 | Female Amenities (05.532) | Fix 2 checklist
|  | Level 05 - Zone 6 - UD WC (05.533) |  | QA | Hydraulics | New | Level 05 | Zone 6 | UD WC (05.533) | Fix 2 checklist
|  | Level 05 - Zone 6 - UD Ambulant (05.534) |  | QA | Hydraulics | New | Level 05 | Zone 6 | UD Ambulant (05.534) | Fix 2 checklist
|  | Level 05 - Zone 6 - All Gender Inclusive (05.537) |  | QA | Hydraulics | New | Level 05 | Zone 6 | All Gender Inclusive (05.537) | Fix 2 checklist
|  | Level 05 - Zone 6 - Male Amenities (05.535) |  | QA | Hydraulics | New | Level 05 | Zone 6 | Male Amenities (05.535) | Fix 2 checklist
|  | Level 05A - Zone 1 - WC (05.523) |  | QA | Hydraulics | New | Level 05A | Zone 1 | WC (05.523) | Fix 2 checklist
|  | Level 05A - Zone 1 - WC (05.544) |  | QA | Hydraulics | New | Level 05A | Zone 1 | WC (05.544) | Fix 2 checklist
|  | Level 05A - Zone 1 - WC (05.545) |  | QA | Hydraulics | New | Level 05A | Zone 1 | WC (05.545) | Fix 2 checklist
|  | Level 05A - Zone 2 - Dock Manager's Office (05.515) |  | QA | Hydraulics | New | Level 05A | Zone 2 | Dock Manager's Office (05.515) | Fix 2 checklist
|  | Level 05A - Zone 6 - Grid (AA-ZA, 15-16) |  | QA | Hydraulics | New | Level 05A | Zone 6 | Grid (AA-ZA, 15-16) | Fix 2 checklist
|  | Level 06 - Zone 1 - Stage Door Entry (06.501) |  | QA | Hydraulics | New | Level 06 | Zone 1 | Stage Door Entry (06.501) | Fix 2 checklist
Columns
|  | Fixtures - Employee trained for task & reviewed installation instructions |  | employee trained for task and reviewed installation instructions (product qr code / manufacturer's website / instruction manual) | fixtures
|  | Fixtures - Notify & gain permit from principal contractor/client for inspection |  | notify and gain permit from principal contractor / client for inspection (hold point) | fixtures
|  | Fixtures - Correct product (samples provided) |  | correct product (samples provided) | fixtures
|  | Fixtures - Check products for imperfections |  | check products for imperfections | fixtures
|  | Fixtures - Location & fixings (as per drawings & manufacturer guidelines) |  | location & fixings (as per drawings & manufacturer guidelines) | fixtures
|  | Fixtures - Silicone seals are acceptable standard |  | silicone seals are acceptable standard (as applicable) | fixtures
|  | Fixtures - Operation of all fixtures, taps & points of demand |  | operation of all fixtures, taps & points of demand | fixtures
|  | Fixtures - Final fit off inspection on all items |  | final fit off inspection on all items | fixtures
|  | Fixtures - Inspection date | Inspection date | final fit off inspection on all items | fixtures
|  | Fixtures - Items protected until commissioning |  | items protected until commissioning (attach photos below) | fixtures
|  | Fixtures - Final sign off |  | final sign off - pass when satisfied to proceed (any issues please comment & add photos below) | fixtures
|  | Commissioning - Employee trained for task & reviewed installation instructions |  | commissioning | employee trained for task and reviewed installation instructions (product qr code / manufacturer's website / instruction manual)
|  | Commissioning - Notify & gain permit from principal contractor/client for inspection |  | commissioning | notify and gain permit from principal contractor / client for inspection (hold point)
|  | Commissioning - Check products for imperfections |  | commissioning | check products for imperfections
|  | Commissioning - Fixtures location & fixings all correct (as per drawings & samples) |  | fixtures location & fixings all correct (as per drawings & samples) | commissioning
|  | Commissioning - Clean out all strainers/aerators |  | clean out all strainers / aerators | commissioning
|  | Commissioning - Check for no cross connections/leaks/access to isolation valves |  | check for no cross connections / leaks / access to isolation valves | commissioning
|  | Commissioning - Floor wastes (clear of debris & draining correctly) |  | commissioning | floor wastes (clear of debris & draining correctly)
|  | Commissioning - Quality of silicone seals to fixtures acceptable |  | commissioning | quality of silicone seals to fixtures acceptable
|  | Commissioning - Hot water tempering valve set to 50c (+/- 5c) & DDA thermostatic mixing valve set to 42 degrees. |  | hot water tempering valve set to 50c (+/- 5c) & dda thermostatic mixing valve set to 42 degrees. | commissioning
|  | Commissioning - Water pressure acceptable 350Kpa to 500 Kpa |  | water pressure acceptable 350kpa to 500 kpa | commissioning
|  | Commissioning - Final sign off |  | final sign off - pass when satisfied to proceed (any issues please comment & add photos below) | commissioning
|  | Commissioning - Area clean | Area clean | final sign off - pass when satisfied to proceed (any issues please comment & add photos below) | commissioning
Rough In Checklist
| Scope |  |  | qa
Rows
|  | Hydraulics - New | grouping | hydraulics - new
|  | Level 02 - Zone 1 - Grid (AA-AE, 07-09) - Pump Line (PL) |  | QA | Hydraulics | New | Level 02 | Zone 1 | Grid (AA-AE, 07-09) | Pump Line (PL)
Columns
|  | Employee trained for task & reviewed installation instructions |  | Employee trained for task and reviewed installation instructions (product QR code / manufacturer's website / instruction manual)
|  | Notify & gain permit from principal contractor/client for inspection |  | Notify and gain permit from principal contractor / client for inspection (hold point)
|  | Setout & alignment as per drawing |  | Setout & alignment as per drawing (include revision below)
|  | Drawing & revision number(s) | Drawing & revision number(s) | Setout & alignment as per drawing (include revision below)
|  | Material type (as per sample submission) |  | Material type (as per sample submission)
|  | Welding/pressfit/push fit/witness marks (as per AS 3500.1) |  | Welding / pressfit / push fit / witness marks (as per AS 3500.1)
|  | Support & fixings checked (acoustic/seismic/water hammer/ silicone) |  | Support & fixings checked (acoustic / seismic / water hammer/ silicone) - Add Photos below
|  | Pipework installation checked against standards (as per AS 3500.1) |  | Pipework installation checked against standards (as per AS 3500.1)
|  | Check no cross connection |  | Check no cross connection
|  | Heights double checked before room sign off as per sample submission |  | Heights double checked before room sign off as per sample submission
|  | Pipe risers water sealed per floor & capped off to prevent damage |  | Pipe risers water sealed per floor & capped off to prevent damage
|  | Correct sewer ventilation installed |  | Correct sewer ventilation installed
|  | Pressure test water lines to (1500kpa) |  | Pressure test water lines to (1500kpa)
|  | Identification of services |  | Identification of services
|  | Services | Services | Identification of services
|  | Final sign off |  | Final sign off - Pass when satisfied to proceed (Any issues please comment & Add photos below)
|  | Area clean | Area clean | Final sign off - Pass when satisfied to proceed (Any issues please comment & Add photos below)
Sanitary
| Scope |  |  | qa
Rows
|  | Hydraulics - New | grouping | hydraulics - new
|  | Level 02 - Zone 1 - Grid (AA-AE, 07-09) - Sanitary Drainage (SS) |  | QA | Hydraulics | New | Level 02 | Zone 1 | Grid (AA-AE, 07-09) | Sanitary Drainage (SS)
|  | Level 02 - Zone 1 - Grid (AA-AE, 07-09) - Chamber Vent (CHV) |  | QA | Hydraulics | New | Level 02 | Zone 1 | Grid (AA-AE, 07-09) | Chamber Vent (CHV)
|  | Level 02 - Zone 6 - Chamber Vent (CHV) |  | QA | Hydraulics | New | Level 02 | Zone 6 | Chamber Vent (CHV)
|  | Level 03 - Zone 1 - Chamber Vent (CHV) |  | QA | Hydraulics | New | Level 03 | Zone 1 | Chamber Vent (CHV)
|  | Level 03 - Zone 5 - Chamber Vent (CHV) |  | QA | Hydraulics | New | Level 03 | Zone 5 | Chamber Vent (CHV)
|  | Level 03 - Zone 6 - Chamber Vent (CHV) |  | QA | Hydraulics | New | Level 03 | Zone 6 | Chamber Vent (CHV)
|  | Level 03 - Zone 6 - Space Theatre Function Space (Cold Shell) - Planting Room (03.522) - Sanitary Service AG (SS) |  | QA | Hydraulics | New | Level 03 | Zone 6 | Space Theatre Function Space (Cold Shell) | Planting Room (03.522) | Sanitary Service AG (SS)
|  | Level 04 - Zone 1 - Chamber Vent (CHV) |  | QA | Hydraulics | New | Level 04 | Zone 1 | Chamber Vent (CHV)
|  | Level 04 - Zone 2 - Vent Pipe (VP) |  | QA | Hydraulics | New | Level 04 | Zone 2 | Vent Pipe (VP)
|  | Level 04 - Zone 2 - Mechanical Condensate Drainage |  | QA | Hydraulics | New | Level 04 | Zone 2 | Mechanical Condensate Drainage
|  | Level 05 - Zone 1 - Grid (AA-AD, 6-7) - Chamber Vent (CHV) |  | QA | Hydraulics | New | Level 05 | Zone 1 | Grid (AA-AD, 6-7) | Chamber Vent (CHV)
|  | Level 05 - Zone 2 - Vent Pipe (VP) |  | QA | Hydraulics | New | Level 05 | Zone 2 | Vent Pipe (VP)
|  | Level 05 - Zone 6 - 50mm Chamber Vent (CHV) |  | QA | Hydraulics | New | Level 05 | Zone 6 | 50mm Chamber Vent (CHV)
|  | Level 05 - Zone 6 - GIT 1 - Chamber Vent (CHV) |  | QA | Hydraulics | New | Level 05 | Zone 6 | GIT 1 | Chamber Vent (CHV)
|  | Level 05 - Zone 6 - GIT 2 - Chamber Vent (CHV) |  | QA | Hydraulics | New | Level 05 | Zone 6 | GIT 2 | Chamber Vent (CHV)
|  | Level 05A - Zone 1 - Sanitary Drainage AG (SS) |  | QA | Hydraulics | New | Level 05A | Zone 1 | Sanitary Drainage AG (SS)
|  | Level 05A - Zone 2 - Sanitary Drainage (SS) |  | QA | Hydraulics | New | Level 05A | Zone 2 | Sanitary Drainage (SS)
|  | Level 05A - Zone 5 - Chamber Vent (CHV) - Grid (AA-ZA, 01-02) |  | QA | Hydraulics | New | Level 05A | Zone 5 | Chamber Vent (CHV) | Grid (AA-ZA, 01-02)
|  | Level 07 - Zone 2 - Sanitary Drainage - Grid (AA-AE, 08-11) |  | QA | Hydraulics | New | Level 07 | Zone 2 | Sanitary Drainage | Grid (AA-AE, 08-11)
|  | Level 07 - Zone 2 - Sanitary Drainage - Grid (AA-AC, 17-19) |  | QA | Hydraulics | New | Level 07 | Zone 2 | Sanitary Drainage | Grid (AA-AC, 17-19)
|  | Level 08 - Zone 1 - Chamber Vent (CHV) |  | QA | Hydraulics | New | Level 08 | Zone 1 | Chamber Vent (CHV)
Columns
|  | Employee trained for task & reviewed installation instructions |  | Employee trained for task and reviewed installation instructions (product QR code / manufacturer's website / instruction manual)
|  | Notify & gain permit from principal contractor/client for inspection |  | Notify and gain permit from principal contractor / client for inspection (hold point)
|  | Setout & alignment as per drawing |  | Setout and alignment as per drawing (include revision in comments)
|  | Materials Type (as per sample submission) | Materials Type (as per sample submission) | Setout and alignment as per drawing (include revision in comments)
|  | Fittings & fixings (as per AS 2032) |  | Fittings & fixings (as per AS 2032)
|  | Identification of services |  | Identification of services
|  | Heights double checked before room sign off off fixture approvals tech data |  | Heights double checked before room sign off off fixture approvals tech data
|  | Pipe risers sealed per floor & capped off to prevent damage |  | Pipe risers sealed per floor and capped off to prevent damage
|  | Correct ventilation |  | Correct ventilation
|  | CCTV drainage |  | CCTV drainage
|  | Testing (air testing to 15kpa) |  | Testing (air testing to 15kpa)
|  | Identifications of services |  | Identifications of services
|  | Final sign off |  | Final sign off - Pass when satisfied to proceed (Any issues please comment & Add photos below)
|  | Area clean | Area clean | Final sign off - Pass when satisfied to proceed (Any issues please comment & Add photos below)
Service Log - Thermostatic Mixing Valves (TMV)
| Scope |  |  | qa
Rows
|  | Hydraulics - Thermostatic Mixing Valves | grouping | hydraulics - thermostatic mixing valves
|  | Level 02 - Zone 1 - Toilet (02.504) |  | QA | Hydraulics | Thermostatic Mixing Valves | Level 02 | Zone 1 | Toilet (02.504)
|  | Level 02 - Zone 1 - UD WC (02.537) |  | QA | Hydraulics | Thermostatic Mixing Valves | Level 02 | Zone 1 | UD WC (02.537)
|  | Level 02 - Zone 1 - Ensuite (02.572) |  | QA | Hydraulics | Thermostatic Mixing Valves | Level 02 | Zone 1 | Ensuite (02.572)
|  | Level 02 - Zone 1 - UD WC (02.570) |  | QA | Hydraulics | Thermostatic Mixing Valves | Level 02 | Zone 1 | UD WC (02.570)
|  | Level 03 - Zone 2 - UD Ambulant (03.541) |  | QA | Hydraulics | Thermostatic Mixing Valves | Level 03 | Zone 2 | UD Ambulant (03.541)
|  | Level 03 - Zone 2 - Female Amenities (03.517) |  | QA | Hydraulics | Thermostatic Mixing Valves | Level 03 | Zone 2 | Female Amenities (03.517)
|  | Level 03 - Zone 2 - UD WC (03.518) |  | QA | Hydraulics | Thermostatic Mixing Valves | Level 03 | Zone 2 | UD WC (03.518)
|  | Level 03 - Zone 6 - Male Amenities (03.516) |  | QA | Hydraulics | Thermostatic Mixing Valves | Level 03 | Zone 6 | Male Amenities (03.516)
|  | Level 05 - Zone 5 - Female Amenities (05.532) |  | QA | Hydraulics | Thermostatic Mixing Valves | Level 05 | Zone 5 | Female Amenities (05.532)
|  | Level 05 - Zone 5 - UD WC (05.533) |  | QA | Hydraulics | Thermostatic Mixing Valves | Level 05 | Zone 5 | UD WC (05.533)
|  | Level 05 - Zone 5 - UD Ambulant (05.534) |  | QA | Hydraulics | Thermostatic Mixing Valves | Level 05 | Zone 5 | UD Ambulant (05.534)
|  | Level 05 - Zone 5 - All Gender Inclusive (05.537) |  | QA | Hydraulics | Thermostatic Mixing Valves | Level 05 | Zone 5 | All Gender Inclusive (05.537)
|  | Level 05 - Zone 5 - Male Amenities (05.535) |  | QA | Hydraulics | Thermostatic Mixing Valves | Level 05 | Zone 5 | Male Amenities (05.535)
|  | Level 05A - Zone 1 - WC (05.523) |  | QA | Hydraulics | Thermostatic Mixing Valves | Level 05A | Zone 1 | WC (05.523)
|  | Level 06 - Zone 5 - UD Toilet (06.503) |  | QA | Hydraulics | Thermostatic Mixing Valves | Level 06 | Zone 5 | UD Toilet (06.503)
Columns
|  | TMV - SLS - Service Log Details |  | Service Log Details | TMV - Service Log Sheet
|  | TMV - SLS - Name of Establishment | Name of Establishment | Service Log Details | TMV - Service Log Sheet
|  | TMV - SLS - Address of Establishment | Address of Establishment | Service Log Details | TMV - Service Log Sheet
|  | TMV - SLS - Contact Person | Contact Person | Service Log Details | TMV - Service Log Sheet
|  | TMV - SLS - Phone Number | Phone Number | Service Log Details | TMV - Service Log Sheet
|  | TMV - SLS - Work Order Number | Work Order Number | Service Log Details | TMV - Service Log Sheet
|  | TMV - SLS - Date | Date | Service Log Details | TMV - Service Log Sheet
|  | TMV - SLS - Make & Type of Hot Water Unit | Make & Type of Hot Water Unit | Service Log Details | TMV - Service Log Sheet
|  | TMV - SLS - Make of Mixing Valve | Make of Mixing Valve | Service Log Details | TMV - Service Log Sheet
|  | TMV - SLS - Model | Model | Service Log Details | TMV - Service Log Sheet
|  | TMV - SLS - Size | Size | Service Log Details | TMV - Service Log Sheet
|  | TMV - SLS - Valve Location/Building | Valve Location/Building | Service Log Details | TMV - Service Log Sheet
|  | TMV - SLS - Room or Area Designation | Room or Area Designation | Service Log Details | TMV - Service Log Sheet
|  | TMV - SLS - No. of Outlets Served |  | No. of Outlets Served (Pass when Entered) | TMV - Service Log Sheet
|  | TMV - SLS - Total No. of Mixing Valves On-Site/Building | Total No. of Mixing Valves On-Site/Building | No. of Outlets Served (Pass when Entered) | TMV - Service Log Sheet
|  | TMV - SLS - Baths | Baths | No. of Outlets Served (Pass when Entered) | TMV - Service Log Sheet
|  | TMV - SLS - Basins | Basins | No. of Outlets Served (Pass when Entered) | TMV - Service Log Sheet
|  | TMV - SLS - Showers | Showers | No. of Outlets Served (Pass when Entered) | TMV - Service Log Sheet
|  | TMV - SLS - Other Outlets | Other Outlets (Add Details) | No. of Outlets Served (Pass when Entered) | TMV - Service Log Sheet
|  | TMV - SLS - Valve installed to requirements of valve manufacturer/supplier, Department of Health & the local water supply authority |  | Valve installed to requirements of valve manufacturer / supplier, Department of Health & the local water supply authority | TMV - Service Log Sheet
|  | TMV - SLS - Failure Details | Failure Details | Valve installed to requirements of valve manufacturer / supplier, Department of Health & the local water supply authority | TMV - Service Log Sheet
|  | TMV - SLS - Date of Previous Service on this Valve | Date of Previous Service on this Valve | Valve installed to requirements of valve manufacturer / supplier, Department of Health & the local water supply authority | TMV - Service Log Sheet
|  | TMV - SLS - Previous Service carried out by | Previous Service carried out by | Valve installed to requirements of valve manufacturer / supplier, Department of Health & the local water supply authority | TMV - Service Log Sheet
|  | TMV - SLS - Any current complaints concerning installation or operation reported by establishment personel | Any current complaints concerning installation or operation reported by establishment personel | Valve installed to requirements of valve manufacturer / supplier, Department of Health & the local water supply authority | TMV - Service Log Sheet
|  | TMV - SLS - Failure Details | Failure Details | Valve installed to requirements of valve manufacturer / supplier, Department of Health & the local water supply authority | TMV - Service Log Sheet
|  | TMV - SLS - Particulars of Service Work carried out | Particulars of Service Work carried out | Valve installed to requirements of valve manufacturer / supplier, Department of Health & the local water supply authority | TMV - Service Log Sheet
|  | TMV - SLS - List of Items replaced & Part Numbers | List of Items replaced & Part Numbers | Valve installed to requirements of valve manufacturer / supplier, Department of Health & the local water supply authority | TMV - Service Log Sheet
|  | TMV - SLS - Temp, of warm water at outlet | Temp, of warm water at outlet | Valve installed to requirements of valve manufacturer / supplier, Department of Health & the local water supply authority | TMV - Service Log Sheet
|  | TMV - SLS - Fail Safe Test |  | Fail Safe Test (Add comments below) | TMV - Service Log Sheet
|  | TMV - SLS - Valve considered satisfactory for further use |  | Valve considered satisfactory for further use | TMV - Service Log Sheet
|  | TMV - SLS - Failure Details | Failure Details | Valve considered satisfactory for further use | TMV - Service Log Sheet
|  | TMV - SLS - Next Service Due (12 Months Maximum) | Next Service Due (12 Months Maximum) | Valve considered satisfactory for further use | TMV - Service Log Sheet
|  | Service Log Details - Sign-off |  | Sign-off (Pass once completed & signature Details added) | Service Log Details
|  | Service Log Details - License Number | License Number | Sign-off (Pass once completed & signature Details added) | Service Log Details
|  | Service Log Details - Contractors Authority No | Contractors Authority No | Sign-off (Pass once completed & signature Details added) | Service Log Details
|  | Service Log Details - Date of Service | Date of Service | Sign-off (Pass once completed & signature Details added) | Service Log Details
|  | Valve Install - Valve Installation Details |  | Valve Installation Details | Valve Install
|  | Valve Install - Valve size & Installation recommended by | Valve size & Installation recommended by | Valve Installation Details | Valve Install
|  | Valve Install - Valve Supplied by | Valve Supplied by | Valve Installation Details | Valve Install
|  | Valve Install - Valve Comissioned by | Valve Comissioned by | Valve Installation Details | Valve Install
|  | Valve Install - Date of Installation | Date of Installation | Valve Installation Details | Valve Install
|  | Valve Install - Drawing No. & Revision | Drawing No. & Revision | Valve Installation Details | Valve Install
|  | Valve Install - Certificate of Compliance/Inspection No | Certificate of Compliance/Inspection No | Valve Installation Details | Valve Install
|  | Valve Install - Service Manual On-site |  | Service Manual On-site | Valve Install
|  | Valve Install - Report received by | Report received by | Service Manual On-site | Valve Install
|  | Valve Install - Position | Position | Service Manual On-site | Valve Install
|  | Valve Install - Date | Date | Service Manual On-site | Valve Install
Sewer AG
| Scope |  |  | qa
Rows
|  | Hydraulics - New | grouping | hydraulics - new
|  | Level 05 - Zone 2 - Sewer AG (SS) |  | QA | Hydraulics | New | Level 05 | Zone 2 | Sewer AG (SS)
|  | Level 05A - Zone 5 - Sanitary Drainage (AG) - Grid (AA-ZA, 04-05) |  | QA | Hydraulics | New | Level 05A | Zone 5 | Sanitary Drainage (AG) | Grid (AA-ZA, 04-05)
|  | Level 05A - Zone 6 - Sanitary Drainage AG (SS) - Grid (ZA-ZB, 09-10) |  | QA | Hydraulics | New | Level 05A | Zone 6 | Sanitary Drainage AG (SS) | Grid (ZA-ZB, 09-10)
|  | Level 05A - Zone 6 - Sanitary Drainage AG (SS) - Grid (ZA-ZB, 11-12) |  | QA | Hydraulics | New | Level 05A | Zone 6 | Sanitary Drainage AG (SS) | Grid (ZA-ZB, 11-12)
Columns
|  | Employee trained for task and reviewed installation instructions |  | Employee trained for task and reviewed installation instructions (product QR code / manufacturer's website / instruction manual)
|  | Notify and gain permit from principal contractor/client for inspection |  | Notify and gain permit from principal contractor / client for inspection (hold point)
|  | Setout & alignment as per drawing |  | Setout & alignment as per drawing (include revision below)
|  | Drawing & revision number(s) | Drawing & revision number(s) | Setout & alignment as per drawing (include revision below)
|  | Grades, fittings & joints installed to standards |  | Grades, fittings & joints installed to standards
|  | Fixings & seismic support to standards |  | Fixings & seismic support to standards
|  | Expansion joints per floor installed correctly & clipped |  | Expansion joints per floor installed correctly & clipped
|  | Pipe risers sealed per floor & capped off to prevent damage |  | Pipe risers sealed per floor & capped off to prevent damage
|  | Correct invert level (As per Standards) |  | Correct invert level (As per Standards)
|  | Vents and AAV installed (As per Standards) |  | Vents and AAV installed (As per Standards)
|  | Acoustic lagging installed to acoustic specification |  | Acoustic lagging installed to acoustic specification
|  | Pipework water tested to 15Kpa |  | Pipework water tested to 15Kpa
|  | Identifications of services |  | Identifications of services
|  | Final sign off |  | Final sign off - Pass when satisfied to proceed (Any issues please comment & Add photos below)
|  | Area clean | Area clean | Final sign off - Pass when satisfied to proceed (Any issues please comment & Add photos below)
Sewer BG
| Scope |  |  | qa
Rows
|  | Civil - Sewer Drains | grouping | civil - sewer drains
|  | Section 01-2 - 01-3 |  | QA | Civil | Sewer Drains | Section 01-2 - 01-3
|  | Section 01-3 - Building |  | QA | Civil | Sewer Drains | Section 01-3 - Building
|  | Section 01-3 - 01-4 |  | QA | Civil | Sewer Drains | Section 01-3 - 01-4
|  | Section 01-4 - 01-5 |  | QA | Civil | Sewer Drains | Section 01-4 - 01-5
|  | Section 01-5 - 01-6 |  | QA | Civil | Sewer Drains | Section 01-5 - 01-6
|  | Section 01-6 - 01-7 |  | QA | Civil | Sewer Drains | Section 01-6 - 01-7
|  | Section 01-7 - Building |  | QA | Civil | Sewer Drains | Section 01-7 - Building
|  | Section 01-7 - 01-8 |  | QA | Civil | Sewer Drains | Section 01-7 - 01-8
|  | Hydraulics - New | grouping | hydraulics - new
|  | Level 02 - Zone 6 - Sewer BG (SS) |  | QA | Hydraulics | New | Level 02 | Zone 6 | Sewer BG (SS)
|  | Level 05 - Zone 4 - Sewer BG |  | QA | Hydraulics | New | Level 05 | Zone 4 | Sewer BG
|  | Level 05 - Zone 6 - GIT 1 - Sewer BG (SS) |  | QA | Hydraulics | New | Level 05 | Zone 6 | GIT 1 | Sewer BG (SS)
|  | Level 05 - Zone 6 - GIT 2 - Sewer BG (SS) |  | QA | Hydraulics | New | Level 05 | Zone 6 | GIT 2 | Sewer BG (SS)
Columns
|  | Employee trained for task & reviewed installation instructions |  | Employee trained for task and reviewed installation instructions (product QR code / manufacturer's website / instruction manual)
|  | Notify & gain permit from principal contractor/client for inspection |  | Notify and gain permit from principal contractor / client for inspection (hold point)
|  | Latest specifications & standards nominated in ITP |  | Latest specifications and standards nominated in ITP
|  | Setout & alignment as per latest available drawing |  | Setout & alignment as per latest available drawing (include revision below)
|  | Drawing & revision number(s) | Drawing & revision number(s) | Setout & alignment as per latest available drawing (include revision below)
|  | Correct approved materials as per sample register |  | Correct approved materials as per sample register
|  | Excavation undertaken & no issues |  | Excavation undertaken & no issues (Any issues comment below)
|  | Pipe bedding material comply (as per AS 3500) |  | Pipe bedding material comply (as per AS 3500)
|  | Grades, fittings & joints installed to standards |  | Grades, fittings & joints installed to standards
|  | Pipe clean out via water flush |  | Pipe clean out via water flush
|  | Inspection & Testing Prior to Concealment to AS 3500.2 section 13 |  | Inspection & Testing Prior to Concealment to AS 3500.2 section 13
|  | Builder sign off prior concealment |  | Builder sign off prior concealment
|  | Seal open ends with caps & high light to avoid damage |  | Seal open ends with caps & high light to avoid damage
|  | Backfill & Compaction of Material (As per Specification/Geotechnical report) |  | Backfill & Compaction of Material (As per Specification / Geotechnical report)
|  | CCTV on completion & record results |  | CCTV on completion & record results
|  | Final sign off |  | Final sign off - Pass when satisfied to proceed (Any issues please comment & Add photos below)
|  | Area clean | Area clean | Final sign off - Pass when satisfied to proceed (Any issues please comment & Add photos below)
Slab Penetrations Template
| Scope |  |  | qa
Rows
|  | Civil | grouping | civil
|  | Civil |  | qa | slab penetrations template | civil
|  | Hydraulics - New | grouping | hydraulics - new
|  | Level 06 - Zone 4 - Level 6 zone 4 deck - Lv 6 zone 4 |  | qa | level 6 zone 4 deck | new | hydraulics | level 06 | lv 6 zone 4 | zone 4
|  | Level 06 - Zone 4 - Level 6 zone 4 deck - Level 6 zone 4 pour 1 |  | qa | level 6 zone 4 deck | new | hydraulics | level 06 | zone 4 | level 6 zone 4 pour 1
|  | Level 06 - Zone 4 - Level 6 zone 4 deck - Level 6 zone 4 pour 2 |  | qa | level 6 zone 4 deck | new | level 6 zone 4 pour 2 | hydraulics | level 06 | zone 4
Columns
|  | Employee trained for task & reviewed installation instructions |  | Employee trained for task and reviewed installation instructions (product QR code / manufacturer's website / instruction manual)
|  | Notify & gain permit from principal contractor/client for inspection |  | Notify and gain permit from principal contractor / client for inspection (hold point)
|  | Setout & alignment as per drawing |  | Setout & alignment as per drawing (include revision below)
|  | Drawing & revision number(s) | Drawing & revision number(s) | Setout & alignment as per drawing (include revision below)
|  | Approved fire protection material installed (as per approved samples) |  | Approved fire protection material installed (as per approved samples)
|  | Fire protection material installed as per Manufacturer's Instructions |  | Fire protection material installed as per Manufacturer's Instructions
|  | Fire protection material installed in correct locations |  | Fire protection material installed in correct locations
|  | Penetration secured down for concrete pour |  | Penetration secured down for concrete pour
|  | Final sign off |  | Final sign off - Pass when satisfied to proceed (Any issues please comment & Add photo's below)
|  | Area clean | Area clean | Final sign off - Pass when satisfied to proceed (Any issues please comment & Add photo's below)
Stormwater BG
| Scope |  |  | qa
Rows
|  | Civil | grouping | civil
|  | Stormwater Drains - Section 4.1 - 4.2 |  | QA | Civil | Stormwater Drains | Section 4.1 - 4.2
|  | Stormwater Drains - Section 1.1 - 1.2 |  | QA | Civil | Stormwater Drains | Section 1.1 - 1.2
|  | Stormwater Drains - Section 1.2 - 1.3 |  | QA | Civil | Stormwater Drains | Section 1.2 - 1.3
|  | Stormwater Drains - Section GPT 525 Pipe - Building |  | QA | Civil | Stormwater Drains | Section GPT 525 Pipe - Building
|  | Stormwater Drains - Section 1.3 - 1.4/EX.3 |  | QA | Civil | Stormwater Drains | Section 1.3 - 1.4/EX.3
|  | Stormwater Drains - Section 1.4 - 2.1 |  | QA | Civil | Stormwater Drains | Section 1.4 - 2.1
|  | Stormwater Drains - Section 2.1 - 2.2 |  | QA | Civil | Stormwater Drains | Section 2.1 - 2.2
|  | Stormwater Drains - Section 2.1 - Building |  | QA | Civil | Stormwater Drains | Section 2.1 - Building
|  | Stormwater Drains - Section 2.2 - 2.3 |  | QA | Civil | Stormwater Drains | Section 2.2 - 2.3
|  | Stormwater Drains - Section 2.2 - Building |  | QA | Civil | Stormwater Drains | Section 2.2 - Building
|  | Stormwater Drains - Section 2.3 - 2.4 |  | QA | Civil | Stormwater Drains | Section 2.3 - 2.4
|  | Stormwater Drains - Section 2.4 - 2.5 |  | QA | Civil | Stormwater Drains | Section 2.4 - 2.5
|  | Stormwater Drains - Section 2.5 - 3.2 |  | QA | Civil | Stormwater Drains | Section 2.5 - 3.2
|  | Stormwater Drains - Section 2.5 - Building |  | QA | Civil | Stormwater Drains | Section 2.5 - Building
|  | Stormwater Drains - Section 2.5 - 2.6 |  | QA | Civil | Stormwater Drains | Section 2.5 - 2.6
|  | Stormwater Drains - Section 2.6 - 2.7 |  | QA | Civil | Stormwater Drains | Section 2.6 - 2.7
|  | Stormwater Drains - Section 2.6 - Buiding |  | QA | Civil | Stormwater Drains | Section 2.6 - Buiding
|  | Stormwater BG Kavanagh St stage 1 |  | QA | Civil | Stormwater BG Kavanagh St stage 1
|  | Stormwater BG Southern end Kav St |  | QA | Civil | Stormwater BG Southern end Kav St
Columns
|  | Employee trained for task & reviewed installation instructions |  | employee trained for task and reviewed installation instructions (product qr code / manufacturer's website / instruction manual)
|  | Notify & gain permit from principal contractor/client for inspection |  | notify and gain permit from principal contractor / client for inspection (hold point)
|  | Latest specifications & standards nominated in ITP |  | latest specifications and standards nominated in itp
|  | Setout & alignment as per latest available drawing |  | setout & alignment as per latest available drawing (include revision below)
|  | Drawing & revision number(s) | Drawing & revision number(s) | setout & alignment as per latest available drawing (include revision below)
|  | Correct approved materials as per sample register |  | correct approved materials as per sample register
|  | Excavation undertaken & no issues |  | excavation undertaken & no issues (any issues comment below)
|  | Pipe bedding material (as per AS 500) |  | pipe bedding material (as per as 500)
|  | Grades, fittings & joints installed to standards |  | grades, fittings & joints installed to standards
|  | Pipe clean out via water flush |  | pipe clean out via water flush
|  | Inspection & Testing Prior to Concealment to AS 3500.2 section 13 |  | inspection and testing prior to concealment to as 3500.2 section 13
|  | Builder sign off prior concealment |  | builder sign off prior concealment
|  | Seal open ends with caps & high light to avoid damage |  | seal open ends with caps & high light to avoid damage
|  | Backfill & Compaction of Material (As per Specification/Geotechnical report) |  | backfill & compaction of material (as per specification / geotechnical report)
|  | CCTV on completion & record results |  | cctv on completion & record results (if applicable)
|  | Final sign off |  | final sign off - pass when satisfied to proceed (any issues please comment & add photos below)
|  | Area clean | Area clean | final sign off - pass when satisfied to proceed (any issues please comment & add photos below)