## Sheet1
3.1 | Pre-construction Photos | Photos of worksite including vehicle access points. Photos of any existing defects/damage. | Coverage of whole site | Photos saved | D1.4 | PM | 3.1 - Pre-construction Photos | Inspection Point: Quality Control Activity - Photos of worksite including vehicle access points. Photos of any existing defects/damage. | Acceptance Criteria - Coverage of whole site | Verifying Document - Photos saved | Reference: Contract Specs/Standards - D1.4 | Inspection Point/Signature CHAR(AMP) Date - PM | 3.1 - Pre-construction Photos
3.2 | Verify Construction Drawings | Verify Construction Drawings that are in the site folder are the latest revision. | Latest drawings approved | Drawings Register |  | PM | 3.2 - Verify Construction Drawings | Inspection Point: Quality Control Activity - Verify Construction Drawings that are in the site folder are the latest revision. | Acceptance Criteria - Latest drawings approved | Verifying Document - Drawings Register | Reference: Contract Specs/Standards - | Inspection Point/Signature CHAR(AMP) Date - PM | Inspection Point: Quality Control Activity - Photos of worksite including vehicle access points. Photos of any existing defects/damage.
3.3 | Road Authority Notifications | Corridor access Permit. Block by block Temporary Traffic Management Plans. | Permit CHAR(AMP) Traffic Plan approved | Work Access Permit CHAR(AMP) TMP | C1.09, D1.4 | PM | 3.3 - Road Authority Notifications | Inspection Point: Quality Control Activity - Corridor access Permit. Block by block Temporary Traffic Management Plans. | Acceptance Criteria - Permit CHAR(AMP) Traffic Plan approved | Verifying Document - Work Access Permit CHAR(AMP) TMP | Reference: Contract Specs/Standards - C1.09, D1.4 | Inspection Point/Signature CHAR(AMP) Date - PM | Acceptance Criteria - Coverage of whole site
3.4 | Management Plan | HCHAR(AMP)S Plan Environmental Plan Quality Assurances | Plans CHAR(AMP) Safety Measures in place | HCHAR(AMP)S Plan, Method Statement | D1.3 | PM, CR | 3.4 - Management Plan | Inspection Point: Quality Control Activity - HCHAR(AMP)S Plan Environmental Plan Quality Assurances | Acceptance Criteria - Plans CHAR(AMP) Safety Measures in place | Verifying Document - HCHAR(AMP)S Plan, Method Statement | Reference: Contract Specs/Standards - D1.3 | Inspection Point/Signature CHAR(AMP) Date - PM, CR | Verifying Document - Photos saved
3.5 | Public Notification | Notice of works to properties in the construction zone in each block Notification to Rubbish collection contractor. Project Signage | 48 hours prior notification | Letter to residents | D1.10 | PM | 3.5 - Public Notification | Inspection Point: Quality Control Activity - Notice of works to properties in the construction zone in each block Notification to Rubbish collection contractor. Project Signage | Acceptance Criteria - 48 hours prior notification | Verifying Document - Letter to residents | Reference: Contract Specs/Standards - D1.10 | Inspection Point/Signature CHAR(AMP) Date - PM | Reference: Contract Specs/Standards - D1.4
3.6 | Shutdown/Isolation | Shutdown/Isolation process verified in each block closure | Shutdown process verified | Notification letters | C1.16, D2.7.8 | PS | 3.6 - Shutdown/Isolation | Inspection Point: Quality Control Activity - Shutdown/Isolation process verified in each block closure | Acceptance Criteria - Shutdown process verified | Verifying Document - Notification letters | Reference: Contract Specs/Standards - C1.16, D2.7.8 | Inspection Point/Signature CHAR(AMP) Date - PS | Inspection Point/Signature CHAR(AMP) Date - PM
3.7 | Construction Set Out | Correctly mark out the position of the new pipelines for construction. | Construction Plans checked | Construction Plans | D2.7.1 | PS, CR | 3.7 - Construction Set Out | Inspection Point: Quality Control Activity - Correctly mark out the position of the new pipelines for construction. | Acceptance Criteria - Construction Plans checked | Verifying Document - Construction Plans | Reference: Contract Specs/Standards - D2.7.1 | Inspection Point/Signature CHAR(AMP) Date - PS, CR | 3.2 - Verify Construction Drawings
3.8 | Pre-Excavation Permits | Permit to excavate for the location has been endorsed by an authorised person. • Existing service plans CHAR(AMP) locates • Close approach permits • Notifiable works | Permit to excavate endorsed | Ground Disturbance Permit | D1.7 | PS | 3.8 - Pre-Excavation Permits | Inspection Point: Quality Control Activity - Permit to excavate for the location has been endorsed by an authorised person. • Existing service plans CHAR(AMP) locates • Close approach permits • Notifiable works | Acceptance Criteria - Permit to excavate endorsed | Verifying Document - Ground Disturbance Permit | Reference: Contract Specs/Standards - D1.7 | Inspection Point/Signature CHAR(AMP) Date - PS | Inspection Point: Quality Control Activity - Verify Construction Drawings that are in the site folder are the latest revision.
4.1 | Pipe CHAR(AMP) Fitting Inspections | Visual check of materials delivered: • Correct Material CHAR(AMP) dimensions • Condition CHAR(AMP) Quantity • Free of defects – surface abrasion, ovality, not kinked or crushed • Batch/serial numbers present | Correct material CHAR(AMP) no defects | Packing Slips | D2.4,D3.3, D4.3, D5.3, D8.3 | PS | 4.1 - Pipe CHAR(AMP) Fitting Inspections | Inspection Point: Quality Control Activity - Visual check of materials delivered: • Correct Material CHAR(AMP) dimensions • Condition CHAR(AMP) Quantity • Free of defects – surface abrasion, ovality, not kinked or crushed • Batch/serial numbers present | Acceptance Criteria - Correct material CHAR(AMP) no defects | Verifying Document - Packing Slips | Reference: Contract Specs/Standards - D2.4,D3.3, D4.3, D5.3, D8.3 | Inspection Point/Signature CHAR(AMP) Date - PS | Acceptance Criteria - Latest drawings approved
4.2 | Pipe CHAR(AMP) Fitting Storage | Stored as per manufacturers specifications including maximum height limits and safely chocked in place. • All pipes are end capped. • No scoring of pipe more than 10% of thickness. • No damage to epoxy coating on Ductile fittings. | Stored as per manufacturer | Manufacturer’s Storage Instructions |  | PS, CR | 4.2 - Pipe CHAR(AMP) Fitting Storage | Inspection Point: Quality Control Activity - Stored as per manufacturers specifications including maximum height limits and safely chocked in place. • All pipes are end capped. • No scoring of pipe more than 10% of thickness. • No damage to epoxy coating on Ductile fittings. | Acceptance Criteria - Stored as per manufacturer | Verifying Document - Manufacturer’s Storage Instructions | Reference: Contract Specs/Standards - | Inspection Point/Signature CHAR(AMP) Date - PS, CR | Verifying Document - Drawings Register
5.1 | Trench Excavation | Trench width to be sufficient to safely lay the pipe (including shoring if required) and compact the side support of the new pipe. Bedding details below; Sufficient room to enable the pipe, joint, bed, haunch or surround shown in the drawings to be accommodated. Trench depth to enable pipe to be laid with the designed cover as shown on construction plans. If trench bottom to be suitable to compact pipe bedding as support pipe. | Trench dimensions correct | Daily Site Diary | D2.6, D2.7 | PS | 5.1 - Trench Excavation | Inspection Point: Quality Control Activity - Trench width to be sufficient to safely lay the pipe (including shoring if required) and compact the side support of the new pipe. Bedding details below; Sufficient room to enable the pipe, joint, bed, haunch or surround shown in the drawings to be accommodated. Trench depth to enable pipe to be laid with the designed cover as shown on construction plans. If trench bottom to be suitable to compact pipe bedding as support pipe. | Acceptance Criteria - Trench dimensions correct | Verifying Document - Daily Site Diary | Reference: Contract Specs/Standards - D2.6, D2.7 | Inspection Point/Signature CHAR(AMP) Date - PS | Reference: Contract Specs/Standards -
5.2 | Encountered Services | Block by block ensure existing live services are not unnecessarily damaged by works. Repair any services that are temporarily removed during construction. Record any services found. | Existing services not damaged | Encountered Services Record | D1.7, D2.7.7 | PS | 5.2 - Encountered Services | Inspection Point: Quality Control Activity - Block by block ensure existing live services are not unnecessarily damaged by works. Repair any services that are temporarily removed during construction. Record any services found. | Acceptance Criteria - Existing services not damaged | Verifying Document - Encountered Services Record | Reference: Contract Specs/Standards - D1.7, D2.7.7 | Inspection Point/Signature CHAR(AMP) Date - PS | Inspection Point/Signature CHAR(AMP) Date - PM
5.3 | Pipe Installation | Interior of each pipe visually inspected to ensure free of debris. Re-cap end of pipe after installation. Check pipe installed at correct depth. Ensure all collars are free from contamination in McDougall St berm | Pipes free of debris CHAR(AMP) correctly installed | Daily Site Diary | D2.5, D2.7, D8.4.2 | PS | 5.3 - Pipe Installation | Inspection Point: Quality Control Activity - Interior of each pipe visually inspected to ensure free of debris. Re-cap end of pipe after installation. Check pipe installed at correct depth. Ensure all collars are free from contamination in McDougall St berm | Acceptance Criteria - Pipes free of debris CHAR(AMP) correctly installed | Verifying Document - Daily Site Diary | Reference: Contract Specs/Standards - D2.5, D2.7, D8.4.2 | Inspection Point/Signature CHAR(AMP) Date - PS | 3.3 - Road Authority Notifications
5.4 | Concrete Pre-Pour Inspection | Check dimensions of formwork match details in the Construction Drawings. Check pipe fitting joints are clear of concrete pour. Thrust blocks to be poured against good solid natural ground. | Thrust blocks against solid ground | Daily Site Diary CHAR(AMP) Photos | D5.1, D5.3.2, D5.7 | PS, CR | 5.4 - Concrete Pre-Pour Inspection | Inspection Point: Quality Control Activity - Check dimensions of formwork match details in the Construction Drawings. Check pipe fitting joints are clear of concrete pour. Thrust blocks to be poured against good solid natural ground. | Acceptance Criteria - Thrust blocks against solid ground | Verifying Document - Daily Site Diary CHAR(AMP) Photos | Reference: Contract Specs/Standards - D5.1, D5.3.2, D5.7 | Inspection Point/Signature CHAR(AMP) Date - PS, CR | Inspection Point: Quality Control Activity - Corridor access Permit. Block by block Temporary Traffic Management Plans.
5.5 | Hydrant Depth | Confirm depth requirements have been met; Hydrant outlet: 200mm min. to 400mm max. | Hydrant depth verified | Daily Site Diary | D5.5 | PS | 5.5 - Hydrant Depth | Inspection Point: Quality Control Activity - Confirm depth requirements have been met; Hydrant outlet: 200mm min. to 400mm max. | Acceptance Criteria - Hydrant depth verified | Verifying Document - Daily Site Diary | Reference: Contract Specs/Standards - D5.5 | Inspection Point/Signature CHAR(AMP) Date - PS | Acceptance Criteria - Permit CHAR(AMP) Traffic Plan approved
5.6 | Compaction Testing | Confirm trenches in paved areas are compacted to standard block by block. | Compaction confirmed | Clegg Record Sheet | D2.7.10 | PS | 5.6 - Compaction Testing | Inspection Point: Quality Control Activity - Confirm trenches in paved areas are compacted to standard block by block. | Acceptance Criteria - Compaction confirmed | Verifying Document - Clegg Record Sheet | Reference: Contract Specs/Standards - D2.7.10 | Inspection Point/Signature CHAR(AMP) Date - PS | Verifying Document - Work Access Permit CHAR(AMP) TMP
5.7 | Watermain Pressure Testing | Hydrostatic pressure test on new pipeline and fittings block by block. | Pressure test passed | Pressure Test Record Sheet | D2.9.1, AS/NSZ 2566.2:2002 Section 6 | PS, CR | 5.7 - Watermain Pressure Testing | Inspection Point: Quality Control Activity - Hydrostatic pressure test on new pipeline and fittings block by block. | Acceptance Criteria - Pressure test passed | Verifying Document - Pressure Test Record Sheet | Reference: Contract Specs/Standards - D2.9.1, AS/NSZ 2566.2:2002 Section 6 | Inspection Point/Signature CHAR(AMP) Date - PS, CR | Reference: Contract Specs/Standards - C1.09, D1.4
5.8 | Watermain Sterilization | Flushing and sterilizing full length of new pipeline and fittings block by block. | Sterilization completed | Sterilization Record Sheet | D2.9.1, AS/NSZ 2566.2:2002 Section 6 | PS, CR | 5.8 - Watermain Sterilization | Inspection Point: Quality Control Activity - Flushing and sterilizing full length of new pipeline and fittings block by block. | Acceptance Criteria - Sterilization completed | Verifying Document - Sterilization Record Sheet | Reference: Contract Specs/Standards - D2.9.1, AS/NSZ 2566.2:2002 Section 6 | Inspection Point/Signature CHAR(AMP) Date - PS, CR | Inspection Point/Signature CHAR(AMP) Date - PM
5.9 | As-built Information | Capture data for all new construction work. | Redline mark-up plan submitted | Redline Mark-up Plan | C1.22 | PM | 5.9 - As-built Information | Inspection Point: Quality Control Activity - Capture data for all new construction work. | Acceptance Criteria - Redline mark-up plan submitted | Verifying Document - Redline Mark-up Plan | Reference: Contract Specs/Standards - C1.22 | Inspection Point/Signature CHAR(AMP) Date - PM | 3.4 - Management Plan
6.1 | Final Inspection of Works | Work is inspected by the authorised person and complies with the nominated specification/standards | Work inspected CHAR(AMP) complies with standards | Practical Completion Certificate |  | PM | 6.1 - Final Inspection of Works | Inspection Point: Quality Control Activity - Work is inspected by the authorised person and complies with the nominated specification/standards | Acceptance Criteria - Work inspected CHAR(AMP) complies with standards | Verifying Document - Practical Completion Certificate | Reference: Contract Specs/Standards - | Inspection Point/Signature CHAR(AMP) Date - PM | Inspection Point: Quality Control Activity - HCHAR(AMP)S Plan Environmental Plan Quality Assurances
Acceptance Criteria - Plans CHAR(AMP) Safety Measures in place
Verifying Document - HCHAR(AMP)S Plan, Method Statement
Reference: Contract Specs/Standards - D1.3
Inspection Point/Signature CHAR(AMP) Date - PM, CR
3.5 - Public Notification
Inspection Point: Quality Control Activity - Notice of works to properties in the construction zone in each block Notification to Rubbish collection contractor. Project Signage
Acceptance Criteria - 48 hours prior notification
Verifying Document - Letter to residents
Reference: Contract Specs/Standards - D1.10
Inspection Point/Signature CHAR(AMP) Date - PM
3.6 - Shutdown/Isolation
Inspection Point: Quality Control Activity - Shutdown/Isolation process verified in each block closure
Acceptance Criteria - Shutdown process verified
Verifying Document - Notification letters
Reference: Contract Specs/Standards - C1.16, D2.7.8
Inspection Point/Signature CHAR(AMP) Date - PS
3.7 - Construction Set Out
Inspection Point: Quality Control Activity - Correctly mark out the position of the new pipelines for construction.
Acceptance Criteria - Construction Plans checked
Verifying Document - Construction Plans
Reference: Contract Specs/Standards - D2.7.1
Inspection Point/Signature CHAR(AMP) Date - PS, CR
3.8 - Pre-Excavation Permits
Inspection Point: Quality Control Activity - Permit to excavate for the location has been endorsed by an authorised person. • Existing service plans CHAR(AMP) locates • Close approach permits • Notifiable works
Acceptance Criteria - Permit to excavate endorsed
Verifying Document - Ground Disturbance Permit
Reference: Contract Specs/Standards - D1.7
Inspection Point/Signature CHAR(AMP) Date - PS
4.1 - Pipe CHAR(AMP) Fitting Inspections
Inspection Point: Quality Control Activity - Visual check of materials delivered: • Correct Material CHAR(AMP) dimensions • Condition CHAR(AMP) Quantity • Free of defects – surface abrasion, ovality, not kinked or crushed • Batch/serial numbers present
Acceptance Criteria - Correct material CHAR(AMP) no defects
Verifying Document - Packing Slips
Reference: Contract Specs/Standards - D2.4,D3.3, D4.3, D5.3, D8.3
Inspection Point/Signature CHAR(AMP) Date - PS
4.2 - Pipe CHAR(AMP) Fitting Storage
Inspection Point: Quality Control Activity - Stored as per manufacturers specifications including maximum height limits and safely chocked in place. • All pipes are end capped. • No scoring of pipe more than 10% of thickness. • No damage to epoxy coating on Ductile fittings.
Acceptance Criteria - Stored as per manufacturer
Verifying Document - Manufacturer’s Storage Instructions
Reference: Contract Specs/Standards -
Inspection Point/Signature CHAR(AMP) Date - PS, CR
5.1 - Trench Excavation
Inspection Point: Quality Control Activity - Trench width to be sufficient to safely lay the pipe (including shoring if required) and compact the side support of the new pipe. Bedding details below; Sufficient room to enable the pipe, joint, bed, haunch or surround shown in the drawings to be accommodated. Trench depth to enable pipe to be laid with the designed cover as shown on construction plans. If trench bottom to be suitable to compact pipe bedding as support pipe.
Acceptance Criteria - Trench dimensions correct
Verifying Document - Daily Site Diary
Reference: Contract Specs/Standards - D2.6, D2.7
Inspection Point/Signature CHAR(AMP) Date - PS
5.2 - Encountered Services
Inspection Point: Quality Control Activity - Block by block ensure existing live services are not unnecessarily damaged by works. Repair any services that are temporarily removed during construction. Record any services found.
Acceptance Criteria - Existing services not damaged
Verifying Document - Encountered Services Record
Reference: Contract Specs/Standards - D1.7, D2.7.7
Inspection Point/Signature CHAR(AMP) Date - PS
5.3 - Pipe Installation
Inspection Point: Quality Control Activity - Interior of each pipe visually inspected to ensure free of debris. Re-cap end of pipe after installation. Check pipe installed at correct depth. Ensure all collars are free from contamination in McDougall St berm
Acceptance Criteria - Pipes free of debris CHAR(AMP) correctly installed
Verifying Document - Daily Site Diary
Reference: Contract Specs/Standards - D2.5, D2.7, D8.4.2
Inspection Point/Signature CHAR(AMP) Date - PS
5.4 - Concrete Pre-Pour Inspection
Inspection Point: Quality Control Activity - Check dimensions of formwork match details in the Construction Drawings. Check pipe fitting joints are clear of concrete pour. Thrust blocks to be poured against good solid natural ground.
Acceptance Criteria - Thrust blocks against solid ground
Verifying Document - Daily Site Diary CHAR(AMP) Photos
Reference: Contract Specs/Standards - D5.1, D5.3.2, D5.7
Inspection Point/Signature CHAR(AMP) Date - PS, CR
5.5 - Hydrant Depth
Inspection Point: Quality Control Activity - Confirm depth requirements have been met; Hydrant outlet: 200mm min. to 400mm max.
Acceptance Criteria - Hydrant depth verified
Verifying Document - Daily Site Diary
Reference: Contract Specs/Standards - D5.5
Inspection Point/Signature CHAR(AMP) Date - PS
5.6 - Compaction Testing
Inspection Point: Quality Control Activity - Confirm trenches in paved areas are compacted to standard block by block.
Acceptance Criteria - Compaction confirmed
Verifying Document - Clegg Record Sheet
Reference: Contract Specs/Standards - D2.7.10
Inspection Point/Signature CHAR(AMP) Date - PS
5.7 - Watermain Pressure Testing
Inspection Point: Quality Control Activity - Hydrostatic pressure test on new pipeline and fittings block by block.
Acceptance Criteria - Pressure test passed
Verifying Document - Pressure Test Record Sheet
Reference: Contract Specs/Standards - D2.9.1, AS/NSZ 2566.2:2002 Section 6
Inspection Point/Signature CHAR(AMP) Date - PS, CR
5.8 - Watermain Sterilization
Inspection Point: Quality Control Activity - Flushing and sterilizing full length of new pipeline and fittings block by block.
Acceptance Criteria - Sterilization completed
Verifying Document - Sterilization Record Sheet
Reference: Contract Specs/Standards - D2.9.1, AS/NSZ 2566.2:2002 Section 6
Inspection Point/Signature CHAR(AMP) Date - PS, CR
5.9 - As-built Information
Inspection Point: Quality Control Activity - Capture data for all new construction work.
Acceptance Criteria - Redline mark-up plan submitted
Verifying Document - Redline Mark-up Plan
Reference: Contract Specs/Standards - C1.22
Inspection Point/Signature CHAR(AMP) Date - PM
6.1 - Final Inspection of Works
Inspection Point: Quality Control Activity - Work is inspected by the authorised person and complies with the nominated specification/standards
Acceptance Criteria - Work inspected CHAR(AMP) complies with standards
Verifying Document - Practical Completion Certificate
Reference: Contract Specs/Standards -
Inspection Point/Signature CHAR(AMP) Date - PM