## Table 1
[6 empty] | Inspection and Test Plan - Control and Supervision of the Works | [10 empty] | Doc ID: FH-ZU2-QU-ITP049 REV: 0
Client: Melbourne Airport | [6 empty] | Contract No: | [6 empty] | Prepared By: Ahmad El Wazer
Project: Taxiway Zulu | [10 empty] | Reviewed By: Jamal Khodr | [5 empty] | Date: 03/07/2025
Construction Process: ALER 3 AGL Equipment Installation | [10 empty] | Approved By: Marco Poggenberg | [5 empty] | Date: 03/07/2025
Specifications: ZULU-BECA-001-SPC-00003, ZULU-BECA-001-SPC-00005, Drawings
Structure / Component: AGL Equipment within ALER 3
Lot No: |  |  | Lot Details: | [5 empty] | Lot size/Quantity: |  |  | Date:
Item No. |  | Task/Activity Description | Inspection/Test | [11 empty] | HP/ WP/ AP/ IP/ TP/ SCP | Responsibility |  | Checked by:
|  |  | Frequency |  | Acceptance Criteria |  |  |  | Reference Documents |  | Inspection/ Test Method | Record of conformity |  |  |  | Project Engineer / Site Engineer |  | Principal’s Rep. | FH | Date
1 |  | Preliminary Activities – Permits, Documentation, Approvals, Survey Documentation
1.1 |  | Check for correct documentation | Prior to commencing activity |  | Ensure that all employees and subcontractors are: - using the correct and complete set of drawings. - all drawings are the latest revision. |  |  |  | Drawings / Aconex Register |  | Verify | Drawings and drawing registers |  |  | HP* | Project Engineer / Site Engineer
1.2 |  | Implementation of all measures and controls | Prior to commencing activity |  | All necessary measures and controls being implemented, that is PSP, EMP, TMP, SWMS & WP. |  |  |  | PSP, EMP, TMP, JSEA, SWMS, WP |  | Visual inspection | This ITP signed |  |  | HP* | Project Engineer / Site Engineer
1.3 |  | Survey Checks | Prior to commencing activity |  | Survey set out to be completed for all assets |  |  |  | Drawings |  | Verify | This ITP signed |  |  | HP* | Project Engineer / Site Engineer
1.4 |  | Submission & approval of shop drawings | Prior to commencing activity |  | HOLD POINT Submit shop drawings to the principal’s representative for approval prior to fabrication commencement. Items to include but not limited to:  DB-AGL1  DB-AGL2  CCRs  SACs  SCOs  ILCMS equipment |  |  |  | ZULU-BECA-001-SPC- 00005 C2100 Page 10 Drawings 030- 3100 set Approved Shop drawings |  | Verify | Aconex Reference |  |  | HP | Project Engineer / Site Engineer /Principal’s Representative
1.5 |  | Material Submission | Prior to commencing activity |  | HOLD POINT Items to include but not limited to:  Control Systems  Power Control  Switchgear  Cables |  |  |  | Drawings / Aconex Register |  | Verify | Aconex Reference |  |  | HP | Project Engineer / Site Engineer /Principal’s Representative
1.6 |  | Off-site Inspections | Each Lot |  | WITNESS POINT Switchboards shall be fully tested before leaving the manufacturer’s premises. Inspection and attendance on site for Factory Acceptance Testing for: - Switchboards - Distribution Boards Following these inspections FAT testing shall be submitted. |  |  |  | ZULU-BECA- 001-SPC- 00005 C2121.20 Page 58 AS/NZS 3000 Drawings 030- 3100 set |  | Verify | This ITP Signed Factory Acceptance Tests |  |  | WP TP | Project Engineer / Site Engineer /Principal’s Representative
2 |  | Construction
2.1 |  | Delivery of Materials to site | Each Lot |  | Inspection of materials whilst still loaded on the truck prior to accepting the delivery on site. Identify any damage/defects prior to unloading of the material. |  |  |  | ZULU-BECA- 001-SPC- 00005 Drawings |  | Visual Inspection | This ITP Signed Materials Inspection Checklist on ConQA |  |  | IP | Project Engineer / Site Engineer
2.2 |  | Inspection of installed works | Each Lot |  | AGL contractor to inspect the installation to confirm suitability and as per design, including but not limited to:  Pits  Conduits  Slabs  Structure  Cable trays |  |  |  | Drawings |  | Visual Inspection | This ITP Signed |  |  | IP | Project Engineer / Site Engineer
2.5 |  | SCO | Each Lot |  | Supply and installation of (Nos.04) SCOs as per drawings and approved shop drawings. Including but not limited to:  Cubicle to be plinth mounted  Cabling  Labelling |  |  |  | AS/NZS 3000 Drawings 030- 3100 set Shop Drawings |  | Visual Inspection | This ITP Signed ADB Safegate ITC |  |  | IP | Project Engineer / Site Engineer
2.6 |  | SAC | Each Lot |  | Supply and Installation of (Nos 04) SACs (with 36 x SDH-100-2000-PH Surge Diverters per Cubicle) as per drawings and approved shop drawings. Including but not limited to:  Cubicle to be plinth mounted  Conduit hood installed  Cabling  Labelling |  |  |  | AS/NZS 3000 Drawings 030- 3100 set Shop Drawings |  | Visual Inspection | This ITP Signed ADB Safegate ITC |  |  | IP | Project Engineer / Site Engineer
2.7 |  | ILCMs | Each Lot |  | Supply and Installation of ILCMs equipment (including NCU cabinet, ASP cabinet, and existing SFAL) as per drawings and approved shop drawings. Including but not limited to:  TFO 200W NO E 6.6A/6.6A 50/60HZ Installed  SCF Complete Capsuled Installed  Two SCI Series Circuit Inductors Installed  Cabling  Labelling |  |  |  | AS/NZS 3000 Drawings 030- 3100 set Shop Drawings |  | Visual Inspection | This ITP Signed ADB Safegate ITC |  |  | IP | Project Engineer / Site Engineer
2.8 |  | SCM | Each Lot |  | Supply and Installation of SCM equipment as per drawings and approved shop drawings. Including but not limited to:  SCM Cabinet Modems Labelled  OFLEX CLASSIC 110 CY 2x1.5 installed from CCRs to SCM Cabinet  OFLEX Cables tied and labelled on the cable tray  OFLEX Cables terminated inside the SCM Cabinet  SCM Cabinet Energised |  |  |  | AS/NZS 3000 Drawings 030- 3100 set |  | Verify | This ITP Signed ADB Safegate ITC |  |  | TP | Project Engineer / Site Engineer
2.9 |  | CCR | Each Lot |  | Supply and Installation of CCR equipment as per drawings and approved shop drawings. Including but not limited to:  7.5 kW CRE CCR’s to be installed  CCR Power supply Cables with 50A Plugs Installed  Cables form CCR SCO to the 2 SCI Series Circuit Inductors with Female Connectors Installed |  |  |  | AS/NZS 3000 Drawings 030- 3100 set |  | Verify | This ITP Signed ADB Safegate ITC |  |  | TP | Project Engineer / Site Engineer
2.11 |  | DBs | Each Lot |  | Confirm the following items are constructed in accordance with IFC design and specification.  Size, colour, location  Plinth (if required)  Secure and anchored.  Labels  Tightness & alignment  All wiring tidy and neat |  |  |  | ZULU-BECA- 001-SPC- 00005 C2100.2 AS/NZS 3000 Drawings 030- 3100 set |  | Verify | This ITP Signed ADB Safegate ITC |  |  | TP | Project Engineer / Site Engineer
2.12 |  | Cabling – Mains, Submains, | Each Lot |  | Confirm the following items are constructed in accordance with IFC design and specification.  Type, size, colour, quantities, location  Secure Verify and confirm the following tests as per AS/NZS 3000 (not limited to):  Polarity Check  Cable Loop Resistance (Ohms)  Insulation Resistance (Core-Core& Core to Earth) |  |  |  | ZULU-BECA- 001-SPC- 00005 C2111.5 AS/NZS 3000 Drawings 030- 3100 set |  | Verify | This ITP Signed ADB Safegate ITC |  |  | TP | Project Engineer / Site Engineer
Final Inspection The signature below verifies that this ITP has been completed in accordance with the Fulton Hogan’s Quality system Procedures and verifies lot compliance with specifications. Print Name: Position: Signature: Date: / /
Legend:
| HP | Hold Point |  | Work shall not proceed past the HP until released by the Principal’s Representative |  |  |  | IP |  | Inspection point |  |  | Formal Inspection to be done and recorded
| HP* | Fulton Hogan Hold Point |  | Work shall not proceed past the HP* until released by Fulton Hogan |  |  |  | TP |  | Test Point |  |  | Product compliance test to be undertaken and recorded/reported
| WP | Witness Point |  | An inspection which must be witnessed by the Principal’s Representative |  |  |  | SCP |  | Survey conformance point |  |  | A qualified surveyor to check product/section/structure and report
| AP | Approval Point |  | Written or verbal approval given by the Principal’s Representative
Notes