## ITP Cover Page
Streetlighting Inspection and Test Plan
Project: SH29 Tauriko West Enabling Project
Number and Revision: DN1210 - 027 - Rev 1
SECTION 1 – GENERAL DETAILS
Project Name: |  |  | SH29 Tauriko West Enabling Project |  |  |  |  | ITP Number: |  | 027
Project Number: |  |  | DN1210 |  |  |  |  | ITP Status: |  | Final
ITP Description: |  |  | Streetlight Inspection and Test Plan |  |  |  |  | Revision: |  | 1
Contract Number: |  |  | 8287 |  |  |  |  | Drawing Sets: |  | 23273502 - WSP-DR-LIG
Customer: |  |  | Waka Kotahi |  |  |  |  | Specification: |  | SH29 Tauriko West Enabling Works Contract No.NZTA8287 Section 23
Quality Specified: |  |  | ISO9001: 2015
Review / Update History | [8 empty] | Verification Activity
Rev: | Status: | Date: |  | Reviewed By: |  | Revision Details: |  |  | Activity Key |  |  | Responsibilities Key
0 | Draft for Approval |  |  | Cordelia Girdler-Brown and Chris Benson |  | Streetlighting Inspection and Test Plan |  |  | A | Action |  | ENG | Engineer / Engineer's Rep
[9 empty] | B | Report by Breach |  | CR | Customer Rep
[9 empty] | C | Check |  | PD | Project Director
[9 empty] | D | Dimension Inspection |  | PM | Project Manager
[9 empty] | E | Examine |  | OP | Operations Manager
[9 empty] | HP | Hold Point (Engineer) |  | HSE | HSE Manager / Rep
[9 empty] | H | Hold Point (Internal) |  | QM | QA Manager / Rep
[9 empty] | I | Inspection |  | PE | Project Engineer
[9 empty] | M | Monitor on Random Basis |  | SE | Site Engineer
[9 empty] | O | Operation |  | QE | Quality Engineer
[9 empty] | R | Review |  | SUP | Superintendent / Supervisor
[9 empty] | S | Subcontractor |  | SV | Surveyor
[9 empty] | V | Visual Verification |  | ITP | Third Party Inspector
[9 empty] | W | Witness Point |  | SPEC | Specialist
SECTION 2A – ITP Approval | [7 empty] | SECTION 2B – ITP CLOSEOUT
Position |  | Name: |  |  | Signature: |  | Date: | Position | Name: |  | Signature: |  |  | Date:
Downer PM |  | Chris Benson | [5 empty] | Downer PM | Chris
Downer QM |  | Cordelia Girdler-Brown |  |  |  |  | 2025-01-13 | Downer QM | Cordelia Girdler-Brown
Client (If Applicable) | [7 empty] | Client (If Applicable)

## STREETLIGHT
Streetlighting Inspection and Test Plan
SH29 Tauriko West Enabling Project
Number and Revision: DN1210 - 027-001 - Rev 0
Item No. | Inspection and Test Point | Acceptance / Conformance Criteria | Standard / Specification | Verifying Document | Frequency | Verification Activity |  | Downer Conformance of Compliance Signoff
[6 empty] | Activity | By | Downer Signature | Date | Comments / Closeout Details | ENGINEERS COMMENTS - Date: | DOWNER RESPONSE - Date:
SECTION 1 – MATERIAL, PERSONNEL & THIRD PARTY APPROVAL
1.1 | Pre-Construction Set Up | [11 empty] | Final
1.1.1 | Underground Services | Pothole all services prior to commencement of trenching. Suitably protect the existing services from construction damage. | PS23.5.3 b) | Survey Data/Site Photo | Pre - excavation | H | PE/SE | [5 empty] | 1
1.1.2 | Ducting and Cabling Route | Confirm on site the exact location of cabling routes before trenching. Where connecting and or coordinating with existing services, engineers shall make local modifications necessary for the correct operation of the entire system. | PS 23.1.5 p) & 23.5.3 a) | Survey data/Comms with Client | Prior to Installation | H | PE
1.1.3 | Location of Lighting Poles, Cameras, Cable Pits and Montrose Boxes | Confirm with surveyor and mark out the exact locations of lighting poles, Cameras, Cable Pits and Montrose boxes before installation. | IFC Drawings | Survey data/Comms with Client | Prior to Installation | H | PE
1.2 | Material Testing and Approval
1.2.1 | Bedding and Overlay | Coarse Sand | PS23.11.8.a) ii-iii | Coase Sand - PSD Report | Before construction | HP | ENG
1.2.2 | Backfilling | Under roads and paved areas: Coarse sand, controlled low strength material or fine crushed rock. In topsoil areas: Complete the backfilling with topsoil for at least the top 50mm. | PS23.11.8.a) ii-iii | Material data sheet and engineers approval | Before construction | HP | ENG |  |  | Backfill materials will either be site excavated GAP65 which had been approved at Earthworks stage) or Soil at berm area.
1.2.3 | Ducts and Fittings | Use heavy duty HD PVC for underground services. Use best practice PVC where possible. Orange colour for all conduits containing consumer mains, sub-mains or final sub-circuits cabling | PS23.11.8.a) iv | Material data sheet and engineers approval | Before construction | HP | ENG |  |  | Same power ducts applied as Utility works
1.2.4 | Cable Pit | Aco Cablemate Polycrete "type 66" Dimension: 665mm x 665mm x 620mm with heavy duty steel lid. | PS 23.1.5 d) & Drawing 0122 | Material data sheet and engineers approval | Before construction | HP | ENG
1.2.5 | Montrose Box | Provide MSB-NMB shop drawings complete with wiring schematics for review and approval by the Engineer prior to construction. | PS 23.1.5.a) ii | Shop Drawings and approval | Prior to Purchase | HP | ENG
1.2.6 | Pad, Hasp and Staple | Supply new Montrose Boxes on concrete plinth as per Electrical Services drawings. Box need to be fitted with a stainless steel hasp and staple brackets to allow for Waka Kotahi to fit their own padlock onto it. | PS 23.1.3.b) & 23.1.5 a) ii; Drawing 0413, 0411, 0412. | Material data sheet and engineers approval | Before construction | HP | ENG
1.2.7 | Luminaires & Poles -WK & TCC Redwood Ln RAB | Luminaire and Pole types shall be supplied and installed as detailed on the drawings or as per instruction of Client Luminaire Controller - PDL- 56SS10. | PS 23.1.5 g) & Drawing 0411, 0412 | Material data sheet and engineers approval | Before each Installation | HP | ENG |  |  | Purchase of Luminaires/Poles already approved by Client. PE/SE need to check on site to guarantee right type of luminaries and poles are installed at specific location.
1.2.8 | Luminaires - Underpass | Luminaire and Pole types shall be supplied as detailed on the drawings or as per instruction of Client. Luminaires Controller - CASAMBI "CBU-TED" procured directly from Energy Light NZ. | PS 23.1.5 g) & Drawing 0412 | Material data sheet and engineers approval | Before each Installation | HP | ENG |  |  | PE/SE need to check on site to guarantee right type of luminaries and switch are installed at specific location.
1.2.9 | CCTV Cameras and PoE Switches | TCC Approved IP67 IK10+ With Weatherproof Housing , Vandal Resistant and PoE Dome (HD1080p, 2MP), Sensitivity down to 0.01 lux Have intelligent auto exposure to offer front and back light compensation. TCC approved Power-over- Ethernet (PoE) | PS23.1.5 n) | Material data sheet and engineers approval | Before each Installation | HP | ENG
SECTION 2 – CONSTRUCTION
2.1 | Ducting and Cable Pit
2.1.1 | Foundation & Bedding Compliance | Keep trenches free of water No sharp projections, roots and other obstructions. Then bedding with sand for 50mm | PS23.11.8.a) ii | Photo/Visual Inspection | Each excavation | C | SE
2.1.2 | Ducting | Minimum 50mm separation from other conduits; Also follow separation requirements by utility operators when in shared trench. Depth as per drawing (survey data): ≥900mm under Roadways, ≥600mm under Sidewalks/Berm; Or Client Instruction on site. Where services cross, install electrical conduit at the topmost | PS23.11.8.a) v | Photo/Visual Inspection/Comms | Each installation | M | SE
2.1.3 | Sealing Ducts | Seal buried entries of ducts and conduits using waterproof seals and/or conduit fittings. Seal spare ducts and conduits immediately after installation and seal other ducts and conduits after cable installation. | PS23.11.8.a) vi | Photo/Visual Inspection | Each installation | M | SE
2.1.4 | Survey data for ducting routes | As built every ducts joint before backfill to accurately record the routes of underground cables. | PS23.11.8.b) | Survey Data | Each installation | H | SE
2.1.5 | Marker Tape | Install orange marker tape at 150mm or 50% of the depth of burial, whichever is greater, below finished ground level. | PS23.11.8.b) ii | Photo/Visual | Each installation | M | SE
2.1.6 | Backfilling | Backfill trenches as soon as possible after approval of laid and bedded service. Place the backfill in layers < 150mm thick and compact to the density which applies to the location of the trenches to minimize settlement. - Under maintenance pad, Clegg test will be used, with target CIV 25 for GAP65. - Under berm area, no test needed on topsoil. | PS23.11.8.a) iii | Photo/Visual Inspection/Compaction result when under Road or paved areas | Each installation | M | SE |  |  | Backfill materials will either be site excavated GAP65 which had been approved at Earthworks stage) or Soil at berm area.
2.1.7 | Cable Pit | Install cable pits as detailed on the drawings. | PS 23.1.5 d) | Comms with WSP/ Photo/Visual Inspection | Each installation | W | ENG
2.2 | Montrose Box
2.2.1 | Pad, Hasp and Staple | Install new Montrose Boxes on concrete plinth as per Electrical Services drawings. Install stainless steel hasp and staple brackets to allow for Waka Kotahi to fit their own padlock onto it. | PS 23.1.3.b) & 23.1.5 a) ii; Drawing 0411 - 0413. | Photo/Visual Inspection | During construction | I | SE
2.2.2 | Earthing, Bonding & Surge Protection | Install an earth electrode in accordance with the AS/NZS 3000. Install new Earth Bar and Neutral Bar c/w MEN link; Install Circuit Protective Devices as specified in Drawings; Install Switchboard as per details in Specification. | PS 23.1.5.a) ii & iii | Photo/Visual Inspection | During construction | I | PE/SE
2.2.3 | Metering Compartment | Liaise with the client’s electricity retailer for the installation of their three-phase meter within the metering compartment of the new Montrose Box. Metering Agency supply of low Voltage meters and metering current transformers. | PS 23.1.5 a) & 23.3.1& 23.9.4 | Comms and Photo/Visual Inspection | Prior to Installation | H | PE
2.3 | Lighting Equipment
2.3.1 | Luminaires & Poles (WK & TCC @ RAB) | Types of luminaires and poles shall be installed as per details on the drawings or as per instruction of Client Luminaire Controller - PDL- 56SS10. Luminaires shall be fitted with Shorting Caps. | PS 23.1.3 c-d); 23.1.5 f-g) & Drawing 0004, 0407-0409,0413 | Photo/Visual Inspection | Each Installation | I | PE/SE
2.3.2 | Circuit Cabling (WK & TCC @ RAB) | Supply and Install final circuit cabling to Luminaires from the Montrose Boxes via underground ducts and conduits as per Drawing - proposed circuiting layout. | PS23.1.3 g); 23.1.5 e) & Drawing 0131 -0135 | Photo/Visual Inspection | Each installation | I | PE/SE
2.3.3 | Luminaires - Underpass | Types of luminaire and poles shall be installed as per details on the drawings or as per instruction of Client. Luminaire Dimmer Controller - CASAMBI "CBU-TED". Time and Dimming percentage to be adviced by Light Engineer WSP. | PS 23.1.3 c-d); 23.1.5 f-g) & Drawing 0415 | Comms and Photo/Visual Inspection | Each Installation | I | PE
2.3.4 | Circuit Cabling - Underpass | Every second luminaire shall be on separate circuit (MSB-TC-NMB/R3 and B7) as per Drawing and terminate into a CASAMBI "CBU-TED" Dimmer Driver Controller via individual 230V-rated Switches. | PS 23.1.5 g) & Drawing 0405,0415 | Comms /Photo/Visual Inspection | Each Installation | I | PE/SE
2.4 | CCTV Camera Underpass
2.4.1 | Camera and Cabinet Location | Cameras mount at high level on chamfered edge of underpass or the underside of the sealing if no space after lighting installation. Lockable CCTV Cabinet mount at high level underneath the chamfered edge of underpass. | Drawing 0406 | Photo/Visual Inspection | Prior to installation | H | PE
2.4.2 | Circuit Cabling | Cabling from cabinet to camera through rigid conduit. Between Montrose Box(MSB-TC-NMB/R7) and Cabinet - Tight buffered outdoor OM4 Optical Fibre Between Cabinet and Cameras --CAT6A U/UTP Cable in 25 mm conduit | Drawing 0414 | Photo/Visual Inspection | Each installation | I | PE/SE
2.4.3 | IP Addressing, Programming of PoE Network Switches | Liaison with TCC for IP addressing and Programming of PoE Network switches. | PS 23.1.4 m) | Comms Record | Prior Installation | H | PE
SECTION 3 – Commissioning and Testing
3.1 | Luminaire Controls
3.1.1 | Commissioning - Luminaires (WK RAB) | Carry out full commissioning of the Light Controls as detailed on the drawings. | PS 23.1.5 f) -g) | Photo/Visual Inspection and Commissioning Records | Each Commissioning | W | ENG
3.1.2 | Commissioning - Luminaires (TCC RAB) | Carry out full commissioning of the Light Controls as detailed on the drawings. Also record "Benchmark" energy meter reading from the lighting switchboards of all levels to demonstrate power consumption when ALL luminaires are running at 100%. | PS 23.1.5 g) & h) | Photo/Visual Inspection and Commissioning Records | Each Commissioning | W | ENG
3.1.3 | Commissioning - Luminaires Underpass | ON/OFF Operation + Dimming Function etc. on each Lighting Circuit under direction of Energy Light NZ utilising Calibrated Lux Meter. | PS 23.1.3 e); 23.1.5 g) & Drawing | Photo/Visual Inspection and Commissioning Records | Each Commissioning | W | ENG
3.2 | CCTV Cameras
3.2.1 | Cameras | Testing Optic fibre from TCC Montrose Cabinet to underpass CCTV Cabinet; Testing CAT6A U/UTP Cabling from CCTV Cabinet to each CCTV Camera. Liaison with TCC for Commissioning and Testing including camera adjustment to achieve the desired FOV. | PS 23.1.4 m) | Testing/Commissioning Record | Each Testing/ Commissioning | H | PE
SECTION 4 – POST CONSTRUCTION ACTIVITY
4.1 | Electrical Certificate of Compliance (CoC) & Record of inspection (ROI) Electrical Safety Certificate (ESC) | Obtain final certification of the installed systems by an independent electrical inspector approved by the Electricity Workers Registration Board. | PS 23.1.5 p) | CoC,ROI and ESC | Post commissioning | R | PE
4.2 | As-Built | As-built drawings with 1) ducting routes. 2)) control groups, 3) scene settings 4) override sequences, 5) luminaire and pole locations, 6) the individual addresses of each luminaire, and their corresponding groups (if DALI) shown clearly for maintenance purposes. 7) All changes to design to be noted, highlighted or markup clearly. | PS 23.1.5 h) & 23.8.5 a)-b) | As-built Drawing/Survey Data | Post construction | H | PE/ ENG

## ITP Cover Page - 001
Streetlighting Inspection and Test Plan
Project: SH29 Tauriko West Enabling Project
Number and Revision: DN1210 - 027-001 - Rev 0
SECTION 1 – GENERAL DETAILS
Project Name: |  |  | SH29 Tauriko West Enabling Project |  |  |  |  | ITP Number: |  |  | 027-001
Project Number: |  |  | DN1210 |  |  |  |  | ITP Status: |  |  | Draft
ITP Description: |  |  | Streetlight Inspection and Test Plan 001 - Ducting and Cable Installation |  |  |  |  | Revision: | 1000 |  | 0
Contract Number: |  |  | 8287 |  |  |  |  | Drawing Sets: |  |  | 23273502 - WSP-DR-LIG
Customer: |  |  | Waka Kotahi |  |  |  |  | Specification: |  |  | SH29 Tauriko West Enabling Works Contract No.NZTA8287 Section 23
Quality Specified: |  |  | ISO9001: 2015
Review / Update History | [9 empty] | Verification Activity
Rev: | Status: | Date: |  | Reviewed By: |  | Revision Details: |  |  |  | Activity Key |  |  | Responsibilities Key
0 | Draft for Approval |  |  | Cordelia Girdler-Brown and Chris Benson |  | Streetlighting Inspection and Test Plan |  |  |  | A | Action |  | ENG | Engineer / Engineer's Rep
[10 empty] | B | Report by Breach |  | CR | Customer Rep
[10 empty] | C | Check |  | PD | Project Director
[10 empty] | D | Dimension Inspection |  | PM | Project Manager
[10 empty] | E | Examine |  | OP | Operations Manager
[10 empty] | HP | Hold Point (Engineer) |  | HSE | HSE Manager / Rep
[10 empty] | H | Hold Point (Internal) |  | QM | QA Manager / Rep
[10 empty] | I | Inspection |  | PE | Project Engineer
[10 empty] | M | Monitor on Random Basis |  | SE | Site Engineer
[10 empty] | O | Operation |  | QE | Quality Engineer
[10 empty] | R | Review |  | SUP | Superintendent / Supervisor
[10 empty] | S | Subcontractor |  | SV | Surveyor
[10 empty] | V | Visual Verification |  | ITP | Third Party Inspector
[10 empty] | W | Witness Point |  | SPEC | Specialist
SECTION 2A – ITP Approval | [7 empty] | SECTION 2B – ITP CLOSEOUT
Position |  | Name: |  |  | Signature: |  | Date: | Position |  | Name: |  | Signature: |  |  | Date:
Downer PM |  | Chris Benson | [5 empty] | Downer PM |  | Chris Benson
Downer QM |  | Cordelia Girdler-Brown | [5 empty] | Downer QM |  | Cordelia Girdler-Brown
Client (If Applicable) | [7 empty] | Client (If Applicable)

## 001-SL-Ducting and Cable Instal
Streetlight Inspection and Test Plan Part 1
SH29 Tauriko West Enabling Project
Number and Revision: DN1210 - 027-001 - Rev 0
Item No. | Inspection and Test Point | Acceptance / Conformance Criteria | Standard / Specification | Verifying Document | Frequency | Verification Activity |  | Downer Conformance of Compliance Signoff
[6 empty] | Activity | By | Downer Signature | Date | Comments / Closeout Details | ENGINEERS COMMENTS - Date: | DOWNER RESPONSE - Date:
SECTION 1 – MATERIAL, PERSONNEL & THIRD PARTY APPROVAL
1.1 | Pre-Construction Set Up
1.1.1 | Underground Services | Pothole all services prior to commencement of trenching. Suitably protect the existing services from construction damage. | PS23.5.3 b) | Survey Data/Site Photo | Pre - excavation | H | PE/SE
1.1.2 | Ducting and Cabling Route | Confirm on site the exact location of cabling routes before trenching. Where connecting and or coordinating with existing services, engineers shall make local modifications necessary for the correct operation of the entire system. | PS 23.1.5 p) & 23.5.3 a) | Survey data/Comms with Client | Prior to Installation | H | PE
1.1.3 | Location of Lighting Poles, Cameras, Cable Pits and Montrose Boxes | Confirm with surveyor and mark out the exact locations of lighting poles, Cameras, Cable Pits and Montrose boxes before installation. | IFC Drawings | Survey data/Comms with Client | Prior to Installation | H | PE
1.2 | Material Testing and Approval
1.2.1 | Bedding and Overlay | Coarse Sand | PS23.11.8.a) ii-iii | Coase Sand - PSD Report | Before construction | H | ENG
1.2.2 | Backfilling | Under roads and paved areas: Coarse sand, controlled low strength material or fine crushed rock. In topsoil areas: Complete the backfilling with topsoil for at least the top 50mm. | PS23.11.8.a) ii-iii | Material data sheet and engineers approval | Before construction | H | ENG |  |  | Backfill materials will either be site excavated GAP65 which had been approved at Earthwork stage) or Soil
1.2.3 | Ducts and Fittings | Use heavy duty HD PVC for underground services. Use best practice PVC where possible. Orange colour for all conduits containing consumer mains, sub-mains or final sub-circuits cabling | PS23.11.8.a) iv | Material data sheet and engineers approval | Before construction | H | ENG |  |  | Same power ducts applied as Utility works
1.2.4 | Cable Pit | Aco Cablemate Polycrete "type 66" Dimension: 665mm x 665mm x 620mm with heavy duty steel lid. | PS 23.1.5 d) & Drawing 0122 | Material data sheet and engineers approval | Before construction | H | ENG
SECTION 2 – CONSTRUCTION
2.1 | Ducting and Cable Pit
2.1.1 | Foundation & Bedding Compliance | Keep trenches free of water No sharp projections, roots and other obstructions. Then bedding with sand for 50mm | PS23.11.8.a) ii | Photo/Visual Inspection | Each excavation | C | SE
2.1.2 | Ducting | Minimum 50mm separation from other conduits; Also follow separation requirements by utility operators when in shared trench. Depth as per drawing (survey data): ≥900mm under Roadways, ≥600mm under Sidewalks/Berm; Or Client Instruction on site. Where services cross, install electrical conduit at the topmost | PS23.11.8.a) v | Photo/Visual Inspection/Comms | Each installation | M | SE
2.1.3 | Sealing Ducts | Seal buried entries of ducts and conduits using waterproof seals and/or conduit fittings. Seal spare ducts and conduits immediately after installation and seal other ducts and conduits after cable installation. | PS23.11.8.a) vi | Photo/Visual Inspection | Each installation | M | SE
2.1.4 | Survey data for ducting routes | As built every ducts joint before backfill to accurately record the routes of underground cables. | PS23.11.8.b) | Survey Data | Each installation | H | SE
2.1.5 | Marker Tape | Install orange marker tape at 150mm or 50% of the depth of burial, whichever is greater, below finished ground level. | PS23.11.8.b) ii | Photo/Visual | Each installation | M | SE
2.1.6 | Backfilling | Backfill trenches as soon as possible after approval of laid and bedded service. Place the backfill in layers < 150mm thick and compact to the density which applies to the location of the trenches to minimize settlement. - Under maintenance pad, Clegg test will be used, with target CIV 25 for GAP65. - Under berm area, no test needed on topsoil. | PS23.11.8.a) iii | Photo/Visual Inspection/Compaction result when under Road or paved areas | Each installation | M | SE
2.1.7 | Cable Pit | Install cable pits as detailed on the drawings. | PS 23.1.5 d) | Comms with WSP/ Photo/Visual Inspection | Each installation | W | ENG
SECTION 3 – POST CONSTRUCTION ACTIVITY
3.1 | As-Built | As-built drawings with 1) ducting routes. 2)) control groups, 3) scene settings 4) override sequences, 5) luminaire and pole locations, 6) the individual addresses of each luminaire, and their corresponding groups (if DALI) shown clearly for maintenance purposes. 7) All changes to design to be noted, highlighted or markup clearly. | PS 23.1.5 h) & 23.8.5 a)-b) | As-built Drawing/Survey Data | Post construction | HP | PE/ ENG

## ITP Cover Page - 002
Streetlighting Inspection and Test Plan
Project: SH29 Tauriko West Enabling Project
Number and Revision: DN1210 - 027-002 - Rev 0
SECTION 1 – GENERAL DETAILS
Project Name: |  |  | SH29 Tauriko West Enabling Project |  |  |  |  | ITP Number: |  |  | 027-002
Project Number: |  |  | DN1210 |  |  |  |  | ITP Status: |  |  | Draft
ITP Description: |  |  | Streetlight Inspection and Test Plan 002 - Luminaire @ RAB |  |  |  |  | Revision: | 1000 |  | 0
Contract Number: |  |  | 8287 |  |  |  |  | Drawing Sets: |  |  | 23273502 - WSP-DR-LIG
Customer: |  |  | Waka Kotahi |  |  |  |  | Specification: |  |  | SH29 Tauriko West Enabling Works Contract No.NZTA8287 Section 23
Quality Specified: |  |  | ISO9001: 2015
Review / Update History | [9 empty] | Verification Activity
Rev: | Status: | Date: |  | Reviewed By: |  | Revision Details: |  |  |  | Activity Key |  |  | Responsibilities Key
0 | Draft for Approval |  |  | Cordelia Girdler-Brown and Chris Benson |  | Streetlighting Inspection and Test Plan |  |  |  | A | Action |  | ENG | Engineer / Engineer's Rep
[10 empty] | B | Report by Breach |  | CR | Customer Rep
[10 empty] | C | Check |  | PD | Project Director
[10 empty] | D | Dimension Inspection |  | PM | Project Manager
[10 empty] | E | Examine |  | OP | Operations Manager
[10 empty] | HP | Hold Point (Engineer) |  | HSE | HSE Manager / Rep
[10 empty] | H | Hold Point (Internal) |  | QM | QA Manager / Rep
[10 empty] | I | Inspection |  | PE | Project Engineer
[10 empty] | M | Monitor on Random Basis |  | SE | Site Engineer
[10 empty] | O | Operation |  | QE | Quality Engineer
[10 empty] | R | Review |  | SUP | Superintendent / Supervisor
[10 empty] | S | Subcontractor |  | SV | Surveyor
[10 empty] | V | Visual Verification |  | ITP | Third Party Inspector
[10 empty] | W | Witness Point |  | SPEC | Specialist
SECTION 2A – ITP Approval | [7 empty] | SECTION 2B – ITP CLOSEOUT
Position |  | Name: |  |  | Signature: |  | Date: | Position |  | Name: |  | Signature: |  |  | Date:
Downer PM |  | Chris Benson | [5 empty] | Downer PM |  | Chris Benson
Downer QM |  | Cordelia Girdler-Brown | [5 empty] | Downer QM |  | Cordelia Girdler-Brown
Client (If Applicable) | [7 empty] | Client (If Applicable)

## 002-SL-Luminaire@RAB
Streetlighting Inspection and Test Plan
SH29 Tauriko West Enabling Project
Number and Revision: DN1210-027-002 - Rev 0
Item No. | Inspection and Test Point | Acceptance / Conformance Criteria | Standard / Specification | Verifying Document | Frequency | Verification Activity |  | Downer Conformance of Compliance Signoff
[6 empty] | Activity | By | Downer Signature | Date | Comments / Closeout Details
SECTION 1 – MATERIAL, PERSONNEL & THIRD PARTY APPROVAL
1.1 | Pre-Construction Set Up
1.1.1 | Underground Services | Pothole all services prior to commencement of trenching. Suitably protect the existing services from construction damage. | PS23.5.3 b) | Survey Data/Site Photo | Pre - excavation | H | PE/SE
1.1.2 | Ducting and Cabling Route | Confirm on site the exact location of cabling routes before trenching. Where connecting and or coordinating with existing services, engineers shall make local modifications necessary for the correct operation of the entire system. | PS 23.1.5 p) & 23.5.3 a) | Survey data/Comms with Client | Prior to Installation | H | PE
1.1.3 | Location of Lighting Poles, Cameras, Cable Pits and Montrose Boxes | Confirm with surveyor and mark out the exact locations of lighting poles, Cameras, Cable Pits and Montrose boxes before installation. | IFC Drawings | Survey data/Comms with Client | Prior to Installation | H | PE
1.2 | Material Testing and Approval
1.2.1 | Montrose Box | Provide MSB-NMB shop drawings complete with wiring schematics for review and approval by the Engineer prior to construction. | PS 23.1.5.a) ii | Shop Drawings and engineers approval | Prior to Purchase | H | ENG
1.2.2 | Pad, Hasp and Staple | Supply new Montrose Boxes on concrete plinth as per Electrical Services drawings. Box need to be fitted with a stainless steel hasp and staple brackets to allow for Waka Kotahi to fit their own padlock onto it. | PS 23.1.3.b) & 23.1.5 a) ii; Drawing 0413, 0411, 0412. | Material data sheet and engineers approval | Before construction | H | ENG
1.2.3 | Luminaires & Poles -WK & TCC Redwood Ln RAB | Luminaire and Pole types shall be supplied and installed as detailed on the drawings or as per instruction of Client Luminaire Controller - PDL- 56SS10. | PS 23.1.5 g) & Drawing 0411, 0412 | Material data sheet and engineers approval | Before each Installation | H | ENG |  |  | Purchase of Luminaires/Poles already approved by Client. PE/SE need to check on site to guarantee right type of luminaries and poles are installed at specific location.
SECTION 2 – CONSTRUCTION
2.1 | Montrose Box
2.1.1 | Pad, Hasp and Staple | Install new Montrose Boxes on concrete plinth as per Electrical Services drawings. Install stainless steel hasp and staple brackets to allow for Waka Kotahi to fit their own padlock onto it. | PS 23.1.3.b) & 23.1.5 a) ii; Drawing 0411 - 0413. | Photo/Visual Inspection | During construction | I | SE
2.1.2 | Earthing, Bonding & Surge Protection | Install an earth electrode in accordance with the AS/NZS 3000. Install new Earth Bar and Neutral Bar c/w MEN link; Install Circuit Protective Devices as specified in Drawings; Install Switchboard as per details in Specification. | PS 23.1.5.a) ii & iii | Photo/Visual Inspection | During construction | I | PE/SE
2.1.3 | Metering Compartment | Liaise with the client’s electricity retailer for the installation of their three-phase meter within the metering compartment of the new Montrose Box. Metering Agency supply of low Voltage meters and metering current transformers. | PS 23.1.5 a) & 23.3.1& 23.9.4 | Comms and Photo/Visual Inspection | Prior to Installation | H | PE
2.2 | Lighting Equipment
2.2.1 | Luminaires & Poles (WK & TCC @ RAB) | Types of luminaires and poles shall be installed as per details on the drawings or as per instruction of Client Luminaire Controller - PDL- 56SS10. Luminaires shall be fitted with Shorting Caps. | PS 23.1.3 c-d); 23.1.5 f-g) & Drawing 0004, 0407-0409,0413 | Photo/Visual Inspection | Each Installation | I | PE/SE
2.2.2 | Circuit Cabling (WK & TCC @ RAB) | Supply and Install final circuit cabling to Luminaires from the Montrose Boxes via underground ducts and conduits as per Drawing - proposed circuiting layout. | PS23.1.3 g); 23.1.5 e) & Drawing 0131 -0135 | Photo/Visual Inspection | Each installation | I | PE/SE
SECTION 3 – POST CONSTRUCTION ACTIVITY
3.1 | As-Built | As-built drawings with 1) ducting routes. 2)) control groups, 3) scene settings 4) override sequences, 5) luminaire and pole locations, 6) the individual addresses of each luminaire, and their corresponding groups (if DALI) shown clearly for maintenance purposes. 7) All changes to design to be noted, highlighted or markup clearly. | PS 23.1.5 h) & 23.8.5 a)-b) | As-built Drawing/Survey Data | Post construction | H | PE/ ENG

## ITP Cover page - 003
Streetlighting Inspection and Test Plan
Project: SH29 Tauriko West Enabling Project
Number and Revision: DN1210 - 027-003 - Rev 0
SECTION 1 – GENERAL DETAILS
Project Name: |  |  | SH29 Tauriko West Enabling Project |  |  |  |  | ITP Number: |  |  | 027-003
Project Number: |  |  | DN1210 |  |  |  |  | ITP Status: |  |  | Draft
ITP Description: |  |  | Streetlight Inspection and Test Plan 003 - Luminaire and CCTV @ Underpass |  |  |  |  | Revision: | 1000 |  | 0
Contract Number: |  |  | 8287 |  |  |  |  | Drawing Sets: |  |  | 23273502 - WSP-DR-LIG
Customer: |  |  | Waka Kotahi |  |  |  |  | Specification: |  |  | SH29 Tauriko West Enabling Works Contract No.NZTA8287 Section 23
Quality Specified: |  |  | ISO9001: 2015
Review / Update History | [9 empty] | Verification Activity
Rev: | Status: | Date: |  | Reviewed By: |  | Revision Details: |  |  |  | Activity Key |  |  | Responsibilities Key
0 | Draft for Approval |  |  | Cordelia Girdler-Brown and Chris Benson |  | Streetlighting Inspection and Test Plan |  |  |  | A | Action |  | ENG | Engineer / Engineer's Rep
[10 empty] | B | Report by Breach |  | CR | Customer Rep
[10 empty] | C | Check |  | PD | Project Director
[10 empty] | D | Dimension Inspection |  | PM | Project Manager
[10 empty] | E | Examine |  | OP | Operations Manager
[10 empty] | HP | Hold Point (Engineer) |  | HSE | HSE Manager / Rep
[10 empty] | H | Hold Point (Internal) |  | QM | QA Manager / Rep
[10 empty] | I | Inspection |  | PE | Project Engineer
[10 empty] | M | Monitor on Random Basis |  | SE | Site Engineer
[10 empty] | O | Operation |  | QE | Quality Engineer
[10 empty] | R | Review |  | SUP | Superintendent / Supervisor
[10 empty] | S | Subcontractor |  | SV | Surveyor
[10 empty] | V | Visual Verification |  | ITP | Third Party Inspector
[10 empty] | W | Witness Point |  | SPEC | Specialist
SECTION 2A – ITP Approval | [7 empty] | SECTION 2B – ITP CLOSEOUT
Position |  | Name: |  |  | Signature: |  | Date: | Position |  | Name: |  | Signature: |  |  | Date:
Downer PM |  | Chris Benson | [5 empty] | Downer PM |  | Chris Benson
Downer QM |  | Cordelia Girdler-Brown | [5 empty] | Downer QM |  | Cordelia Girdler-Brown
Client (If Applicable) | [7 empty] | Client (If Applicable)

## 003-SL-Luminaire CCTV@Underpass
Streetlighting Inspection and Test Plan
SH29 Tauriko West Enabling Project
Number and Revision: DN1210-027-003 - Rev 0
Item No. | Inspection and Test Point | Acceptance / Conformance Criteria | Standard / Specification | Verifying Document | Frequency | Verification Activity |  | Downer Conformance of Compliance Signoff
[6 empty] | Activity | By | Downer Signature | Date | Comments / Closeout Details | ENGINEERS COMMENTS - Date: | DOWNER RESPONSE - Date:
SECTION 1 – MATERIAL, PERSONNEL & THIRD PARTY APPROVAL
1.1 | Pre-Construction Set Up
1.1.1 | Underground Services | Pothole all services prior to commencement of trenching. Suitably protect the existing services from construction damage. | PS23.5.3 b) | Survey Data/Site Photo | Pre - excavation | H | PE/SE
1.1.2 | Ducting and Cabling Route | Confirm on site the exact location of cabling routes before trenching. Where connecting and or coordinating with existing services, engineers shall make local modifications necessary for the correct operation of the entire system. | PS 23.1.5 p) & 23.5.3 a) | Survey data/Comms with Client | Prior to Installation | H | PE
1.1.3 | Location of Lighting Poles, Cameras, Cable Pits and Montrose Boxes | Confirm with surveyor and mark out the exact locations of lighting poles, Cameras, Cable Pits and Montrose boxes before installation. | IFC Drawings | Survey data/Comms with Client | Prior to Installation | H | PE
1.2 | Material Testing and Approval
1.2.1 | Luminaires - Underpass | Luminaire and Pole types shall be supplied as detailed on the drawings or as per instruction of Client. Luminaires Controller - CASAMBI "CBU-TED" procured directly from Energy Light NZ. | PS 23.1.5 g) & Drawing 0412 | Material data sheet and engineers approval | Before each Installation | H | ENG |  |  | PE/SE need to check on site to guarantee right type of luminaries and switch are installed at specific location.
1.2.2 | CCTV Cameras and PoE Switches | TCC Approved IP67 IK10+ With Weatherproof Housing , Vandal Resistant and PoE Dome (HD1080p, 2MP), Sensitivity down to 0.01 lux Have intelligent auto exposure to offer front and back light compensation. TCC approved Power-over- Ethernet (PoE) | PS23.1.5 n) | Material data sheet and engineers approval | Before each Installation | H | ENG
SECTION 2 – CONSTRUCTION
2.1 | Lighting Equipment
2.1.1 | Luminaires - Underpass | Types of luminaire and poles shall be installed as per details on the drawings or as per instruction of Client. Luminaire Dimmer Controller - CASAMBI "CBU-TED". Time and Dimming percentage be adviced by Light Engineer WSP. | PS 23.1.3 c-d); 23.1.5 f-g) & Drawing 0415 | Comms and Photo/Visual Inspection | Each Installation | I | PE
2.1.2 | Circuit Cabling - Underpass | Every second luminaire shall be on separate circuit (MSB-TC-NMB/R3 and B7) as per Drawing and terminate into a CASAMBI "CBU-TED" Dimmer Driver Controller via individual 230V-rated Switches. | PS 23.1.5 g) & Drawing 0405,0415 | Comms /Photo/Visual Inspection | Each Installation | I | PE/SE
2.2 | CCTV Camera Underpass
2.2.1 | Camera and Cabinet Location | Cameras mount at high level on chamfered edge of underpass or the underside of the sealing if no space after lighting installation. Lockable CCTV Cabinet mount at high level underneath the chamfered edge of underpass. | Drawing 0406 | Photo/Visual Inspection | Prior to installation | H | PE
2.2.2 | Circuit Cabling | Cabling from cabinet to camera through ridged conduit. Between Montrose Box(MSB-TC-NMB/R7) and Cabinet - Tight buffered outdoor OM4 Optical Fibre Between Cabinet and Cameras --CAT6A U/UTP Cable in 25 mm conduit | Drawing 0414 | Photo/Visual Inspection | Each installation | I | PE/SE
2.2.3 | IP Addressing, Programming of PoE Network Switches | Liaison with TCC for IP addressing and Programming of PoE Network switches. | PS 23.1.4 m) | Comms Record | Prior Installation | H | PE
SECTION 3 – POST CONSTRUCTION ACTIVITY
3.1 | As-Built | As-built drawings with 1) ducting routes. 2)) control groups, 3) scene settings 4) override sequences, 5) luminaire and pole locations, 6) the individual addresses of each luminaire, and their corresponding groups (if DALI) shown clearly for maintenance purposes. 7) All changes to design to be noted, highlighted or markup clearly. | PS 23.1.5 h) & 23.8.5 a)-b) | As-built Drawing/Survey Data | Post construction | H | PE/ ENG

## ITP Cover page - 004
Streetlighting Inspection and Test Plan
Project: SH29 Tauriko West Enabling Project
Number and Revision: DN1210 - 027-004 - Rev 0
SECTION 1 – GENERAL DETAILS
Project Name: |  |  | SH29 Tauriko West Enabling Project |  |  |  |  | ITP Number: |  |  | 027-004
Project Number: |  |  | DN1210 |  |  |  |  | ITP Status: |  |  | Draft
ITP Description: |  |  | Streetlight Inspection and Test Plan 004 - Commissioning and Post Construction |  |  |  |  | Revision: | 1000 |  | 0
Contract Number: |  |  | 8287 |  |  |  |  | Drawing Sets: |  |  | 23273502 - WSP-DR-LIG
Customer: |  |  | Waka Kotahi |  |  |  |  | Specification: |  |  | SH29 Tauriko West Enabling Works Contract No.NZTA8287 Section 23
Quality Specified: |  |  | ISO9001: 2015
Review / Update History | [9 empty] | Verification Activity
Rev: | Status: | Date: |  | Reviewed By: |  | Revision Details: |  |  |  | Activity Key |  |  | Responsibilities Key
0 | Draft for Approval |  |  | Cordelia Girdler-Brown and Chris Benson |  | Streetlighting Inspection and Test Plan |  |  |  | A | Action |  | ENG | Engineer / Engineer's Rep
[10 empty] | B | Report by Breach |  | CR | Customer Rep
[10 empty] | C | Check |  | PD | Project Director
[10 empty] | D | Dimension Inspection |  | PM | Project Manager
[10 empty] | E | Examine |  | OP | Operations Manager
[10 empty] | HP | Hold Point (Engineer) |  | HSE | HSE Manager / Rep
[10 empty] | H | Hold Point (Internal) |  | QM | QA Manager / Rep
[10 empty] | I | Inspection |  | PE | Project Engineer
[10 empty] | M | Monitor on Random Basis |  | SE | Site Engineer
[10 empty] | O | Operation |  | QE | Quality Engineer
[10 empty] | R | Review |  | SUP | Superintendent / Supervisor
[10 empty] | S | Subcontractor |  | SV | Surveyor
[10 empty] | V | Visual Verification |  | ITP | Third Party Inspector
[10 empty] | W | Witness Point |  | SPEC | Specialist
SECTION 2A – ITP Approval | [7 empty] | SECTION 2B – ITP CLOSEOUT
Position |  | Name: |  |  | Signature: |  | Date: | Position |  | Name: |  | Signature: |  |  | Date:
Downer PM |  | Chris Benson | [5 empty] | Downer PM |  | Chris Benson
Downer QM |  | Cordelia Girdler-Brown | [5 empty] | Downer QM |  | Cordelia Girdler-Brown
Client (If Applicable) | [7 empty] | Client (If Applicable)

## 004-SL-Commission&Post Construt
Streetlighting Inspection and Test Plan
SH29 Tauriko West Enabling Project
[7 empty] | Number and Revision DN1210-027-004- Rev 0 |  |  |  | #REF!
Item No. | Inspection and Test Point | Acceptance / Conformance Criteria | Standard / Specification | Verifying Document | Frequency | Verification Activity |  | Downer Conformance of Compliance Signoff
[6 empty] | Activity | By | Downer Signature | Date | Comments / Closeout Details | ENGINEERS COMMENTS - Date: | DOWNER RESPONSE - Date:
SECTION 1 – Commissioning and Testing
1.1 | Luminaire Controls
1.1.1 | Commissioning - Luminaires (WK RAB) | Carry out full commissioning of the Light Controls as detailed on the drawings. | PS 23.1.5 f) -g) | Photo/Visual Inspection and Commissioning Records | Each Commissioning | I | ENG
1.1.2 | Commissioning - Luminaires (TCC RAB) | Carry out full commissioning of the Light Controls as detailed on the drawings. Also record "Benchmark" energy meter reading from the lighting switchboards of all levels to demonstrate power consumption when ALL luminaires are running at 100%. | PS 23.1.5 g) & h) | Photo/Visual Inspection and Commissioning Records | Each Commissioning | I | ENG
1.1.3 | Commissioning - Luminaires Underpass | ON/OFF Operation + Dimming Function etc. on each Lighting Circuit under direction of Energy Light NZ utilising Calibrated Lux Meter. | PS 23.1.3 e); 23.1.5 g) & Drawing | Photo/Visual Inspection and Commissioning Records | Each Commissioning | I | ENG
1.2 | CCTV Cameras
1.2.1 | Cameras | Testing Optic fibre fromTCC Montrose Cabinet to underpass CCTV Cabinet; Testing CAT6A U/UTP Cabling from CCTV Cabinet to each CCTV Camera. Liaison with TCC for Commissioning and Testing including camera adjustment to achieve the desired FOV. | PS 23.1.4 m) | Testing/Commissioning Record | Each Testing/ Commissioning | H | PE
SECTION 2 – POST CONSTRUCTION ACTIVITY
2.1 | Electrical Certificate of Compliance (CoC) & Electrical Safety Certificate (ESC) | Obtain final certification of the installed systems by an independent electrical inspector approved by the Electricity Workers Registration Board. | PS 23.1.5 p) | CoC and ESC | Post commissioning | R | PE
2.2 | As-Built | As-built drawings with 1) ducting routes. 2)) control groups, 3) scene settings 4) override sequences, 5) luminaire and pole locations, 6) the individual addresses of each luminaire, and their corresponding groups (if DALI) shown clearly for maintenance purposes. 7) All changes to design to be noted, highlighted or markup clearly. | PS 23.1.5 h) & 23.8.5 a)-b) | As-built Drawing/Survey Data | Post construction | HP | PE/ ENG