## res
type | name | values | prefix | postfix | usage count | user addable | template name | Resource Id
checklist | DN1210-027-001 - ITP Streetlighting - Ducting and Cable installation | itp |  |  |  |  | DN1210-027-001 - ITP Streetlighting - Ducting and Cable installation Rev 0
section | SECTION 1 – MATERIAL, PERSONNEL & THIRD PARTY APPROVAL
checkpoint | 1.1.1 - Underground Services
label | Acceptance / Conformance Criteria - Pothole all services prior to commencement of trenching. Suitably protect the existing services from construction damage.
label | Standard / Specification - PS23.5.3 b)
label | Verifying Document - Survey Data/Site Photo
label | Frequency - Pre - excavation
label | Verification Activity: Activity - H
label | Verification Activity: By - PE/SE
checkpoint | 1.1.2 - Ducting and Cabling Route
label | Acceptance / Conformance Criteria - Confirm on site the exact location of cabling routes before trenching.
label | ○ Where connecting and or coordinating with existing services, engineers shall make local modifications necessary for the correct operation of the entire system.
label | Standard / Specification - PS 23.1.5 p) & 23.5.3 a)
label | Verifying Document - Survey data/Comms with Client
label | Frequency - Prior to Installation
label | Verification Activity: Activity - H
label | Verification Activity: By - PE
checkpoint | 1.1.3 - Location of Lighting Poles, Cameras, Cable Pits and Montrose Boxes
label | Acceptance / Conformance Criteria - Confirm with surveyor and mark out the exact locations of lighting poles, Cameras, Cable Pits and Montrose boxes before installation.
label | Standard / Specification - IFC Drawings
label | Verifying Document - Survey data/Comms with Client
label | Frequency - Prior to Installation
label | Verification Activity: Activity - H
label | Verification Activity: By - PE
checkpoint | 1.2.1 - Bedding and Overlay
label | Acceptance / Conformance Criteria - Coarse Sand
label | Standard / Specification - PS23.11.8.a) ii-iii
label | Verifying Document - Coase Sand - PSD Report
label | Frequency - Before construction
label | Verification Activity: Activity - H
label | Verification Activity: By - ENG
checkpoint | 1.2.2 - Backfilling
label | Acceptance / Conformance Criteria - Under roads and paved areas: Coarse sand, controlled low strength material or fine crushed rock. In topsoil areas: Complete the backfilling with topsoil for at least the top 50mm.
label | Standard / Specification - PS23.11.8.a) ii-iii
label | Verifying Document - Material data sheet and engineers approval
label | Frequency - Before construction
label | Verification Activity: Activity - H
label | Verification Activity: By - ENG
label | Comments / Closeout Details - Backfill materials will either be site excavated GAP65 which had been approved at Earthwork stage) or Soil
checkpoint | 1.2.3 - Ducts and Fittings
label | Acceptance / Conformance Criteria - Use heavy duty HD PVC for underground services. Use best practice PVC where possible. Orange colour for all conduits containing consumer mains, sub-mains or final sub-circuits cabling
label | Standard / Specification - PS23.11.8.a) iv
label | Verifying Document - Material data sheet and engineers approval
label | Frequency - Before construction
label | Verification Activity: Activity - H
label | Verification Activity: By - ENG
label | Comments / Closeout Details - Same power ducts applied as Utility works
checkpoint | 1.2.4 - Cable Pit
label | Acceptance / Conformance Criteria - Aco Cablemate Polycrete "type 66" Dimension: 665mm x 665mm x 620mm with heavy duty steel lid.
label | Standard / Specification - PS 23.1.5 d) & Drawing 0122
label | Verifying Document - Material data sheet and engineers approval
label | Frequency - Before construction
label | Verification Activity: Activity - H
label | Verification Activity: By - ENG
section | SECTION 2 – CONSTRUCTION
checkpoint | 2.1.1 - Foundation & Bedding Compliance
label | Acceptance / Conformance Criteria - Keep trenches free of water
label | ○ No sharp projections, roots and other obstructions.
label | ○ Then bedding with sand for 50mm
label | Standard / Specification - PS23.11.8.a) ii
label | Verifying Document - Photo/Visual Inspection
label | Frequency - Each excavation
label | Verification Activity: Activity - C
label | Verification Activity: By - SE
checkpoint | 2.1.2 - Ducting
label | Acceptance / Conformance Criteria - Minimum 50mm separation from other conduits; Also follow separation requirements by utility operators when in shared trench.
label | Depth as per drawing (survey data):
label | ○ ≥900mm under Roadways, ≥600mm under Sidewalks/Berm;
label | ○ Or Client Instruction on site.
label | ○ Where services cross, install electrical conduit at the topmost
label | Standard / Specification - PS23.11.8.a) v
label | Verifying Document - Photo/Visual Inspection/Comms
label | Frequency - Each installation
label | Verification Activity: Activity - M
label | Verification Activity: By - SE
checkpoint | 2.1.3 - Sealing Ducts
label | Acceptance / Conformance Criteria - Seal buried entries of ducts and conduits using waterproof seals and/or conduit fittings.
label | ○ Seal spare ducts and conduits immediately after installation and seal other ducts and conduits after cable installation.
label | Standard / Specification - PS23.11.8.a) vi
label | Verifying Document - Photo/Visual Inspection
label | Frequency - Each installation
label | Verification Activity: Activity - M
label | Verification Activity: By - SE
checkpoint | 2.1.4 - Survey data for ducting routes
label | Acceptance / Conformance Criteria - As built every ducts joint before backfill to accurately record the routes of underground cables.
label | Standard / Specification - PS23.11.8.b)
label | Verifying Document - Survey Data
label | Frequency - Each installation
label | Verification Activity: Activity - H
label | Verification Activity: By - SE
checkpoint | 2.1.5 - Marker Tape
label | Acceptance / Conformance Criteria - Install orange marker tape at 150mm or 50% of the depth of burial, whichever is greater, below finished ground level.
label | Standard / Specification - PS23.11.8.b) ii
label | Verifying Document - Photo/Visual
label | Frequency - Each installation
label | Verification Activity: Activity - M
label | Verification Activity: By - SE
checkpoint | 2.1.6 - Backfilling
label | Acceptance / Conformance Criteria - Backfill trenches as soon as possible after approval of laid and bedded service.
label | ○ Place the backfill in layers < 150mm thick and compact to the density which applies to the location of the trenches to minimize settlement.
label | — Under maintenance pad, Clegg test will be used, with target CIV 25 for GAP65.
label | — Under berm area, no test needed on topsoil.
label | Standard / Specification - PS23.11.8.a) iii
label | Verifying Document - Photo/Visual Inspection/Compaction result when under Road or paved areas
label | Frequency - Each installation
label | Verification Activity: Activity - M
label | Verification Activity: By - SE
checkpoint | 2.1.7 - Cable Pit
label | Acceptance / Conformance Criteria - Install cable pits as detailed on the drawings.
label | Standard / Specification - PS 23.1.5 d)
label | Verifying Document - Comms with WSP/ Photo/Visual Inspection
label | Frequency - Each installation
label | Verification Activity: Activity - W
label | Verification Activity: By - ENG
section | SECTION 3 – POST CONSTRUCTION ACTIVITY
checkpoint | 3.1 - As-Built
label | Acceptance / Conformance Criteria - As-built drawings with
label | 1) ducting routes.
label | 2) control groups,
label | 3) scene settings
label | 4) override sequences,
label | 5) luminaire and pole locations,
label | 6) the individual addresses of each luminaire, and their corresponding groups (if DALI) shown clearly for maintenance purposes.
label | 7) All changes to design to be noted, highlighted or markup clearly.
label | Standard / Specification - PS 23.1.5 h) & 23.8.5 a)-b)
label | Verifying Document - As-built Drawing/Survey Data
label | Frequency - Post construction
label | Verification Activity: Activity - HP
label | Verification Activity: By - PE/ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | Client Final Inspection - the signature below verifies that this ITP has been completed in accordance with the Specifications and verifies lot compliance.
textbox | Contractor's Rep Name:
textbox | Engineer's Rep. Name:
date | Date:
signoff | Add Signature
checklist | DN1210-027-002 - ITP Streetlighting - Luminaire @RAB | itp |  |  |  |  | DN1210-027-002 - ITP Streetlighting - Luminaire @RAB Rev 0
section | SECTION 1 – MATERIAL, PERSONNEL & THIRD PARTY APPROVAL
checkpoint | 1.1.1 - Underground Services
label | Acceptance / Conformance Criteria - Pothole all services prior to commencement of trenching. Suitably protect the existing services from construction damage.
label | Standard / Specification - PS23.5.3 b)
label | Verifying Document - Survey Data/Site Photo
label | Frequency - Pre - excavation
label | Verification Activity: Activity - H
label | Verification Activity: By - PE/SE
checkpoint | 1.1.2 - Ducting and Cabling Route
label | Acceptance / Conformance Criteria - Confirm on site the exact location of cabling routes before trenching.
label | ○ Where connecting and or coordinating with existing services, engineers shall make local modifications necessary for the correct operation of the entire system.
label | Standard / Specification - PS 23.1.5 p) & 23.5.3 a)
label | Verifying Document - Survey data/Comms with Client
label | Frequency - Prior to Installation
label | Verification Activity: Activity - H
label | Verification Activity: By - PE
checkpoint | 1.1.3 - Location of Lighting Poles, Cameras, Cable Pits and Montrose Boxes
label | Acceptance / Conformance Criteria - Confirm with surveyor and mark out the exact locations of lighting poles, Cameras, Cable Pits and Montrose boxes before installation.
label | Standard / Specification - IFC Drawings
label | Verifying Document - Survey data/Comms with Client
label | Frequency - Prior to Installation
label | Verification Activity: Activity - H
label | Verification Activity: By - PE
checkpoint | 1.2.1 - Montrose Box
label | Acceptance / Conformance Criteria - Provide MSB-NMB shop drawings complete with wiring schematics for review and approval by the Engineer prior to construction.
label | Standard / Specification - PS 23.1.5.a) ii
label | Verifying Document - Shop Drawings and engineers approval
label | Frequency - Prior to Purchase
label | Verification Activity: Activity - H
label | Verification Activity: By - ENG
checkpoint | 1.2.2 - Pad, Hasp and Staple
label | Acceptance / Conformance Criteria - Supply new Montrose Boxes on concrete plinth as per Electrical Services drawings. Box need to be fitted with a stainless steel hasp and staple brackets to allow for Waka Kotahi to fit their own padlock onto it.
label | Standard / Specification - PS 23.1.3.b) & 23.1.5 a) ii; Drawing 0413, 0411, 0412.
label | Verifying Document - Material data sheet and engineers approval
label | Frequency - Before construction
label | Verification Activity: Activity - H
label | Verification Activity: By - ENG
checkpoint | 1.2.3 - Luminaires & Poles -WK & TCC Redwood Ln RAB
label | Acceptance / Conformance Criteria - Luminaire and Pole types shall be supplied and installed as detailed on the drawings or as per instruction of Client
label | ○ Luminaire Controller - PDL- 56SS10.
label | Standard / Specification - PS 23.1.5 g) & Drawing 0411, 0412
label | Verifying Document - Material data sheet and engineers approval
label | Frequency - Before each Installation
label | Verification Activity: Activity - H
label | Verification Activity: By - ENG
label | Comments / Closeout Details - Purchase of Luminaires/Poles already approved by Client.
label | ○ PE/SE need to check on site to guarantee right type of luminaries and poles are installed at specific location.
section | SECTION 2 – CONSTRUCTION
checkpoint | 2.1.1 - Pad, Hasp and Staple
label | Acceptance / Conformance Criteria - Install new Montrose Boxes on concrete plinth as per Electrical Services drawings.
label | ○ Install stainless steel hasp and staple brackets to allow for Waka Kotahi to fit their own padlock onto it.
label | Standard / Specification - PS 23.1.3.b) & 23.1.5 a) ii; Drawing 0411 - 0413.
label | Verifying Document - Photo/Visual Inspection
label | Frequency - During construction
label | Verification Activity: Activity - I
label | Verification Activity: By - SE
checkpoint | 2.1.2 - Earthing, Bonding & Surge Protection
label | Acceptance / Conformance Criteria - Install an earth electrode in accordance with the AS/NZS 3000. Install new Earth Bar and Neutral Bar c/w MEN link;
label | ○ Install Circuit Protective Devices as specified in Drawings;
label | ○ Install Switchboard as per details in Specification.
label | Standard / Specification - PS 23.1.5.a) ii & iii
label | Verifying Document - Photo/Visual Inspection
label | Frequency - During construction
label | Verification Activity: Activity - I
label | Verification Activity: By - PE/SE
checkpoint | 2.1.3 - Metering Compartment
label | Acceptance / Conformance Criteria - Liaise with the client’s electricity retailer for the installation of their three-phase meter within the metering compartment of the new Montrose Box.
label | ○ Metering Agency supply of low Voltage meters and metering current transformers.
label | Standard / Specification - PS 23.1.5 a) & 23.3.1& 23.9.4
label | Verifying Document - Comms and Photo/Visual Inspection
label | Frequency - Prior to Installation
label | Verification Activity: Activity - H
label | Verification Activity: By - PE
checkpoint | 2.2.1 - Luminaires & Poles (WK & TCC @ RAB)
label | Acceptance / Conformance Criteria - Types of luminaires and poles shall be installed as per details on the drawings or as per instruction of Client
label | ○ Luminaire Controller - PDL- 56SS10.
label | ○ Luminaires shall be fitted with Shorting Caps.
label | Standard / Specification - PS 23.1.3 c-d); 23.1.5 f-g) & Drawing 0004, 0407-0409,0413
label | Verifying Document - Photo/Visual Inspection
label | Frequency - Each Installation
label | Verification Activity: Activity - I
label | Verification Activity: By - PE/SE
checkpoint | 2.2.2 - Circuit Cabling (WK & TCC @ RAB)
label | Acceptance / Conformance Criteria - Supply and Install final circuit cabling to Luminaires from the Montrose Boxes via underground ducts and conduits as per Drawing - proposed circuiting layout.
label | Standard / Specification - PS23.1.3 g); 23.1.5 e) & Drawing 0131 -0135
label | Verifying Document - Photo/Visual Inspection
label | Frequency - Each installation
label | Verification Activity: Activity - I
label | Verification Activity: By - PE/SE
section | SECTION 3 – POST CONSTRUCTION ACTIVITY
checkpoint | 3.1 - As-Built
label | Acceptance / Conformance Criteria - As-built drawings with
label | 1) ducting routes.
label | 2) control groups,
label | 3) scene settings
label | 4) override sequences,
label | 5) luminaire and pole locations,
label | 6) the individual addresses of each luminaire, and their corresponding groups (if DALI) shown clearly for maintenance purposes.
label | 7) All changes to design to be noted, highlighted or markup clearly.
label | Standard / Specification - PS 23.1.5 h) & 23.8.5 a)-b)
label | Verifying Document - As-built Drawing/Survey Data
label | Frequency - Post construction
label | Verification Activity: Activity - H
label | Verification Activity: By - PE/ENG
checkpoint | Client Final Inspection - the signature below verifies that this ITP has been completed in accordance with the Specifications and verifies lot compliance.
textbox | Contractor's Rep Name:
textbox | Engineer's Rep. Name:
date | Date:
signoff | Add Signature
checklist | DN1210-027-003 - ITP Streetlighting - Luminaire and CCTV @underpass | itp |  |  |  |  | DN1210-027-003 - ITP Streetlighting - Luminaire and CCTV @underpass Rev 0
section | SECTION 1 – MATERIAL, PERSONNEL & THIRD PARTY APPROVAL
checkpoint | 1.1.1 - Underground Services
label | Acceptance / Conformance Criteria - Pothole all services prior to commencement of trenching. Suitably protect the existing services from construction damage.
label | Standard / Specification - PS23.5.3 b)
label | Verifying Document - Survey Data/Site Photo
label | Frequency - Pre - excavation
label | Verification Activity: Activity - H
label | Verification Activity: By - PE/SE
checkpoint | 1.1.2 - Ducting and Cabling Route
label | Acceptance / Conformance Criteria - Confirm on site the exact location of cabling routes before trenching.
label | ○ Where connecting and or coordinating with existing services, engineers shall make local modifications necessary for the correct operation of the entire system.
label | Standard / Specification - PS 23.1.5 p) & 23.5.3 a)
label | Verifying Document - Survey data/Comms with Client
label | Frequency - Prior to Installation
label | Verification Activity: Activity - H
label | Verification Activity: By - PE
checkpoint | 1.1.3 - Location of Lighting Poles, Cameras, Cable Pits and Montrose Boxes
label | Acceptance / Conformance Criteria - Confirm with surveyor and mark out the exact locations of lighting poles, Cameras, Cable Pits and Montrose boxes before installation.
label | Standard / Specification - IFC Drawings
label | Verifying Document - Survey data/Comms with Client
label | Frequency - Prior to Installation
label | Verification Activity: Activity - H
label | Verification Activity: By - PE
checkpoint | 1.2.1 - Luminaires - Underpass
label | Acceptance / Conformance Criteria - Luminaire and Pole types shall be supplied as detailed on the drawings or as per instruction of Client.
label | ○ Luminaires Controller - CASAMBI "CBU-TED" procured directly from Energy Light NZ.
label | Standard / Specification - PS 23.1.5 g) & Drawing 0412
label | Verifying Document - Material data sheet and engineers approval
label | Frequency - Before each Installation
label | Verification Activity: Activity - H
label | Verification Activity: By - ENG
label | Comments / Closeout Details - PE/SE need to check on site to guarantee right type of luminaries and switch are installed at specific location.
checkpoint | 1.2.2 - CCTV Cameras and PoE Switches
label | Acceptance / Conformance Criteria - TCC Approved IP67 IK10+
label | ○ With Weatherproof Housing , Vandal Resistant and PoE Dome (HD1080p, 2MP), Sensitivity down to 0.01 lux
label | ○ Have intelligent auto exposure to offer front and back light compensation.
label | ○ TCC approved Power-over- Ethernet (PoE)
label | Standard / Specification - PS23.1.5 n)
label | Verifying Document - Material data sheet and engineers approval
label | Frequency - Before each Installation
label | Verification Activity: Activity - H
label | Verification Activity: By - ENG
section | SECTION 2 – CONSTRUCTION
checkpoint | 2.1.1 - Luminaires - Underpass
label | Acceptance / Conformance Criteria - Types of luminaire and poles shall be installed as per details on the drawings or as per instruction of Client.
label | ○ Luminaire Dimmer Controller - CASAMBI "CBU-TED".
label | ○ Time and Dimming percentage be adviced by Light Engineer WSP.
label | Standard / Specification - PS 23.1.3 c-d); 23.1.5 f-g) & Drawing 0415
label | Verifying Document - Comms and Photo/Visual Inspection
label | Frequency - Each Installation
label | Verification Activity: Activity - I
label | Verification Activity: By - PE
checkpoint | 2.1.2 - Circuit Cabling - Underpass
label | Acceptance / Conformance Criteria - Every second luminaire shall be on separate circuit (MSB-TC-NMB/R3 and B7) as per Drawing and terminate into a CASAMBI "CBU-TED" Dimmer Driver Controller via individual 230V-rated Switches.
label | Standard / Specification - PS 23.1.5 g) & Drawing 0405,0415
label | Verifying Document - Comms /Photo/Visual Inspection
label | Frequency - Each Installation
label | Verification Activity: Activity - I
label | Verification Activity: By - PE/SE
checkpoint | 2.2.1 - Camera and Cabinet Location
label | Acceptance / Conformance Criteria - Cameras mount at high level on chamfered edge of underpass or the underside of the sealing if no space after lighting installation.
label | ○ Lockable CCTV Cabinet mount at high level underneath the chamfered edge of underpass.
label | Standard / Specification - Drawing 0406
label | Verifying Document - Photo/Visual Inspection
label | Frequency - Prior to installation
label | Verification Activity: Activity - H
label | Verification Activity: By - PE
checkpoint | 2.2.2 - Circuit Cabling
label | Acceptance / Conformance Criteria - Cabling from cabinet to camera through ridged conduit.
label | ○ Between Montrose Box(MSB-TC-NMB/R7) and Cabinet - Tight buffered outdoor OM4 Optical Fibre
label | ○ Between Cabinet and Cameras --CAT6A U/UTP Cable in 25 mm conduit
label | Standard / Specification - Drawing 0414
label | Verifying Document - Photo/Visual Inspection
label | Frequency - Each installation
label | Verification Activity: Activity - I
label | Verification Activity: By - PE/SE
checkpoint | 2.2.3 - IP Addressing, Programming of PoE Network Switches
label | Acceptance / Conformance Criteria - Liaison with TCC for IP addressing and Programming of PoE Network switches.
label | Standard / Specification - PS 23.1.4 m)
label | Verifying Document - Comms Record
label | Frequency - Prior Installation
label | Verification Activity: Activity - H
label | Verification Activity: By - PE
section | SECTION 3 – POST CONSTRUCTION ACTIVITY
checkpoint | 3.1 - As-Built
label | Acceptance / Conformance Criteria - As-built drawings with
label | 1) ducting routes.
label | 2) control groups,
label | 3) scene settings
label | 4) override sequences,
label | 5) luminaire and pole locations,
label | 6) the individual addresses of each luminaire, and their corresponding groups (if DALI) shown clearly for maintenance purposes.
label | 7) All changes to design to be noted, highlighted or markup clearly.
label | Standard / Specification - PS 23.1.5 h) & 23.8.5 a)-b)
label | Verifying Document - As-built Drawing/Survey Data
label | Frequency - Post construction
label | Verification Activity: Activity - H
label | Verification Activity: By - PE/ENG
checkpoint | Client Final Inspection - the signature below verifies that this ITP has been completed in accordance with the Specifications and verifies lot compliance.
textbox | Contractor's Rep Name:
textbox | Engineer's Rep. Name:
date | Date:
signoff | Add Signature
checklist | DN1210-027-004 - ITP Streetlighting - Commission and Post Construction | itp |  |  |  |  | DN1210-027-004 - ITP Streetlighting - Commission and Post Construction Rev 0
section | SECTION 1 – Commissioning and Testing
checkpoint | 1.1.1 - Commissioning - Luminaires (WK RAB)
label | Acceptance / Conformance Criteria - Carry out full commissioning of the Light Controls as detailed on the drawings.
label | Standard / Specification - PS 23.1.5 f) -g)
label | Verifying Document - Photo/Visual Inspection and Commissioning Records
label | Frequency - Each Commissioning
label | Verification Activity: Activity - I
label | Verification Activity: By - ENG
checkpoint | 1.1.2 - Commissioning - Luminaires (TCC RAB)
label | Acceptance / Conformance Criteria - Carry out full commissioning of the Light Controls as detailed on the drawings.
label | ○ Also record "Benchmark" energy meter reading from the lighting switchboards of all levels to demonstrate power consumption when ALL luminaires are running at 100%.
label | Standard / Specification - PS 23.1.5 g) & h)
label | Verifying Document - Photo/Visual Inspection and Commissioning Records
label | Frequency - Each Commissioning
label | Verification Activity: Activity - I
label | Verification Activity: By - ENG
checkpoint | 1.1.3 - Commissioning - Luminaires Underpass
label | Acceptance / Conformance Criteria - ON/OFF Operation + Dimming Function etc. on each Lighting Circuit under direction of Energy Light NZ utilising Calibrated Lux Meter.
label | Standard / Specification - PS 23.1.3 e); 23.1.5 g) & Drawing
label | Verifying Document - Photo/Visual Inspection and Commissioning Records
label | Frequency - Each Commissioning
label | Verification Activity: Activity - I
label | Verification Activity: By - ENG
checkpoint | 1.2.1 - Cameras
label | Acceptance / Conformance Criteria - Testing Optic fibre fromTCC Montrose Cabinet to underpass CCTV Cabinet;
label | ○ Testing CAT6A U/UTP Cabling from CCTV Cabinet to each CCTV Camera.
label | ○ Liaison with TCC for Commissioning and Testing including camera adjustment to achieve the desired FOV.
label | Standard / Specification - PS 23.1.4 m)
label | Verifying Document - Testing/Commissioning Record
label | Frequency - Each Testing/Commissioning
label | Verification Activity: Activity - H
label | Verification Activity: By - PE
section | SECTION 2 – POST CONSTRUCTION ACTIVITY
checkpoint | 2.1 - Electrical Certificate of Compliance (CoC) & Electrical Safety Certificate (ESC)
label | Acceptance / Conformance Criteria - Obtain final certification of the installed systems by an independent electrical inspector approved by the Electricity Workers Registration Board.
label | Standard / Specification - PS 23.1.5 p)
label | Verifying Document - CoC and ESC
label | Frequency - Post commissioning
label | Verification Activity: Activity - R
label | Verification Activity: By - PE
checkpoint | 2.2 - As-Built
label | Acceptance / Conformance Criteria - As-built drawings with
label | 1) ducting routes.
label | 2) control groups,
label | 3) scene settings
label | 4) override sequences,
label | 5) luminaire and pole locations,
label | 6) the individual addresses of each luminaire, and their corresponding groups (if DALI) shown clearly for maintenance purposes.
label | 7) All changes to design to be noted, highlighted or markup clearly.
label | Standard / Specification - PS 23.1.5 h) & 23.8.5 a)-b)
label | Verifying Document - As-built Drawing/Survey Data
label | Frequency - Post construction
label | Verification Activity: Activity - HP
label | Verification Activity: By - PE/ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | Client Final Inspection - the signature below verifies that this ITP has been completed in accordance with the Specifications and verifies lot compliance.
textbox | Contractor's Rep Name:
textbox | Engineer's Rep. Name:
date | Date:
signoff | Add Signature