## Resources
Rich Type | Id | Warnings | type | name | values | prefix | postfix | Usage Count | User Addable | Template Name | Template Id
checklist-sectioned | 2df36136-31f8-45b7-97aa-f4d64aba110f |  | checklist | Ceiling Lining ITP |  |  |  |  | Yes | Ceiling Lining ITP | 0d2b0799-ef1b-49ff-993c-abde61a55920
checkpoint-group | 573e94a8-d70d-493d-a3cf-42f400af80de |  | section | Construction – Tile ceiling, Grid ceiling, Lining
checkpoint-status | 8850f615-6810-477d-9ef0-a950cb732f6c |  | checkpoint | Provide board lining to a finish and workmanship as per supplier installation guides.
checkpoint-status | 3fe8a1b5-720a-43fa-b463-b5b7f8c76116 |  | checkpoint | Fit accurately and neatly, without distortion and free from air leakage and staining.
checkpoint-status | 84ec4f0b-ec6f-470c-97bb-1990c46e21bb |  | checkpoint | Clip locks: Where ceiling units are exposed to loads from wind actions or as required, insert lock clips at the junction of carrier rails and units.
checkpoint-status | d61793a1-6325-43e8-a6fe-d884b0ef8dcd |  | checkpoint | Set out patterned or heavily textured materials with a consistent direction of pattern or texture.
checkpoint-status | 632e43f2-05d1-4e36-8ce9-994a693f6e9c |  | checkpoint | Cut ceiling unit edges: conceal, or finish to match prefinished edges.
checkpoint-status | 9094a2dc-3057-4f9c-a992-a1be81bf0633 |  | checkpoint | Multiple sheet layers to fire rated and acoustic rated elements: Fill & flush up all joints and fixings in each layer and caulk up perimeters and penetrations before commencing succeeding layers. Stagger all sheet joints by minimum 200mm.
checkpoint-status | 202ecafd-66ab-4178-ae3b-3166ab4fcf1a |  | checkpoint | Board joints support: Provide framing parallel to the joint on each side. Do not fix the lining to abutting building surfaces
checkpoint-status | 0b4bbc9b-83e5-4636-a175-0dab235af7f1 |  | checkpoint | Flush joints: Provide recessed edge sheets and finish flush using perforated paper reinforcing tape. Locate & position joints to intersect light fixtures, vents or air diffusers.
checkpoint-status | 48ec7c6a-6296-4b09-a9a5-0e94fc782f0c |  | checkpoint | Tolerances: Suspension system bearing surface for flush lined ceiling to AS/NZS 2589 table 4.2.2
checkpoint-status | 5a0517f9-1ea5-4d2e-9020-8fc8d1271156 |  | checkpoint | Levelness: Max tolerance of ±5 mm relative to the documented height datum for the particular ceiling in each room or space.
checkpoint-status | 89415b86-aff3-4d13-9761-0e4eff8890ca |  | checkpoint | Trims & accessories: Provide trims at junctions with other building elements and surfaces, including walls, beams and penetrations
checkpoint-status | b8dff5ee-7e9d-49a4-95f6-33764bc84def |  | checkpoint | Layers of gib to match plan or all full under the GIB substitution list
checkpoint-status | a6de79f1-90ae-44f6-a8c1-64910539dbc8 |  | checkpoint | Screw centres = As per GIB instructions 300mm centres 12mm in from the edges
checkpoint-status | ee0cc3b7-a852-4271-b4ca-1c35ec68abe9 |  | checkpoint | Screw length = 32mm length on single layer 47mm on double layer
checkpoint-group | 39b21f39-8d87-4b4c-9643-85f93c101c04 |  | section | Control joints
checkpoint-status | 4c51286e-9a1a-4a27-aeaf-48aed84ba035 |  | checkpoint | Align ceiling control joints with the structural control joints. Do not bridge structural control joints.
checkpoint-status | ba6d9b1e-1631-4968-8c49-99161e72e9d0 |  | checkpoint | Provide purpose made metallic coated control joint beads where documented.
checkpoint-status | 5bbc573a-c3a3-4582-9ea2-7d47adba5366 |  | checkpoint | Provide framing parallel to the joint on each side.
label | 6e61e299-97be-56df-90c4-908dad355411 |  | note | Plasterboard lining: 12m centres
label | 49257437-8d10-52f7-8ac0-5a5137cfb3c7 |  | note | Fibre cement lining: 7.2m centres
checkpoint-status | 1d5c7545-0859-4b38-84f7-841187166297 |  | checkpoint | Infection control: Provide full depth paintable sealant, finished flush with the face of the lining, to locate where documented
checkpoint-group | d87cf7b2-8137-4337-88a0-1a1ab842f1e2 |  | section | Bulkheads
checkpoint-status | 20786364-f822-48c5-9969-d084253c8d4a |  | checkpoint | Integrate bulkheads with the ceiling structure and brace to prevent lateral movement. Where ceiling is terminated at the bulkhead, provide for seismic requirements
checkpoint-group | cdf953db-7761-4866-997a-3e8b28cdfc2d |  | section | Access panels
checkpoint-status | 9837da9d-e8b1-4cff-9ae6-c2f20cb991f8 |  | checkpoint | Match the access panels to the ceiling in appearance and performance
label | b3a8ad34-3211-5651-bbad-879670c45973 |  | note | Provide each access panel with an ID
checkpoint-status | 49ccfdfe-2522-4e1d-9f1e-8985eb1f6035 |  | checkpoint | Provide access panels supported and anchored to permit ready removal and refixing
checkpoint-status | 8e950e33-1ab6-455d-b53b-dc5996e79f96 |  | checkpoint | Reinforce the back of the access panel to prevent warping and facilitate handling
checkpoint-status | b74f78c2-1683-4c04-ac2e-1d423351210c |  | checkpoint | Provide fire rated and acoustic rated panels where documented or where required to maintain the designated rating of the ceiling element
checkpoint-group | 7860f69d-ddb8-4008-bc95-689887a56ca1 |  | section | Additional checks for fire-protective board lining
checkpoint-status | c7277344-13a5-4394-8f8f-9e9dc573b680 |  | checkpoint | Check the fire resistance levels: Drawings and Spec Sec 4.6 Misc. Items Schedule
checkpoint-status | edc26be4-3e94-452a-bc61-3d2e5c749dba |  | checkpoint | Fixings: Direct to concrete elements and to purpose made steel framing
checkpoint-status | 9bb65ab1-2cef-4854-affa-3d4ea4b1e482 |  | checkpoint | Penetrations: Seal penetrations in the board lining to maintain the integrity of the required fire resistance level including suspended ceiling hangers and suspension systems for services.
checkpoint-status | 4f12ae01-0c9c-4c74-9fd4-b4b444199077 |  | checkpoint | Board perimeter: Provide fire sealant and trims at junctions with other building elements and surfaces, including walls, beams and penetrations to maintain the required fire resistance levels.
label | ac94ff35-f4f9-5ec0-8ab4-27c702ab902d |  | note | Label each fire stopping to AS/NZS 2589.1
checklist-sectioned | bb7bc679-8fd4-4f35-95c6-1301468571ef |  | checklist | Ceiling Framing ITP |  |  |  |  | Yes | Ceiling Framing ITP | 112f74de-48e4-44a4-9d11-44a6e250c8f0
checkpoint-group | 6b080bce-74ff-443f-b67f-dc2269d36c6e |  | section | Set Out
checkpoint-status | 730f299e-6767-4c0c-b1a7-4364bc9297c4 |  | checkpoint | Reflected ceiling plans current revisions checked and ceiling set out completed as per the current plans
checkpoint-group | 63acb96c-1d04-4312-89b9-bda4812d136f |  | section | Construction Generally
checkpoint-status | 395f34e9-5ac7-4c15-bb55-32ef57ad8855 |  | checkpoint | Install & fix to prevent looseness or rattling of ceiling components
checkpoint-status | f90fc459-d7e2-426b-bbed-657b2bf9e6ca |  | checkpoint | Ceiling systems do not amplify structural-borne sounds.
checkpoint-status | b6de8dda-e8d5-4bad-b11d-72c76244f568 |  | checkpoint | Install the ceiling to allow for differential movement at abutting surfaces
checkpoint-status | 1719141e-ab75-495d-bb9a-1f148b414301 |  | checkpoint | Post tensioned concrete: Minimum embedment for fixing: 45mm and minimum clearance of fixing from any tendon: 25mm
checkpoint-group | f69cc7e5-f0c2-4aeb-ad32-e1dc4bc7ba11 |  | section | Construction – Suspension system
checkpoint-status | 8ee9e184-676b-469f-b607-352d0e5b013c |  | checkpoint | Provide suspension system and workmanship as per supplier installation guides & KCL Design
checkpoint-status | 8501fc67-cc17-4e34-a55a-b1f9699515dc |  | checkpoint | Services: Do not fix to the installed services. Where services obstruct the ceiling supports, provide bridging and suspension on each side of the services.
checkpoint-status | c5e8c961-a41c-45fb-a8ae-07f85522ddf5 |  | checkpoint | Provide additional back support or suspension members to prevent distortion, overloading or excessive vertical deflection.
checkpoint-status | 8925a046-d3ee-4a32-bf10-a7857bc39228 |  | checkpoint | Ensure that the failure of any one suspension point does not cause a progressive failure of the ceiling.
checkpoint-status | a77c29de-d244-4f07-907e-aa9593b538fa |  | checkpoint | Provide height adjustment with a length adjustment device at each suspension point, permitting length variation of at least 50mm
checkpoint-status | 1b92bf7a-1e84-4530-b0ee-60aa501d9668 |  | checkpoint | Seismic resistant: Provide bracing and clips to framing members to prevent lateral movement and to resist seismic action. Do not provide visible fixings (screws or rivets) where they will be exposed to view.
checkpoint-status | a82f6cfa-6a32-4f49-92e5-103ddd90eeb8 |  | checkpoint | Uplift: Suspension system and framing to resist uplift.
checkpoint-status | 41e2fbfd-168e-4721-a126-466a77b542fb |  | checkpoint | Tolerances: Flatness, twist, winding and bow: 1.5 mm deviation from a 1.5m straightedge places in any position
checkpoint-status | 64160efc-f22b-4621-9589-ca44d94520a9 |  | checkpoint | Suspension system completed – Ready for installation of ceiling tiles, lining and panels.
checkpoint-status | aa7ee05f-7758-45f7-8b57-38246286f1cb |  | checkpoint | Confirm all service trades are complete & ready for closing in of ceiling
checkpoint-group | a553e712-eaa2-42a3-8e29-db1d338e662e |  | section | Bulkheads
checkpoint-status | 820dd576-253f-47a7-88ee-4fae8e8f3cf9 |  | checkpoint | Integrate bulkheads with the ceiling structure and brace to prevent lateral movement. Where ceiling is terminated at the bulkhead, provide for seismic requirements
checkpoint-group | cfe3fb91-3a68-4814-8308-20e82c29cb30 |  | section | Smoke baffles and acoustic baffles
checkpoint-status | 59f57470-683e-4749-a3fc-f8692d99314f |  | checkpoint | Provide approved smoke and acoustic baffles secured fixed to metal angles and smoke sealed at board joints and to adjoining building elements
checklist-flat | 3cf6696b-b6dd-496f-9f72-390d2561093d |  | checklist | Daily Pre Start/Works Checklist |  |  |  |  | Yes | Daily Pre Start/Works Checklist | 3e51efe1-df54-4280-acca-742e3d6bc8c6
checkpoint-status | 9821d8fa-107b-4404-a6cd-8a9c9c60245a |  | checkpoint | Daily pre start meeting completed
text | 71493ecd-4d94-5a7e-b97d-4c60020af824 |  | textbox | Date
text | 1cc2a279-9f7b-59c3-986b-2384038d8793 |  | textbox | Time
text | 2e6de38f-be52-56a5-8f8f-722590320a32 |  | textbox | Location of work being performed
checkpoint-status | bf39421e-b531-4fa4-a717-38d956916c01 |  | checkpoint | Is the area clear, tidy, dry, accessible and well lit? (take multiple photos of installation area)
checkpoint-status | 62912cdd-f28b-4bd5-bab9-a9dc8fa38317 |  | checkpoint | Delivery inspection (Take a photo of the delivery taking place and of delivery docket) (*note: list all items not delivered)
checkpoint-status | f0126cac-a51e-422c-b511-993aae43eb53 |  | checkpoint | Does the delivery/delivery docket match the order placed? (*note: list all items not delivered)
checkpoint-status | 82f3272f-fae6-4a6e-9943-525ae5cb2b53 |  | checkpoint | Are the correct tools ready for todays tasks?
checkpoint-status | c66700d4-ed7d-442a-b786-7617e840eedf |  | checkpoint | Are Power tool batteries on charge?
checkpoint-status | f8270810-4ce1-4af9-8644-e82e79bda5d1 |  | checkpoint | Are the correct height ladders being used for todays tasks?
checkpoint-status | 79aa73f8-a807-49fb-bd43-51e667343ed1 |  | checkpoint | Do you have the correct mandatory PPE on? (Hard Hat, Hi Vis shirt/jumper/jacket, Steel toe Boots, Safety Glasses, Safety gloves and Ear Plugs?
text | 677545ea-d7fe-550e-951b-7aa144b023ec |  | textbox | Project Manager
text | f1871854-8398-5bec-8b85-0db4a803f34a |  | textbox | Any issues from the previous day
text | c51c0acd-d87e-5b78-932e-e4036006577a |  | textbox | Any unfinished works from the previous day in the area of works?
text | c1c90f20-9f7f-5e4d-b558-62e67ca0b1f4 |  | textbox | First aiders on site today
text | ef8ed120-3fb5-5da4-a419-1fc233971c4c |  | textbox | Who are you working with today?
text | 67ffaa9a-e979-5710-a426-3cf33fe7fd53 |  | textbox | Todays tasks / jobs
text | 8f1e289d-7ec0-5557-9cb8-08e1a8988f50 |  | textbox | Any unfinished tasks / jobs from todays items? (list the items unfinished & explain why the tasks were not finished)
text | 2ad9c50b-b661-5910-bac3-58d6844bceeb |  | textbox | Attendees
checkpoint-status | fcc8710f-1edd-498a-95db-88692d46ea9d |  | checkpoint | Wadsworth Contracting Supervisor Signature
checklist-sectioned | 17b4610c-5aaa-41b1-a5e2-70dc0f0fde52 |  | checklist | Partition Lining ITP |  |  |  |  | Yes | Z - SYS - Partition Lining ITP (old version) | 4d67fa02-a507-44fa-9d2c-ba2912b309c7
checkpoint-group | ddcb70be-a117-4a6a-8518-1d73e511a8ef |  | section | Board Lining – Inspection
checkpoint-status | b3c4f4ab-d713-4edf-9533-14ccd7373f7c |  | checkpoint | Run sheets across the framing members (refer GIB standard details)
checkpoint-status | de65b2dc-4c7f-4cb7-96e9-c42361a028d6 |  | checkpoint | Stagger end joints in a brick pattern and locate them on framing members away from the corners of large opening
checkpoint-status | 64d04e68-d1f6-46a1-9a35-a4fef7a5ac4e |  | checkpoint | Achieve level of finish as specified in the Material, Component & Finishes Schedule (Sec 4.2)
checkpoint-status | 630ac749-05f9-4eec-9784-1a8147f591e8 |  | checkpoint | Multiple sheet layers: Fill & flush up all joints and fixings in each layer and caulk up perimeters and penetrations before commencing succeeding layers.
checkpoint-status | e496cd80-5218-4110-98f9-6feb3176e5d9 |  | checkpoint | Stagger all sheet joints by minimum 200mm
checkpoint-status | 0834add2-2b84-48a0-ad96-1926ccf66a9d |  | checkpoint | Doors & Internal Window Opening: Check Door schedule, Window schedule and Kit of parts
checkpoint-status | b57a7a7f-6bfe-4e7e-b9e5-5b92d6cd1144 |  | checkpoint | Board joints: Do not fix the lining to abutting building surfaces
checkpoint-status | 5b645d57-b7fb-44d1-96f7-0d3fca4d9e90 |  | checkpoint | Butt joints: Provide perforated paper reinforcing tape
checkpoint-status | 96566fde-5575-4f18-b942-5e5282fef35e |  | checkpoint | External corners: Provide matching purpose made beads
checkpoint-status | 7450393e-f9b8-456d-8107-986b59335b50 |  | checkpoint | Internal corners: Provide paper tape and bedding compound
checkpoint-status | f7986a20-d0c9-4647-908f-02103309c936 |  | checkpoint | Provide sealants at junctions between partition systems and with other building elements
checkpoint-status | e81383eb-dc5f-4753-896e-a2833ccfddb6 |  | checkpoint | Provide trim such as beads, moulding and stops to make neat junctions between lining components, finishes and adjacent surfaces
checkpoint-group | a60a146a-63b6-41ea-bb41-9669f6892e90 |  | section | Additional Checks for Fire Walls – Inspections
checkpoint-status | 405a577e-dea1-460f-8e5a-3223932a80f0 |  | checkpoint | Installed as per GIB design & install specification
checkpoint-status | 9e011088-13d0-43c0-8cbe-40c9e910cfe7 |  | checkpoint | Correct FRL achieved
checkpoint-status | 474cecdc-d2cc-4a4c-a54e-1a5580185def |  | checkpoint | Deflection heads and all joints sealed, taped and set (Fire Sealant is approved prior)
checkpoint-status | 5e7b895e-d35e-4b24-8d1c-d651aec93019 |  | checkpoint | All penetrations through fire walls below and above ceiling protected/sealed
checkpoint-group | 791a9cfa-f774-484c-8614-2caa2e102e4b |  | section | Additional Checks for Smoke Walls - Inspections
checkpoint-status | c73d19aa-3531-4fed-91cf-f2f70ba29292 |  | checkpoint | Installed as per GIB design & install specification
checkpoint-status | 46916a37-6d5f-4c58-8aff-fd5c23e3dd0d |  | checkpoint | Deflection heads and all joints sealed, taped and set (Sealant is approved prior)
checkpoint-status | 77952f37-6c01-475b-92ff-27d0dc6554a4 |  | checkpoint | All penetrations through smoke walls below and above ceiling protected/sealed
checkpoint-group | 824b5f18-9f68-41c1-9a8f-d5892cd6a02d |  | section | Additional Checks for Acoustic Walls – Inspections
checkpoint-status | f148c3b9-a059-468d-8aa2-92cff60f56c2 |  | checkpoint | Installed as per GIB design & install specification.
checkpoint-status | 08ed8d44-f2cc-43e2-a74d-28cc39bd7c74 |  | checkpoint | Deflection heads and all joints sealed, taped and set (Sealant is approved prior)
checkpoint-status | 6d8f9abb-dcb0-4d94-8bd6-4331d7e55bd6 |  | checkpoint | All penetrations through acoustic walls below and above ceiling protected/sealed
checklist-sectioned | 725f580c-85f9-45f0-bc67-67217009fc11 |  | checklist | Partition Lining ITP |  |  |  |  | Yes | Partition Lining ITP | 7c79d192-1e8c-4737-a2e2-9fca8eb8ccfc
checkpoint-group | 6d3c3bf1-b041-4d5b-b76d-dc7c7b9f8b13 |  | section | Board Lining – Inspection
checkpoint-status | 6cc81177-afb9-427d-b05d-3cb719456bef |  | checkpoint | Run sheets across the framing members (refer GIB standard details)
checkpoint-status | ce641a07-71cd-4ac3-ab12-fa5158a88cb8 |  | checkpoint | Stagger end joints in a brick pattern and locate them on framing members away from the corners of large opening
checkpoint-status | ceaeac6e-5bf0-4339-834d-0fea663cf26d |  | checkpoint | Achieve level of finish as specified in the Material, Component & Finishes Schedule (Sec 4.2)
checkpoint-status | eec9ec05-be8b-4332-8fbc-735b189f520e |  | checkpoint | Multiple sheet layers: Fill & flush up all joints and fixings in each layer and caulk up perimeters and penetrations before commencing succeeding layers.
checkpoint-status | c18e5feb-a286-46d7-9db6-4d52d9ab1966 |  | checkpoint | Stagger all sheet joints by minimum 200mm
checkpoint-status | 88a60d59-0efa-4cf2-85c9-d1abceaa4938 |  | checkpoint | Layers of gib to match plan or all full under the GIB substitution list
checkpoint-status | 042e4a9c-18a9-46e8-8346-5941e5bc73f2 |  | checkpoint | Screw centres = As per GIB instructions 300mm centres 12mm in from the edges
checkpoint-status | ec007ace-0c61-4a79-98c0-4785508fff37 |  | checkpoint | Screw length = 32mm length on single layer 47mm on double layer
checkpoint-status | de9af7a9-9926-49ff-9d7a-cb163bb9011d |  | checkpoint | Doors & Internal Window Opening: Check Door schedule, Window schedule and Kit of parts
checkpoint-status | d64f380b-e499-4262-9ca9-e6d9a1662ea0 |  | checkpoint | Board joints: Do not fix the lining to abutting building surfaces
checkpoint-status | 6ad259b6-6372-4614-9a2e-3b5511218386 |  | checkpoint | Butt joints: Provide perforated paper reinforcing tape
checkpoint-status | e80dd4b3-4df1-4739-acc5-92f3725dddef |  | checkpoint | External corners: Provide matching purpose made beads
checkpoint-status | e0cfe184-f530-4258-aa2e-e00842897874 |  | checkpoint | Internal corners: Provide paper tape and bedding compound
checkpoint-status | 7740e4c4-94f9-4e3c-ae9e-df5995d17795 |  | checkpoint | Provide sealants at junctions between partition systems and with other building elements
checkpoint-status | 75fb4a03-0b42-4818-a316-d37f2f192bb1 |  | checkpoint | Provide trim such as beads, moulding and stops to make neat junctions between lining components, finishes and adjacent surfaces
checkpoint-group | 25bf4836-ea6a-4b93-bfe3-b1ac13820336 |  | section | Additional Checks for Fire Walls – Inspections
checkpoint-status | a6322902-9f0e-4977-8c8b-b85153a0a439 |  | checkpoint | Installed as per GIB design & install specification
checkpoint-status | eab43593-ed5f-4053-8800-cd678719c280 |  | checkpoint | Correct FRL achieved
checkpoint-status | 03665ddf-c188-44e0-bc6b-e48cb71e3f91 |  | checkpoint | Deflection heads and all joints sealed, taped and set (Fire Sealant is approved prior)
checkpoint-status | 3037d087-0752-4565-acdc-48aaed6c9dd5 |  | checkpoint | All penetrations through fire walls below and above ceiling protected/sealed
checkpoint-group | 2c09c774-bc2e-40fa-ae15-f5a9b3b27b57 |  | section | Additional Checks for Smoke Walls - Inspections
checkpoint-status | c0af3dad-89b5-4d7f-91e4-dc1f11d0b195 |  | checkpoint | Installed as per GIB design & install specification
checkpoint-status | 5853ee25-07de-4a5c-ae1e-3f37ae39f435 |  | checkpoint | Deflection heads and all joints sealed, taped and set (Sealant is approved prior)
checkpoint-status | 2bdf26fd-5201-4a46-ba75-635a14dfd90a |  | checkpoint | All penetrations through smoke walls below and above ceiling protected/sealed
checkpoint-group | 2401deae-fac6-4607-9c38-702a8736ab18 |  | section | Additional Checks for Acoustic Walls – Inspections
checkpoint-status | ad10079d-1d46-4c4b-8df9-ce31bc8e915a |  | checkpoint | Installed as per GIB design & install specification.
checkpoint-status | b0b0b078-8568-49c9-889d-069e5004451d |  | checkpoint | Deflection heads and all joints sealed, taped and set (Sealant is approved prior)
checkpoint-status | c07a5bfd-2518-4a69-ba82-ee2292b82b8b |  | checkpoint | All penetrations through acoustic walls below and above ceiling protected/sealed
checklist-sectioned | 5eedaa6b-1f14-4f95-a376-efebe09ab66d |  | checklist | Partition Framing ITP |  |  |  |  | Yes | Partition Framing ITP | 869b3987-e077-4efc-b5d1-fe0229668bc0
checkpoint-group | ec0314b0-02e6-4dec-8052-a8e704c5c27c |  | section | Set Out
checkpoint-status | 3de682d0-f7d5-4389-b755-8a5ff383e54e |  | checkpoint | Partitions set out plans current revisions checked and wall set out competed as per the current plans
checkpoint-group | 932fee3b-ee2d-45d6-b1df-a808b1f87ffb |  | section | Stud Framing / Wall Strapping – Inspection
checkpoint-status | d20c35f3-fb60-4576-9484-c452fb93eea2 |  | checkpoint | Check sizes and spaces as per the partition types / KCL Design.
label | 59177260-4c80-5b41-a77b-88777fe3ad62 |  | note | Fix tracks ?600mm centres and 100mm from ends
checkpoint-status | 5995a4d5-e84f-46e7-a7ca-7007e3515402 |  | checkpoint | Fixing to post tensioned concrete: Maximum embedment for fixings = 45mm
checkpoint-status | 581f68db-bc90-40bb-af8e-948c65386b2c |  | checkpoint | Install boxed double studs / Maxi Jambs at jambs to all openings
label | 542cce95-26d4-5d0a-99ce-53657183aea5 |  | note | Part height partitions: Brace as per KCL Design
label | 9d5a6438-823a-5124-a886-c7400556d4f4 |  | note | Full height partitions: Fix deflection head tracks to the floor slab soffit to allow a minimum deflection capacity of 20mm.
checkpoint-status | 8229566e-4cf2-4a6b-89a1-7532f3932bd8 |  | checkpoint | Achieve overlap of at least 30 mm of the deflection head channel’s section vertical leg with the top plate of the wall framing
checkpoint-status | 911f404a-fff4-4876-8675-6aef7c7fe268 |  | checkpoint | Rotate intermediate studs into tracks for friction fixing
checkpoint-status | 1e08d961-9e53-4d77-b07a-af94a7425f90 |  | checkpoint | Staggered stud framing walls: Studs staggered at 300mm centres set in oversized top & bottom plates to allow each face to have stud fixing at 600mm centres minimum or as per KCL fixing requirement
checkpoint-status | fad016ca-9b9e-4978-951a-78a0b7f0d2b4 |  | checkpoint | Stud service holes: Splice additional stiffening to studs if site cut service holes exceed 1/3 the width of the member
checkpoint-status | 18025ca2-b48f-4e81-a434-5838b71496d9 |  | checkpoint | Provide fire, smoke and acoustic sealing where indicated on the drawings/details
checklist-flat | de4a3226-ef77-41bb-8e53-7308953c3771 |  | checklist | Documents |  |  |  |  | Yes | Documents | 9f66fa66-5d04-4a0f-b57e-d293c0cf5621
checkpoint-status | e75941c1-8f08-4cc7-9fa4-1482609dee55 |  | checkpoint | Structural design, documentation and certification for secondary structural steel elements providing support for partitions and fixtures
checkpoint-status | b0a2236e-0552-4ff5-9db9-493bf63d711b |  | checkpoint | Samples and prototypes submitted and approved (Fire sealants approved)
checkpoint-status | b6d4b748-316a-4767-adae-f95c82ad154d |  | checkpoint | Test results of prototypes submitted
checklist-sectioned | c3102496-9701-4fa5-9c70-53b34f373176 |  | checklist | Partition Framing ITP |  |  |  |  | Yes | Z - SYS - Partition Framing ITP (old version) | 9f8f1a80-c027-477a-a3b8-a24cf6c52b09
checkpoint-group | ea2330b2-1e45-4bc3-ae92-14f5f05441a7 |  | section | Set Out
checkpoint-status | dc4b9f10-1244-4977-a145-42c40279a012 |  | checkpoint | Partitions set out plans current revisions checked and wall set out competed as per the current plans
checkpoint-group | 4597c103-51eb-466f-b83f-346825591bd2 |  | section | Stud Framing / Wall Strapping – Inspection
checkpoint-status | 27a1c153-c785-405f-a911-2d868d1bac2f |  | checkpoint | Check sizes and spaces as per the partition types / KCL Design.
label | 8d4ef346-d00f-5c88-98df-cd5822074acd |  | note | Fix tracks ≤600mm centres and 100mm from ends
checkpoint-status | f8cd1578-770c-4e78-9c25-a9b2670dfc29 |  | checkpoint | Fixing to post tensioned concrete: Maximum embedment for fixings = 45mm
checkpoint-status | c324af5d-0899-4cff-b882-fe97c8c32d68 |  | checkpoint | Install boxed double studs / Maxi Jambs at jambs to all openings
label | 5cc9a693-9f93-5f3c-9fba-27165f4de713 |  | note | Part height partitions: Brace as per KCL Design
label | 830285ea-0f88-5d6b-8a24-cb1e34a3f160 |  | note | Full height partitions: Fix deflection head tracks to the floor slab soffit to allow a minimum deflection capacity of 20mm.
checkpoint-status | ab7d038b-db54-452d-9d18-f621d785be31 |  | checkpoint | Achieve overlap of at least 30 mm of the deflection head channel’s section vertical leg with the top plate of the wall framing
checkpoint-status | 4bf243f0-3d1b-4da6-a06e-4d313b0c9654 |  | checkpoint | Rotate intermediate studs into tracks for friction fixing
checkpoint-status | d7985756-0df1-494f-acf6-0a7f67d56b1d |  | checkpoint | Staggered stud framing walls: Studs staggered at 300mm centres set in oversized top & bottom plates to allow each face to have stud fixing at 600mm centres minimum or as per KCL fixing requirement
checkpoint-status | 20085256-08de-4275-98cc-4e295440b2fe |  | checkpoint | Structural floor control joints: Disconnect partitions over joints with detached double studs and ensure bottom tracks, bracing and top tracks are not fastened across joints
checkpoint-status | 33ec8518-1e38-4f08-b616-208ff71c9c78 |  | checkpoint | Stud service holes: Splice additional stiffening to studs if site cut service holes exceed 1/3 the width of the member
checkpoint-status | 433bb38c-595d-4ccb-8e0f-ef981f47c38a |  | checkpoint | Provide fire, smoke and acoustic sealing where indicated on the drawings/details
checklist-sectioned | fc5dea19-a410-4419-b689-eb2cc04b085e |  | checklist | Ceiling Lining ITP |  |  |  |  | Yes | Z - SYS - Ceiling Lining ITP (old version) | df3def62-6857-461a-9e8f-44a0f57f35bd
checkpoint-group | 580973f8-59e3-4f8a-a470-537b6044e8f3 |  | section | Construction – Tile ceiling, Grid ceiling, Lining
checkpoint-status | 01ace222-86b5-40d0-950d-984b9780012b |  | checkpoint | Provide board lining to a finish and workmanship as per supplier installation guides.
checkpoint-status | 83aa3555-101f-4dfe-b82e-55ef70bd964e |  | checkpoint | Fit accurately and neatly, without distortion and free from air leakage and staining.
checkpoint-status | 29f4609e-09b6-40e5-bdb8-8a16c438f60e |  | checkpoint | Clip locks: Where ceiling units are exposed to loads from wind actions or as required, insert lock clips at the junction of carrier rails and units.
checkpoint-status | a13e9a64-d2de-49d0-86ea-ef5e6745fd88 |  | checkpoint | Set out patterned or heavily textured materials with a consistent direction of pattern or texture.
checkpoint-status | 5e6c8260-5ecd-4fc1-9198-cf9df1144c04 |  | checkpoint | Cut ceiling unit edges: conceal, or finish to match prefinished edges.
checkpoint-status | 1ff2a494-f57c-4d81-8efa-fafdc1b6c2fb |  | checkpoint | Multiple sheet layers to fire rated and acoustic rated elements: Fill & flush up all joints and fixings in each layer and caulk up perimeters and penetrations before commencing succeeding layers. Stagger all sheet joints by minimum 200mm.
checkpoint-status | 564abf2c-3319-445b-b01b-e00861eed1a0 |  | checkpoint | Board joints support: Provide framing parallel to the joint on each side. Do not fix the lining to abutting building surfaces
checkpoint-status | 6a072522-e9e8-4ae4-9dc9-2d97f3ca3018 |  | checkpoint | Flush joints: Provide recessed edge sheets and finish flush using perforated paper reinforcing tape. Locate & position joints to intersect light fixtures, vents or air diffusers.
checkpoint-status | 8db420e5-d759-4ada-a8d2-b1b8e64e77a0 |  | checkpoint | Tolerances: Suspension system bearing surface for flush lined ceiling to AS/NZS 2589 table 4.2.2
checkpoint-status | ac5aeda0-9332-4226-8081-5ec25a1b6051 |  | checkpoint | Levelness: Max tolerance of ±5 mm relative to the documented height datum for the particular ceiling in each room or space.
checkpoint-status | b69f8efb-cfd2-4cf7-a361-fcecd9fce1c1 |  | checkpoint | Trims & accessories: Provide trims at junctions with other building elements and surfaces, including walls, beams and penetrations
checkpoint-group | 22967794-ed34-47a1-b833-8645c7828164 |  | section | Control joints
checkpoint-status | c52c25d9-36ed-4548-9237-a44ffd28afa1 |  | checkpoint | Align ceiling control joints with the structural control joints. Do not bridge structural control joints.
checkpoint-status | 876b7238-3054-434a-9ee7-ccebfff3234b |  | checkpoint | Provide purpose made metallic coated control joint beads where documented.
checkpoint-status | f6ffe0b0-5abb-4cc6-b74b-77439de1f86d |  | checkpoint | Provide framing parallel to the joint on each side.
label | 3e75b228-4c5b-5d2b-baaa-562c37676074 |  | note | Plasterboard lining: 12m centres
label | d0e60426-609f-5322-88a0-77f37da62696 |  | note | Fibre cement lining: 7.2m centres
checkpoint-status | cb195eb7-5cbc-4274-a80c-57a8811f387c |  | checkpoint | Infection control: Provide full depth paintable sealant, finished flush with the face of the lining, to locate where documented
checkpoint-group | 295edd8d-925f-40d3-b743-cc2b65078515 |  | section | Bulkheads
checkpoint-status | 163786cf-1b22-4c6c-ad42-0a9e2fbbc8c0 |  | checkpoint | Integrate bulkheads with the ceiling structure and brace to prevent lateral movement. Where ceiling is terminated at the bulkhead, provide for seismic requirements
checkpoint-group | 6422a1da-a466-4bbb-b217-8c3a231a8300 |  | section | Access panels
checkpoint-status | 4de102eb-41df-4c9e-9842-fbdbbd789fda |  | checkpoint | Match the access panels to the ceiling in appearance and performance
label | 467da263-7d41-5efc-b54a-2dc46f3bdc00 |  | note | Provide each access panel with an ID
checkpoint-status | 05533283-2b76-423e-92e7-dcae23626407 |  | checkpoint | Provide access panels supported and anchored to permit ready removal and refixing
checkpoint-status | 95055a27-67a5-4243-b226-ea920a2d13d4 |  | checkpoint | Reinforce the back of the access panel to prevent warping and facilitate handling
checkpoint-status | 769fb65f-246f-4440-90f1-4a13c6baf47b |  | checkpoint | Provide fire rated and acoustic rated panels where documented or where required to maintain the designated rating of the ceiling element
checkpoint-group | e3612730-05ad-4a64-a990-29b6329296f6 |  | section | Additional checks for fire-protective board lining
checkpoint-status | e57d58d4-dca5-4abc-80f6-79b51c6d7e93 |  | checkpoint | Check the fire resistance levels: Drawings and Spec Sec 4.6 Misc. Items Schedule
checkpoint-status | 8be3f4e1-a45f-4634-a130-95cf77c08ae8 |  | checkpoint | Fixings: Direct to concrete elements and to purpose made steel framing
checkpoint-status | 7bda2930-9e4a-48d9-b107-018a21dc06b3 |  | checkpoint | Penetrations: Seal penetrations in the board lining to maintain the integrity of the required fire resistance level including suspended ceiling hangers and suspension systems for services.
checkpoint-status | a476e53f-ccd3-45d1-aae6-f3e0354dffe7 |  | checkpoint | Board perimeter: Provide fire sealant and trims at junctions with other building elements and surfaces, including walls, beams and penetrations to maintain the required fire resistance levels.
label | bf7c1287-01bb-5eb9-8ee3-4b8280f842e3 |  | note | Label each fire stopping to AS/NZS 2589.1
checklist-flat | 8d427249-6d31-4fed-a2a9-182e1448fedc |  | checklist | Variations |  |  |  |  | Yes | Variations | f8a9069b-1f75-4ff2-85de-b86d4da5ebdd
checkpoint-status | b5614e77-c2e1-475e-8d13-adac6bd34ca5 |  | checkpoint | Work Completed Monday
text | 1c6f5a9e-be9c-54a7-8397-ca4b6bac72de |  | textbox | Daily Notes
holdpoint | 75b39f5b-479c-4748-9c62-eaacebe7facc |  | signoff | Signed Off by Wadsworth & Builder
checkpoint-status | 0486deb6-b5b1-4e69-a47d-b3e6506e79d9 |  | checkpoint | Work Completed Tuesday
text | e68c07b6-a7b7-52e9-8436-91ca798d98dd |  | textbox | Daily Notes
holdpoint | efbcfcbd-ee4e-48bc-a9a2-7548f194c41b |  | signoff | Signed Off by Wadsworth & Builder
checkpoint-status | c9ce8c7b-1b09-42dd-8785-4823de665781 |  | checkpoint | Work Completed Wednesday
text | 9c2a72d5-a1bf-56c3-bf51-9a29a00811c9 |  | textbox | Daily Notes
holdpoint | 82cb75e0-2804-466a-b3c6-8842db4ebe21 |  | signoff | Signed Off by Wadsworth & Builder
checkpoint-status | e09b8334-3f91-421a-8448-6873ea674437 |  | checkpoint | Work Completed Thursday
text | 3ba6b780-f154-5c47-a0a1-02a87c6c14a3 |  | textbox | Daily Notes
holdpoint | 860849b3-5e63-4a93-bdc5-092f40da015a |  | signoff | Signed Off by Wadsworth & Builder
checkpoint-status | af827f8c-2a5b-4388-b2ce-675a558aae86 |  | checkpoint | Work Completed Friday
text | 4d25f518-cb3b-5b37-8f7f-a568bc33acd5 |  | textbox | Daily Notes
holdpoint | 5c0dbc97-7398-43ed-bfdf-449cf3eddaed |  | signoff | Signed Off by Wadsworth & Builder
checkpoint-status | 05b17c36-2637-4a8f-a094-a5b16dcb04f1 |  | checkpoint | Work Completed Saturday
text | 6eff622f-79cf-5801-857b-d065a7b3f53d |  | textbox | Daily Notes
holdpoint | d890bf75-8dd3-4a12-9d5d-5611bf48e78a |  | signoff | Signed Off by Wadsworth & Builder