## res_ITP_1_Inspection_and_Test_P
type | name | values | prefix | postfix | usage count | user addable | template name
checklist-flat | Underground Line Grout Filling |  |  |  |  | Yes | ITP T04 T06 Tank Upgrade T039/C1 - Underground Line Grout Filling
checkpoint | 1. Issued For Construction Drawings & Specification
label | Applicable Documents - General Civil Construction Specification EW-020-203 Construction Drawings
label | Acceptance Criteria - Clear scope of work, Grout capacity calculation
label | Leading Hand - N/A
label | Supervisor - W - UCCL Supervisor or Project Engineer
label | Third Party (state) - R - Civil Inspector
checkpoint | 2. Flushing of redundant underground pipe line with water
label | Applicable Documents - General Civil Construction Specification EW-020-203
label | Acceptance Criteria - Redundant underground pipes cleaned out and free of obstruction
label | Leading Hand - P - Leading Hand
label | Supervisor - H - UCCL Supervisor or Project Engineer
label | Third Party (state) - H - Civil Inspector
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 3. Install filling fittings and breather pipe and or conduit at highest end. Grout fill redundant underground pipeline
label | Applicable Documents - General Civil Construction Specification EW-020-203 Atlas Concrete Grout Specification
label | Acceptance Criteria - Filling fittings shall be pressure rated ≥ max. pump pressure. Grout to be minimum 17.5MPa. Concrete Delivery Dockets, Pipework pre-washed with water, Grout filling witnessed by CTS
label | Leading Hand - P - Leading Hand
label | Supervisor - H - UCCL Supervisor or Project Engineer
label | Third Party (state) - H - Civil Inspector
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 4. Record / As-built drawing
label | Applicable Documents - General Civil Construction Specification EW-020-203 Atlas Concrete Grout Specification
label | Acceptance Criteria - Grouted redundant pipes shall be recorded on as-built drawing and given to CTS drawing Office with a drawing office request (DOR) for the site drawing to be updated
label | Leading Hand - N/A
label | Supervisor - P - UCCL Supervisor or Project Engineer
label | Third Party (state) - H - Worley CE/PE
holdpoint | AUTHORITY HOLDPOINT