## res_ITP_1_Inspection_and_Test_P
type | name | values | prefix | postfix | usage count | user addable | template name
checklist-flat | Tank Annular Stud Welding |  |  |  |  | Yes | ITP T04 T06 Tank Upgrade T039/C1 - Tank Annular Stud Welding
checkpoint | 1. Issued For Construction Drawings
label | Applicable Documents - Civil /Struct Design pack 310449/C1 Rev A IFC drawings issued 05 May 2023
label | Acceptance Criteria - IFC drawings issued. Clear scope of work.
label | Leading Hand - N/A
label | Supervisor - N/A
label | Third Party (state) - P - Worley’s project engineer
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 2. Procurement of studs
label | Applicable Documents - Civil /Struct Design pack 310449/C1 Rev A IFC drawings issued 05 May 2023
label | Acceptance Criteria - IFC drawings issued. Clear scope of work. Studs procured as per drawing pack
label | Leading Hand - N/A
label | Supervisor - H - UCCL Supervisor or Project Engineer
label | Third Party (state) - R - Civil Inspector
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 3. Surface preparation by abrasive blasting on tank 04 annular downturn plate for stud welding
label | Applicable Documents - INVIL methodology to weld studs AWS D1.1
label | Acceptance Criteria - The areas to which the studs are to be welded shall be free of scale, rust, moisture, paint, or other injurious material to the extent necessary to obtain satisfactory welds and prevent objectionable fumes.
label | Leading Hand - N/A
label | Supervisor - W - UCCL Supervisor or Project Engineer
label | Third Party (state) - R - Civil Inspector
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 4. Surface preparation by abrasive blasting on tank 06 annular downturn plate for stud welding
label | Applicable Documents - INVIL methodology to weld studs AWS D1.1
label | Acceptance Criteria - The areas to which the studs are to be welded shall be free of scale, rust, moisture, paint, or other injurious material to the extent necessary to obtain satisfactory welds and prevent objectionable fumes.
label | Leading Hand - N/A
label | Supervisor - W - UCCL Supervisor or Project Engineer
label | Third Party (state) - R - Civil Inspector
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 5. Trial of stud welding at Channel Workshop and weld visual Inspection
label | Applicable Documents - INVIL methodology to weld studs AWS D1.1
label | Acceptance Criteria - Studs shall exhibit full 360° flash with no evidence of undercut into the stud base
label | Third Party (state) - H - Welding Inspector
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 6. Bent Test on 1st two studs by each welder. In addition to visual examination, the test shall consist of bending the studs after they are allowed to cool down, to an angle of approximately 30° from either striking the studs with a hammer on the unwelded end or placing a pipe or other suitable device over the stud and manually or mechanically bending the stud
label | Applicable Documents - AWS D1.1
label | Acceptance Criteria - If on visual examination the test studs do not exhibit 360° flash, or if on testing, failure occurs in the weld zone of either stud, the procedure shall be corrected, and two more studs shall be welded to a separate material or on production member
label | Third Party (state) - H - Welding Inspector
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 7. Studs Welded to Tank 04 Annular downturn plate
label | Applicable Documents - Stud manufacturer’s instructions that accompany studs
label | Acceptance Criteria - Welded as per stud manufacturer’s instructions accompanying studs
label | Leading Hand - N/A - Leading Hand
label | Supervisor - W - UCCL Supervisor or Project Engineer
label | Third Party (state) - W - Civil Inspector
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 8. Studs Welded to Tank 06 Annular downturn plate
label | Applicable Documents - Stud manufacturer’s instructions that accompany studs
label | Acceptance Criteria - Welded as per stud manufacturer’s instructions accompanying studs
label | Leading Hand - N/A - Leading Hand
label | Supervisor - W - UCCL Supervisor or Project Engineer
label | Third Party (state) - W - Civil Inspector
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 9. Signoff by Channel Welding Inspector
label | Applicable Documents - CTS Weld visual report
label | Acceptance Criteria - Welding Inspector inspects welds and is happy that welding has happened in accordance with process developed in workshop methodology
label | Third Party (state) - H - Welding Inspector
holdpoint | AUTHORITY HOLDPOINT