## Table 1
Client: AIAL | [8 empty] | Subcontractor: Mckenzie & Parma | [9 empty] | Work Area: Substructure Pier
Project Name: Domestic Jet Terminal | [8 empty] | Job No: HA0423 | [9 empty] | Subcontractor Representative: Chris Beyer
1. ITP Element : Underground Ducts below slab 2. Revision Records
Rev No. |  |  | Revision Description | [12 empty] | Name of Author |  |  |  |  | Authorised by: |  |  | Date
A |  |  | For Approval | [12 empty] | Chris Beyer | [7 empty] | 2025-08-18
1 |  |  | For Construction - Mott Mac-GCOR-002190 | [12 empty] | Chris Beyer | [7 empty] | 2025-09-08
3. Relevant Documents
Doc No. |  |  |  | Specification/ Drwgs/ Standards |  |  |  | Additional Info |  |  |  | Document No. |  |  | Specification/ Drwgs/ Standards | [8 empty] | Additional Info
1 |  |  |  | Mott Macdonald Containment Layout Zone Drawings |  |  |  | Zones 50 to 55 and 60 to 68 |  |  |  | 6
2 |  |  |  | DP001-MMD-SPC-EL-Z-Z-0001 |  |  |  | Domestic Processor – Buildings Electrical Specification |  |  |  | 7
3 |  |  |  | DP001-MMD-SPC-CV-Z-Z-0001 |  |  |  | Section 12 |  |  |  | 8
4 | [11 empty] | 9
5
4. Process
No. |  | Description Inspection / test |  |  |  | Frequency | Spec/standard |  |  | Acceptance Criteria |  |  | Measuring Devices |  |  |  | Reporting Format | Inspected by* |  |  |  |  | Hold Points Sign off |  | Remarks
[18 empty] | HCL |  | SC |  | Consult
1 |  | Delivery inspection of ducts and fittings |  |  |  | Each delivery | AS/NZS 4130 / Manufacturer CoC 7.3.3.3 12.3.3, 12,3.4 |  |  | Correct SDR, diameter and undamaged |  |  | Visual and CoC |  |  |  | Delivery slip / CoC | R. |  | Sub |  | R | N/A |  | Material CoC matches spec; no damage No damaged packing material.
2 |  | Welder qualification check |  |  |  | Before work start | NZ Certifications; standards and industry training |  |  | Accept / reject |  |  | Document review |  |  |  | Welder Qualification | R |  | I |  | R | Hold Point |  | Welder certification reviewed and approved prior works
3 |  | Duct alignment check |  |  |  | Per section | Project drawings / layout 4.23.2 |  |  | Installed as per drawing |  |  | Visual |  |  |  | NA | M |  | I |  | R |  |  | No excessive bends or misalignments
4 |  | Inspection of duct cleanliness and joint |  |  |  | Before welding | ISO 13954 5.10.3 |  |  | Ends scraped, dry, and clean |  |  | Visual |  |  |  | Quality check sheet | M |  | I |  | R |  |  | Free of debris, scratches, moisture
5 |  | Fusion setup – pipe end scraping, machine check |  |  |  | Each weld | ISO 13954 / ISO 13955 |  |  | Scraping complete, scan barcode |  |  | Scraper / EF machine |  |  |  | Quality check sheet | M |  | M |  | R |  |  | Pre-weld approved by supervisor before fusion
6 |  | Electrofusion weld execution |  |  |  | Each weld | ISO 13955 12.4.6. 12.5.2 |  |  | Parameters met; uniform bead |  |  | EF machine logger |  |  |  | Fusion log / Quality check sheet | M |  | Sub |  | R |  |  | Fusion data logged. Weld number time and date next to weld.
7 |  | Post Weld visual inspection and cooling |  |  |  | Each weld | ISO 13955 / 13956 |  |  | Cooled per spec |  |  | Visual |  |  |  | Quality check sheet | s |  | R Sub |  | R |  |  | Cooling time respected; weld integrity confirmed.
8 |  | Weld traceability and documentation |  |  |  | Each weld | 7.3.4.9 |  |  | Barcode and weld ID logged |  |  | Log Sheet |  |  |  | Quality Check sheet | S |  | Sub |  | R |  |  | Log completed and ID matched field location
9 |  | Post Weld inspection |  |  |  | Project Scope | DP001-MMD-SPC- EL-Z-Z-001 12.5.2 |  |  | CCTV footage of below ground ducting, duct contains no debris or penetrations that could damage cable sheath when pulled |  |  | CCTV |  |  |  | Video | S |  | Sub |  | R |  |  | Submission of CCTV footage before handover
10 |  | Electro fusion welder calibration |  |  |  | Project Scope | As per manufactures specification |  |  | Electro fusion welder calibration certificate |  |  | Calibration certificate |  |  |  | Certificate | S |  | Sub |  | R |  |  | Aconex Field Issue 1262
11 |  | Draw Cord |  |  |  | Each conduit | 2012-03-08 |  |  | 5 kN |  |  | N/A |  |  |  | QC checklist/ photograph | M |  | Sub |  | R
12 |  | Installation of tracer wire |  |  |  | Each installed duct | DP001-MMD-SPC- EL-Z-Z-0017.3.3.11 |  |  | Wire securely fixed on top of duct, continuous, accessible at both ends | [6 empty] | QC checklist Photograph | M |  | T |  | R |  |  | Tracer wire to be installed above duct, secured at 3m intervals. Ends terminated in accessible pits or boxes
13 |  | Pit to Duct Jointing Process |  |  |  | Each duct at each pit | DP001-MMD-SPC- EL-Z-Z-0017.3.3.12 |  |  | Manufacturer’s installation guidelines and project specifications |  |  | Secure, watertight connection between duct and pit; no gaps or misalignment |  |  |  | Visual check, QA checklist / photograph | S |  | R |  | S
5. Document Deliverables (The documents listed below shall be completed and compiled during the course of the construction)
Delivery Slip / Certificate of Conformance (CoC) For delivery inspection of HDPE ducts and fittings. | [13 empty] | Calibration Certificates For electrofusion welder calibration.
Welder qualification checks. | [13 empty] | Log Sheets For weld traceability and documentation.
CCTV Footage For post-weld inspection.
QA Reports For duct alignment checks.
6. Distribution Records
| Name |  |  |  | Position | [5 empty] | Company | [14 empty] | Date
| TBA | [9 empty] | Mott McDonalds
| TBA HAWKINS Inspection and Test Plan ¦ | [9 empty] | BECA | [14 empty] | Page 4 of 4
| TBA | [9 empty] | AIAL
 Inspect (I) – To visually examine or measure an item or contracted work operation to verify its conformance to predetermined quality requirements  Review (R) – To examine any form of documentation to establish its acceptability against specified requirements  Surveillance (S) – To observe in-process activities to the degree necessary to be assured that they comply with the established criteria  Test (T) – To subject a component, structure, or system to a controlled set of physical, chemical, environmental or operational conditions to determine or verify its capability to meet specified requirements  Witness (W) – To watch over, observe or visually examine a specific work operation or test performed by others under Contractor supervision  Monitor (M) – General oversight of work in progress with no need to document formally.  Submission (Sub) – Submission of a document
HAWKINS Inspection and Test Plan ¦ Page 5 of 4