## res
type | name | values | prefix | postfix | usage count | user addable | template name | Resource Id
checklist | ITP - Ngawha | itp |  |  |  |  | ITP - Ngawha Rev 1
section | Materials
checkpoint | Concrete
label | SPECIFICATION REFERENCE: All concrete to be 30 mpa Grade
label | TASK TIMING OR TASK FREQUENCY: Prior to Placement
label | UCCL: R, S
label | Client: R, W, A
checkpoint | Backfill Material
label | SPECIFICATION REFERENCE: Geotechnical Spec (Site Material)
label | TEST REQUIRED: Visual Check
label | TASK TIMING OR TASK FREQUENCY: Prior to Placement
label | ACCEPTANCE CRITERIA: Free from Organic Material, Meets Grading
label | UCCL: R, S
label | Client: R, W, A
checkpoint | Compact
label | TASK TIMING OR TASK FREQUENCY: Prior to Placement
label | UCCL: R, S
label | Client: R, W, A
section | Pre Construction Site works
checkpoint | Layer Placement
label | SPECIFICATION REFERENCE: Project Specification
label | TEST REQUIRED: Visual Check
label | INSPECTION BY: UCCL
label | TASK TIMING OR TASK FREQUENCY: Each Layer
label | ACCEPTANCE CRITERIA: Max 200-300 Loose Layer
label | UCCL: R, S
label | Client: R, W, A
checkpoint | Compaction Testing
label | SPECIFICATION REFERENCE: NZS 4431/ ASTM D1557
label | TEST REQUIRED: Visual Check, Scala test
label | INSPECTION BY: UCCL
label | TASK TIMING OR TASK FREQUENCY: Once desired layer is Achived
label | ACCEPTANCE CRITERIA: 100 kpa Compaction Grade
label | UCCL: R, S
label | Client: R, W, A
checkpoint | Backfill Around Structures
label | SPECIFICATION REFERENCE: Drawings
label | TEST REQUIRED: Visual Check
label | INSPECTION BY: UCCL
label | TASK TIMING OR TASK FREQUENCY: During Works
label | ACCEPTANCE CRITERIA: No voids, Hand compact Near structures
label | UCCL: R, S
label | Client: R, W, A
checkpoint | Pipe support Foundations: PS-02, 03, 04, 07, 08, 10, 11, 17, 22, 24 — (1)
label | SPECIFICATION REFERENCE: 22-30-M-005 (Location)
label | TEST REQUIRED: Visual Check
label | INSPECTION BY: UCCL
label | TASK TIMING OR TASK FREQUENCY: Prior to Concrete Placement
label | ACCEPTANCE CRITERIA: Engineers Approval
label | UCCL: R, S
label | Client: R, W, A
checkpoint | Pipe support Foundations: PS-02, 03, 04, 07, 08, 10, 11, 17, 22, 24 — (2)
label | SPECIFICATION REFERENCE: 22-30-M-006 (Description)
label | TEST REQUIRED: Visual Check
label | INSPECTION BY: UCCL
label | TASK TIMING OR TASK FREQUENCY: Prior to works Comencing, Each Support
label | ACCEPTANCE CRITERIA: Engineers Approval
label | UCCL: R, S
label | Client: R, W, A
checkpoint | Pipe support Foundations: PS-02, 03, 04, 07, 08, 10, 11, 17, 22, 24 — (3)
label | SPECIFICATION REFERENCE: 22-30-S-021 (Spec)
label | TEST REQUIRED: Visual Check
label | INSPECTION BY: UCCL
label | TASK TIMING OR TASK FREQUENCY: Prior to works Comencing, Each Support
label | ACCEPTANCE CRITERIA: Engineers Approval
label | UCCL: R, S
label | Client: R, W, A
checkpoint | PS: Concrete - Procurement
label | SPECIFICATION REFERENCE: 22-30-S-021 (Spec)
label | TEST REQUIRED: Concrete mix design
label | INSPECTION BY: UCCL
label | TASK TIMING OR TASK FREQUENCY: Following Award
label | ACCEPTANCE CRITERIA: Engineers Approval
label | UCCL: W
label | Client: R, A
checkpoint | PS: Reinforcing - Placement
label | SPECIFICATION REFERENCE: DRW No. SPEC 02.
label | TEST REQUIRED: Engineers inspection
label | INSPECTION BY: UCCL
label | TASK TIMING OR TASK FREQUENCY: Prior to Concrete Placement
label | ACCEPTANCE CRITERIA: Engineers Approval
label | UCCL: R, S
label | Client: R, A, V
checkpoint | Pipe support Foundations: PS-18, 19, 20, 21 — (1)
label | SPECIFICATION REFERENCE: 22-30-M-005 (Location)
label | TEST REQUIRED: Visual Check
label | INSPECTION BY: UCCL
label | TASK TIMING OR TASK FREQUENCY: Prior to Concrete Placement
label | ACCEPTANCE CRITERIA: Engineers Approval
label | UCCL: R, S
label | Client: R, W, A
checkpoint | Pipe support Foundations: PS-18, 19, 20, 21 — (2)
label | SPECIFICATION REFERENCE: 22-30-M-006 (Description)
label | TEST REQUIRED: Visual Check
label | INSPECTION BY: UCCL
label | TASK TIMING OR TASK FREQUENCY: Prior to works Comencing, Each Support
label | ACCEPTANCE CRITERIA: Engineers Approval
label | UCCL: R, S
label | Client: R, W, A
checkpoint | Pipe support Foundations: PS-18, 19, 20, 21 — (3)
label | SPECIFICATION REFERENCE: 22-30-S-021 (Spec)
label | TEST REQUIRED: Visual Check
label | INSPECTION BY: UCCL
label | TASK TIMING OR TASK FREQUENCY: Prior to works Comencing, Each Support
label | ACCEPTANCE CRITERIA: Engineers Approval
label | UCCL: R, S
label | Client: R, W, A
checkpoint | PS: Concrete - Procurement
label | SPECIFICATION REFERENCE: 22-30-S-021 (Spec)
label | TEST REQUIRED: Concrete mix design
label | INSPECTION BY: UCCL
label | TASK TIMING OR TASK FREQUENCY: Following Award
label | ACCEPTANCE CRITERIA: Engineers Approval
label | UCCL: W
label | Client: R, A
checkpoint | PS: Reinforcing - Placement
label | SPECIFICATION REFERENCE: DRW No. SPEC 02.
label | TEST REQUIRED: Engineers inspection
label | INSPECTION BY: UCCL
label | TASK TIMING OR TASK FREQUENCY: Prior to Concrete Placement
label | ACCEPTANCE CRITERIA: Engineers Approval
label | UCCL: R, S
label | Client: R, A, V
checkpoint | Pipe support Foundations: PG-01, 02, 03, 05, 06 — (1)
label | SPECIFICATION REFERENCE: 22-30-M-002 (Location)
label | TEST REQUIRED: Visual Check
label | INSPECTION BY: UCCL
label | TASK TIMING OR TASK FREQUENCY: Prior to Concrete Placement
label | ACCEPTANCE CRITERIA: Engineers Approval
label | UCCL: R, S
label | Client: R, W, A
checkpoint | Pipe support Foundations: PG-01, 02, 03, 05, 06 — (2)
label | SPECIFICATION REFERENCE: 22-30-M-003 (Description)
label | TEST REQUIRED: Visual Check
label | INSPECTION BY: UCCL
label | TASK TIMING OR TASK FREQUENCY: Prior to works Comencing, Each Support
label | ACCEPTANCE CRITERIA: Engineers Approval
label | UCCL: R, S
label | Client: R, W, A
checkpoint | Pipe support Foundations: PG-01, 02, 03, 05, 06 — (3)
label | SPECIFICATION REFERENCE: 22-30-C-020 (Spec)
label | TEST REQUIRED: Visual Check
label | INSPECTION BY: UCCL
label | TASK TIMING OR TASK FREQUENCY: Prior to works Comencing, Each Support
label | ACCEPTANCE CRITERIA: Engineers Approval
label | UCCL: R, S
label | Client: R, W, A
checkpoint | PG: Concrete - Procurement
label | SPECIFICATION REFERENCE: 22-30-C-020 (Spec)
label | TEST REQUIRED: Concrete mix design
label | INSPECTION BY: UCCL
label | TASK TIMING OR TASK FREQUENCY: Following Award
label | ACCEPTANCE CRITERIA: Engineers Approval
label | UCCL: W
label | Client: R, A
checkpoint | PG: Reinforcing - Placement
label | SPECIFICATION REFERENCE: 22-30-C-020 (Spec)
label | TEST REQUIRED: Engineers inspection
label | INSPECTION BY: UCCL
label | TASK TIMING OR TASK FREQUENCY: Prior to Concrete Placement
label | ACCEPTANCE CRITERIA: Engineers Approval
label | UCCL: R, S
label | Client: R, A, V
checkpoint | Pipe support Foundations: PGL-04, 06, 07 — (1)
label | SPECIFICATION REFERENCE: 22-30-M-002 (Location)
label | TEST REQUIRED: Visual Check
label | INSPECTION BY: UCCL
label | TASK TIMING OR TASK FREQUENCY: Prior to Concrete Placement
label | ACCEPTANCE CRITERIA: Engineers Approval
label | UCCL: R, S
label | Client: R, W, A
checkpoint | Pipe support Foundations: PGL-04, 06, 07 — (2)
label | SPECIFICATION REFERENCE: 22-30-M-003 (Description)
label | TEST REQUIRED: Visual Check
label | INSPECTION BY: UCCL
label | TASK TIMING OR TASK FREQUENCY: Prior to works Comencing, Each Support
label | ACCEPTANCE CRITERIA: Engineers Approval
label | UCCL: R, S
label | Client: R, W, A
checkpoint | Pipe support Foundations: PGL-04, 06, 07 — (3)
label | SPECIFICATION REFERENCE: 22-30-C-020 (Spec)
label | TEST REQUIRED: Visual Check
label | INSPECTION BY: UCCL
label | TASK TIMING OR TASK FREQUENCY: Prior to works Comencing, Each Support
label | ACCEPTANCE CRITERIA: Engineers Approval
label | UCCL: R, S
label | Client: R, W, A
checkpoint | PGL: Concrete - Procurement
label | SPECIFICATION REFERENCE: 22-30-C-020 (Spec)
label | TEST REQUIRED: Concrete mix design
label | INSPECTION BY: UCCL
label | TASK TIMING OR TASK FREQUENCY: Following Award
label | ACCEPTANCE CRITERIA: Engineers Approval
label | UCCL: W
label | Client: R, A
checkpoint | PGL: Reinforcing - Placement
label | SPECIFICATION REFERENCE: 22-30-C-020 (Spec)
label | TEST REQUIRED: Engineers inspection
label | INSPECTION BY: UCCL
label | TASK TIMING OR TASK FREQUENCY: Prior to Concrete Placement
label | ACCEPTANCE CRITERIA: Engineers Approval
label | UCCL: R, S
label | Client: R, A, V
checkpoint | Brine Pump
label | SPECIFICATION REFERENCE: 22-30-C-020 (Dimentions and Location)
label | TEST REQUIRED: Visual Check
label | INSPECTION BY: UCCL
label | TASK TIMING OR TASK FREQUENCY: Prior to works Comencing
label | ACCEPTANCE CRITERIA: Engineers Approval
label | UCCL: R, S
label | Client: R, W, A
checkpoint | BP: Concrete - Procurement
label | SPECIFICATION REFERENCE: 22-30-C-020 (Spec)
label | TEST REQUIRED: Concrete mix design
label | INSPECTION BY: UCCL
label | TASK TIMING OR TASK FREQUENCY: Following Award
label | ACCEPTANCE CRITERIA: Engineers Approval
label | UCCL: W
label | Client: R, A
checkpoint | BP: Reinforcing - Placement
label | SPECIFICATION REFERENCE: 22-30-C-020 (Spec)
label | TEST REQUIRED: Engineers inspection
label | INSPECTION BY: UCCL
label | TASK TIMING OR TASK FREQUENCY: Prior to Concrete Placement
label | ACCEPTANCE CRITERIA: Engineers Approval
label | UCCL: R, S
label | Client: R, A, V
checkpoint | Seal Water — (1)
label | SPECIFICATION REFERENCE: 22-30-M-007 (Location)
label | TEST REQUIRED: Visual Check
label | INSPECTION BY: UCCL
label | TASK TIMING OR TASK FREQUENCY: Prior to Concrete Placement
label | ACCEPTANCE CRITERIA: Engineers Approval
label | UCCL: R, S
label | Client: R, W, A
checkpoint | Seal Water — (2)
label | SPECIFICATION REFERENCE: RFI-CEC Ref: 18830 (Spec)
label | TEST REQUIRED: Visual Check
label | INSPECTION BY: UCCL
label | TASK TIMING OR TASK FREQUENCY: Prior to works Comencing
label | ACCEPTANCE CRITERIA: Engineers Approval
label | UCCL: R, S
label | Client: R, W, A
checkpoint | Seal: Concrete - Procurement
label | SPECIFICATION REFERENCE: RFI-CEC Ref: 18830 (Spec)
label | TEST REQUIRED: Concrete mix design
label | INSPECTION BY: UCCL
label | TASK TIMING OR TASK FREQUENCY: Following Award
label | ACCEPTANCE CRITERIA: Engineers Approval
label | UCCL: W
label | Client: R, A
checkpoint | Seal: Reinforcing - Placement
label | SPECIFICATION REFERENCE: RFI-CEC Ref: 18830 (Spec)
label | TEST REQUIRED: Engineers inspection
label | INSPECTION BY: UCCL
label | TASK TIMING OR TASK FREQUENCY: Prior to Concrete Placement
label | ACCEPTANCE CRITERIA: Engineers Approval
label | UCCL: R, S
label | Client: R, A, V
section | Post Construction
checkpoint | As builts and Redline Markup
label | TEST REQUIRED: Asbuilt file
label | INSPECTION BY: UCCL
label | TASK TIMING OR TASK FREQUENCY: Following completion of construction
label | ACCEPTANCE CRITERIA: As built drawings, redline markups and RAMM sheets
label | UCCL: S
label | Client: A