## Table 1
No. |  | Description Inspection / test |  | Frequency | Spec/standard | Acceptance Criteria |  | Measuring Devices | Reporting Format | Inspected by* |  |  | Hold Points Sign off | Remarks
[10 empty] | HCL | SC | Consult
1 |  | Material Compliance
1.1 |  | Fill Materials
1.1.1 |  | Bedding material PAP 7 for PE pipes AP40 for Chambers |  | Per Batch | CIV Spec - S12.3.4 | Accept/ Reject |  | N/A | Dockets / Material Data Sheets | R | SUB | R | Hold Point | —
1.1.2 |  | Backfill Material GAP65 or TNZ M/4 AP40 |  | Per Batch | CIV Spec - S12.3.5 CIV Spec - S4.4.5 | Accept / Reject |  | N/A | Dockets / Material Data Sheets | R | SUB | R | Hold Point | —
1.2 |  | Pipes
1.2.1 |  | Pipes: 110 OD PE SDR 17 160 OD PE SDR 17 |  | Each Pipe | CIV Spec - S12.3.3 | Accept/Reject |  | N/A | Dockets / Technical Data Sheets | R | SUB | R | Hold Point | All the PE pipe colors must comply with the respective service as mentioned in S12.3.3
1.2.2 |  | Bends: Pre-Fabricated HDPE bends |  | Each Bend | CIV Spec - S12.4.5 | Accept/Reject |  | N/A | Dockets / Technical Data Sheets | R | SUB | R | Hold Point | —
1.2.3 |  | Electrofusion Couplers |  | Each coupler | CIV Spec – S12.4.6 | Accept/Reject |  | N/A | Dockets / Technical Data Sheets | R | SUB | R | Hold Point | —
2 |  | Construction
2.1 |  | Pre-Condition Assessments
2.1.1 |  | Existing ducts/chambers to be removed |  | Each pipe | CIV Spec - S12.4.1 | Removed and disposed |  | N/A | Photos / Asbuilts | I | SUB | R | — | Once removed, all trenches to be backfilled to Subgrade level
2.1.2 |  | Survey Setout Pipe alignments, Position, Heights |  | Each Pipes/trench | CAD Models | Survey Setout Pipe alignments, Position, Manholes Position and Heights |  | GPS, Total Station | Setout CSV file, Photos/Visual | — | — | — | — | Setout model and CSV provided by HCL
2.2 |  | Ducting
2.2.1 |  | Excavation Extents |  | Each element installed | CIV Spec - S12.4.2 CIV Spec - S4.5.9 (earthworks section) | N/A |  | Rotating level and GPS | N/A | M | — | — | Witness Point | —
2.2.2 |  | HDPE Ground Mat |  | Each Unit | Note 10 – DP0001- MMD-DRW-UT-F-Z- 3137 - 3139 | Accept/Reject |  | Photos, Dockets | N/A | I | SUB | R | — | HDPE ground protection Mat will be installed only in areas shown in the drawings. Single layer, 1m for comms, 2m for HV&LV
2.2.3 |  | Bedding, surround |  | Per installation | As per drwgs min/ max fill | N/A |  | Rotating level / tape / staff | Photos, QVC | M | SUB | R | — | PAP7 for PE
2.2.4 |  | Pipe installation, Connection and jointing Electrofusion weld |  | Each pipe | CIV Spec - S12.4.5 CIV Spec - S12.4.6 | N/A |  | Observation | QVC, As-Builts | I | SUB | R | Witness Point | Caps to be used if lines not complete, All Welding to be performed under controlled Environmental conditions.
2.2.5 |  | Weld Testing |  | All welding Joints | CIV Spec - S12.5.2 | N/A |  | Visual Checks for each Weld Peel Decohesion Testing for at least 3 duct weld pieces is recommended | QVC, Photos, Test Results | R | SUB | R | Witness Point | Frequency of testing in line with ISO13954 & ISO13955
2.2.6 |  | Tracer Wires |  | Comms duct | CIV Spec - S12.4.9 DP001-MMD-DRW- UT-F-Z-3137 - 3139 | Tracer Wire to 4mm2 multi-Strand Accept/Reject |  | Continuity Test (electronically generated tone and detector probe) | Photos, Test results, QC | I | SUB | R | — | —
2.2.7 |  | Inspection for Duct size, color, spacing, |  | All ducts | CIV Spec - S12.4.5 DP001-MMD-DRW- UT-F-Z-3137 - 3139 | N/A |  | N/A | Photos, QVC | M | SUB | I | Witness Point AIAL to inspect (Senior ICT Reliability Engineer) | Engineer & AIAL to inspect before backfilling
2.2.8 |  | Warning Tapes/ marker tapes |  | Each Pipe | CIV Spec - S12.3.9 DP001-MMD-DRW- UT-F-Z-3137 - 3139 | Warning Tapes must refer to respective Services. Installation heights must follow the typical trench details. |  | N/A | Photos | I | SUB | R | — | —
2.2.9 |  | Mag Slabs/Polymeric Slabs |  | HV and LV ducts | CIV Spec - S12.3.10 DP001-MMD-DRW- UT-F-Z-3137 - 3139 | Installation heights must follow the typical trench details. |  | N/A | Photos | I | SUB | R | — | —
2010-02-02 |  | Draw Cord |  | Each pipe | CIV Spec - S12.3.8 S12.4.8 DP001-MMD-DRW- UT-F-Z-3137 - 3139 | Continuous draw cord and excess to be left at the ends of each duct |  | N/A | Photos | I | SUB | R | Hold Point – AIAL to inspect (Senior ICT Reliability Engineer) | —
2011-02-02 |  | Pipe Cover and Backfilling |  | Each Pipe | CIV Spec - S4.4.5 Table 4.3 (Earthworks Section) DP001-MMD-DRW- UT-F-Z-3137 - 3139 | Backfilling CIV > 25 |  | Clegg Hammer | Photos, QVC, Clegg Sheets | M | SUB | I |  | 12.5.2 of the DP Civil Specification only applies to the trench backfill material and does not apply to duct surround material.
3 |  | Post Construction
3.1 |  | As-Builts
3.1.1 |  | As built Works |  | Each pipe | N/A | N/A |  | Surveyor Equipment, Total Station | Certified As- built PDF and DWG file | R | Sub | R | — | —
3.2 |  | Duct Condition
3.2.1 |  | Duct Cleaning and Proving |  | Each Duct | N/A | N/A |  | Brush and Mandrill | Photos/Videos | M | SUB | R | Witness Point | —
5. Document Deliverables (The documents listed below shall be completed and compiled during the course of the construction)
Asbuilts
Testing Results
CCTV
QC Checklist
6. Distribution Records
| Name |  | Position |  |  |  | Company | [7 empty] | Date
| TBA | [5 empty] | Mott McDonalds
| TBA | [5 empty] | BECA
| TBA | [5 empty] | AIAL
Inspect (I) – To visually examine or measure an item or contracted work operation to verify its conformance to predetermined quality requirements  Review (R) – To examine any form of documentation to establish its acceptability against specified requirements  Surveillance (S) – To observe in-process activities to the degree necessary to be assured that they comply with the established criteria  Test (T) – To subject a component, structure, or system to a controlled set of physical, chemical, environmental or operational conditions to determine or verify its capability to meet specified requirements  Witness (W) – To watch over, observe or visually examine a specific work operation or test performed by others under Contractor supervision  Monitor (M) – General oversight of work in progress with no need to document formally.  Submission (Sub) – Submission of a document
Note: The Engineer shall be provided a minimum of two (2) working days’ notice ahead of a requested inspection