## Table 1
No. |  | Description Inspection / test |  | Frequency | Spec/standard | Acceptance Criteria |  | Measuring Devices |  | Reporting Format | Inspected by* |  |  | Hold Points Sign off | Remarks
[11 empty] | HCL | SC | Consult
1 |  | Delivery inspection of ducts and fittings |  | Each delivery | AS/NZS 4130 / Manufacturer CoC 7.3.3.3 12.3.3, 12,3.4 | Correct SDR, diameter and undamaged |  | Visual and CoC |  | Delivery slip / CoC | R. | Sub | R | N/A | Material CoC matches spec; no damage No damaged packing material.
2 |  | Welder qualification check |  | Before work start | NZ Certifications; standards and industry training | Accept / reject |  | Document review |  | Welder Qualification | R | I | R | Hold Point | Welder certification reviewed and approved prior works
3 |  | Duct alignment check |  | Per section | Project drawings / layout 4.23.2 | Installed as per drawing |  | Visual |  | NA | M | I | R | — | No excessive bends or misalignments
4 |  | Inspection of duct cleanliness and joint |  | Before welding | ISO 13954 5.10.3 | Ends scraped, dry, and clean |  | Visual |  | Quality check sheet | M | I | R | — | Free of debris, scratches, moisture
5 |  | Fusion setup – pipe end scraping, machine check |  | Each weld | ISO 13954 / ISO 13955 | Scraping complete, scan barcode |  | Scraper / EF machine |  | Quality check sheet | M | M | R | — | Pre-weld approved by supervisor before fusion
6 |  | Electrofusion weld execution |  | Each weld | ISO 13955 12.4.6. 12.5.2 | Parameters met; uniform bead |  | EF machine logger |  | Fusion log / Quality check sheet | M | Sub | R | — | Fusion data logged. Weld number time and date next to weld.
7 |  | Post Weld visual inspection and cooling |  | Each weld | ISO 13955 / 13956 | Cooled per spec |  | Visual |  | Quality check sheet | s | R Sub | R | — | Cooling time respected; weld integrity confirmed.
8 |  | Weld traceability and documentation |  | Each weld | 7.3.4.9 | Barcode and weld ID logged |  | Log Sheet |  | Quality Check sheet | S | Sub | R | — | Log completed and ID matched field location
9 |  | Post Weld inspection |  | Project Scope | DP001-MMD-SPC- EL-Z-Z-001 12.5.2 | CCTV footage of below ground ducting, duct contains no debris or penetrations that could damage cable sheath when pulled |  | CCTV |  | Video | S | Sub | R | — | Submission of CCTV footage before handover
10 |  | Electro fusion welder calibration |  | Project Scope | As per manufactures specification | Electro fusion welder calibration certificate |  | Calibration certificate |  | Certificate | S | Sub | R | — | Aconex Field Issue 1262
11 |  | Draw Cord |  | Each conduit | 2012-03-08 | 5 kN |  | N/A |  | QC checklist/ photograph | M | Sub | R | — | —
12 |  | Installation of tracer wire |  | Each installed duct | DP001-MMD-SPC- EL-Z-Z-0017.3.3.11 | Wire securely fixed on top of duct, continuous, accessible at both ends |  |  |  | QC checklist Photograph | M | T | R | — | Tracer wire to be installed above duct, secured at 3m intervals. Ends terminated in accessible pits or boxes
13 |  | Pit to Duct Jointing Process |  | Each duct at each pit | DP001-MMD-SPC- EL-Z-Z-0017.3.3.12 | Manufacturer’s installation guidelines and project specifications |  | Secure, watertight connection between duct and pit; no gaps or misalignment |  | Visual check, QA checklist / photograph | S | R | S | — | —
5. Document Deliverables (The documents listed below shall be completed and compiled during the course of the construction)
Delivery Slip / Certificate of Conformance (CoC) For delivery inspection of HDPE ducts and fittings. | [8 empty] | Calibration Certificates For electrofusion welder calibration.
Welder qualification checks. | [8 empty] | Log Sheets For weld traceability and documentation.
CCTV Footage For post-weld inspection.
QA Reports For duct alignment checks.
6. Distribution Records
| Name |  | Position |  |  |  | Company | [8 empty] | Date
| TBA | [5 empty] | Mott McDonalds
| TBA HAWKINS Inspection and Test Plan ¦ | [5 empty] | BECA | [8 empty] | Page 4 of 4
| TBA | [5 empty] | AIAL
 Inspect (I) – To visually examine or measure an item or contracted work operation to verify its conformance to predetermined quality requirements  Review (R) – To examine any form of documentation to establish its acceptability against specified requirements  Surveillance (S) – To observe in-process activities to the degree necessary to be assured that they comply with the established criteria  Test (T) – To subject a component, structure, or system to a controlled set of physical, chemical, environmental or operational conditions to determine or verify its capability to meet specified requirements  Witness (W) – To watch over, observe or visually examine a specific work operation or test performed by others under Contractor supervision  Monitor (M) – General oversight of work in progress with no need to document formally.  Submission (Sub) – Submission of a document
HAWKINS Inspection and Test Plan ¦ Page 5 of 4