## res
type | name | values | prefix | postfix | usage count | user addable | template name | Resource Id
checklist | ITP-CIV-008-1 - Utilities Chambers | itp
section | 1 - Material Compliance (1.1 - Fill Materials)
checkpoint | 1.1.1 - Bedding and Backfill GAP65 or AP40
label | Frequency - Per Batch
label | Spec/standard - CIV Spec - S12.3.5 DP001-MMD-DRW-UT-B-Z-3100-3117
label | Acceptance Criteria - Accept/Reject
label | Measuring Devices - N/A
label | Reporting Format - Dockets / Material Data Sheets
label | HCL - R
label | SC - SUB
label | Consult - R
label | Hold Points Sign off - Hold Point
holdpoint | HOLD POINT
section | 1 - Material Compliance (1.2 - Pits/Chamber)
checkpoint | 1.2.1 - PCC Risers/Chambers With HN-HO-72 Load Bearing Capacity
label | Frequency - Each Unit
label | Spec/standard - CIV Spec - S12.3.3
label | Acceptance Criteria - Accept/Reject
label | Measuring Devices - N/A
label | Reporting Format - Dockets / Material Data Sheets
label | HCL - R
label | SC - SUB
label | Consult - R
label | Hold Points Sign off - Hold Point
holdpoint | HOLD POINT
checkpoint | 1.2.2 - Access covers and frames Landside: 240 kN Class D Airside: 900 kN Class G
label | Frequency - Each unit
label | Spec/standard - CIV Spec - S9.3.8
label | Acceptance Criteria - Shop drawings, Dockets/ Visual Checks
label | Measuring Devices - N/A
label | Reporting Format - Dockets / Technical Data Sheets
label | HCL - R
label | SC - SUB
label | Consult - R
label | Hold Points Sign off - Hold Point
holdpoint | HOLD POINT
section | 1 - Material Compliance (1.3 - Concrete Mix)
checkpoint | 1.3.1 - Standard Concrete Mix
label | Frequency - Each Structure
label | Spec/standard - CIV Spec - S13.3.1.1
label | Acceptance Criteria - Accept/Reject
label | Measuring Devices - N/A
label | Reporting Format - Design Mix
label | HCL - R
label | SC - SUB
label | Consult - R
label | Hold Points Sign off - Hold Point
holdpoint | HOLD POINT
section | 1 - Material Compliance (1.4 - Reinforcement)
checkpoint | 1.4.1 - Reinforcement Bending Schedules
label | Frequency - Each Structure
label | Spec/standard - CIV Spec - S14.3.1
label | Acceptance Criteria - Accept/Reject
label | Measuring Devices - N/A
label | Reporting Format - Dockets / Technical Data Sheets
label | HCL - R
label | SC - SUB
label | Consult - R
label | Hold Points Sign off - Hold Point
holdpoint | HOLD POINT
checkpoint | 1.4.2 - Bending Schedules
label | Frequency - Each Structure
label | Spec/standard - CIV Spec - S14.4.6
label | Acceptance Criteria - Accept/Reject
label | Measuring Devices - N/A
label | Reporting Format - Dockets / Technical Data Sheets
label | HCL - R
label | SC - SUB
label | Consult - R
label | Hold Points Sign off - Hold Point
holdpoint | HOLD POINT
section | 1 - Material Compliance (1.5 - Waterproofing)
checkpoint | 1.5.1 - Pipe & Pit Waterproofing – Hydrotite CJ 0725 3K or Similar
label | Frequency - Each Pipe and Structure
label | Spec/standard - DP001-MMD-DRW- UT-B-Z-3100-3117
label | Acceptance Criteria - Accept/Reject
label | Measuring Devices - N/A
label | Reporting Format - Dockets/ Technical Data Sheets
label | HCL - R
label | SC - SUB
label | Consult - R
section | 2 - Construction (2.1 - Pre-Condition Assessments)
checkpoint | 2.1.1 - Survey Setout Chambers/Pits Position and Heights
label | Frequency - Each Manhole
label | Spec/standard - N/A
label | Acceptance Criteria - Survey Setout records and Setout pegs, Plans
label | Measuring Devices - GPS, Total Station
label | Reporting Format - Setout CSV file, QC Checklist
label | Remarks - Coordinates mentioned in plans
section | 2 - Construction (2.2 - Cast In-Situ Chamber Construction)
checkpoint | 2.2.1 - Excavation Extents
label | Frequency - Each element installed
label | Spec/standard - CIV Spec - S13.4.1 CIV Spec - S4.5.9 (earthworks section)
label | Acceptance Criteria - N/A
label | Measuring Devices - Rotating level and GPS
label | Reporting Format - N/A
label | HCL - M
checkpoint | 2.2.2 - Chambers/Pits subgrade testing
label | Frequency - Utility Access Chambers: 2 tests at the base of excavation
label | Spec/standard - CIV Spec - S4.6.2.2 (earthworks section)
label | Acceptance Criteria - Bearing Capacity as mentioned in the drawings
label | ○ For cohesive soil Shear Vane Test at EGL (0.0m), 0.5m and 1.0m depths
label | ○ For non-cohesive soil scala test to 1m depth. Inspection required by engineer for acceptance
label | Measuring Devices - Shear Vane, Scala Penetrometer
label | Reporting Format - QC Checklist, Visual Checks, Excel & pdf
label | HCL - M
label | SC - SUB
label | Consult - W
label | Hold Points Sign off - Witness Point
label | Remarks - If ground failing, Engineer to advise MM will attend all witness points
checkpoint | 2.2.3 - 200mm thick 20MPa concrete bedding
label | Frequency - Each structure
label | Spec/standard - DP001-MMD-DRW- UT-B-Z-3100-3117
label | Acceptance Criteria - Accept/Reject, 20MPa Concrete
label | Measuring Devices - N/A
label | Reporting Format - QC Checklist, Dockets
label | HCL - M
label | SC - SUB
label | Consult - R
checkpoint | 2.2.4 - Formwork
label | Frequency - Each Structure
label | Spec/standard - CIV Spec - S13.4.2
label | Acceptance Criteria - Accept/Reject Dimension Accuracy, Alignment and position
label | Measuring Devices - GPS/ Total Station/ Rotating Laser
label | Reporting Format - QC Checklist, As-Built drawings to confirm the tolerances
label | HCL - M
label | SC - SUB
label | Consult - I
label | Remarks - Engineer inspection will be done along with the reinforcement
checkpoint | 2.2.5 - Reinforcement Laps
label | Frequency - Each unit
label | Spec/standard - CIV Spec - S14.4.7 DP001-MMD-DRW-CS-B-Z-3013
label | Acceptance Criteria - Accept/Reject
label | Measuring Devices - N/A
label | Reporting Format - QC Checklist, Visual Checks
label | HCL - M/I
label | SC - SUB
label | Remarks - Reinforcement Laps to be followed as shown in the plans
checkpoint | 2.2.6 - Reinforcement fixing and spacing
label | Frequency - Each Structure
label | Spec/standard - CIV Spec - S14.4.8
label | Acceptance Criteria - Accept/Reject
label | Measuring Devices - N/A
label | Reporting Format - QC Checklist, Visual Checks
label | HCL - M/I
label | SC - SUB
label | Consult - I
checkpoint | 2.2.7 - Concrete Cover/Spacer blocks
label | Frequency - Each Structure
label | Spec/standard - CIV Spec - S14.4.8 CIV Spec - S14.4.11 Shop Drawings
label | Acceptance Criteria - Min 50mm unless noted on plans
label | Measuring Devices - N/A
label | Reporting Format - QC Checklist, Visual Checks
label | HCL - M/I
label | SC - SUB
label | Consult - I
checkpoint | 2.2.8 - Duct Penetrations and Water proofing
label | Frequency - Each Duct
label | Spec/standard - Plans and Shop Drawings
label | Acceptance Criteria - Penetration reinforcement installed as shown on the drawings, Hydrotite CJ 0725 3K wrapped around the duct
label | Measuring Devices - N/A
label | Reporting Format - Pre-Pour QC Checklist
label | HCL - M/I
label | SC - SUB
label | Consult - R
label | Remarks - Refer to drawings, shop drawings and plans
checkpoint | 2.2.9 - Inspection of Reinforcement steel and Formwork
label | Frequency - Each Structure
label | Spec/standard - CIV Spec - S13.4.2
label | Acceptance Criteria - Accept/Reject Hydrotite CJ 0725 3K installed in construction joints as per drawings
label | Measuring Devices - N/A
label | Reporting Format - QC Checklist, Visual Checks
label | HCL - R
label | SC - SUB
label | Consult - I
label | Hold Points Sign off - Hold point
label | Remarks - Back formwork shall not be placed until the Engineer Inspection is completed.
holdpoint | HOLD POINT
checkpoint | 2.2.2010 - Concrete Placement
label | Frequency - Each Structure
label | Spec/standard - CIV Spec - S13.4.3.1
label | Acceptance Criteria - Mix Design Docket
label | Measuring Devices - N/A
label | Reporting Format - Dockets, Pre- Pour QC Checklist
label | HCL - M
label | SC - SUB
label | Consult - R
label | Remarks - Pumping concrete to be done with prior approval.
checkpoint | 2.2.2011 - Concrete Finish
label | Frequency - Each Structure
label | Spec/standard - CIV Spec - S13.4.5
label | Acceptance Criteria - Formed Structure:
label | ○ Below Ground: F1
label | ○ With Tanking: F4
label | Unformed Structures:
label | ○ Buried Foundations: U1
label | ○ Exposed Foundations: U5
label | Measuring Devices - N/A
label | Reporting Format - QC Checklist, Visual Checks
label | HCL - M
label | SC - SUB
label | Consult - R
checkpoint | 2.2.2012 - Concrete Testing Slump Test 4x Concrete Cylinder tests
label | Frequency - Each Batch
label | Spec/standard - CIV Spec - S13.5.3.2
label | Acceptance Criteria - 1x Test results at 7 days
label | ○ 3x test results at 28 day
label | ○ Slump test during the concrete pour
label | Measuring Devices - N/A
label | Reporting Format - Test Results, QC Checklist
label | HCL - R/M
label | SC - SUB
label | Consult - R
checkpoint | 2.2.2013 - Grout Testing
label | Frequency - Each Batch
label | Spec/standard - CIV Spec - S13.5.3.3
label | Acceptance Criteria - Test at 28 days
label | Measuring Devices - N/A
label | Reporting Format - Test Results
label | HCL - R/M
label | SC - SUB
label | Consult - R
section | 2 - Construction (2.3 - Mass Concrete Chambers)
checkpoint | 2.3.1 - Formwork
label | Frequency - Each Structure
label | Spec/standard - CIV Spec - S13.4.2 CIV Spec - S13.4.3.2
label | Acceptance Criteria - Accept/Reject Dimension Accuracy, Alignment and position
label | Measuring Devices - GPS/ Total Station/ Rotating Laser
label | Reporting Format - QC Checklist, Visual Checks
label | HCL - M
label | SC - SUB
label | Consult - I
label | Hold Points Sign off - Hold Point
holdpoint | HOLD POINT
checkpoint | 2.3.2 - Concrete Placement
label | Frequency - Each Structure
label | Spec/standard - CIV Spec - S13.4.3.2
label | Acceptance Criteria - 20MPa Concrete
label | Measuring Devices - N/A
label | Reporting Format - Dockets, Pre- Pour QA Checklist
label | HCL - M
label | SC - SUB
label | Consult - R
checkpoint | 2.3.3 - Duct Penetrations and Water proofing
label | Frequency - Each Duct
label | Spec/standard - Plans and Shop Drawings
label | Acceptance Criteria - As shown on the drawings, Hydrotite CJ 0725 3K wrapped around the pipe
label | Measuring Devices - N/A
label | Reporting Format - Pre-Pour QA Checklist
label | HCL - M/I
label | SC - SUB
label | Consult - R
label | Remarks - Refer to Shop drawings and Plans
checkpoint | 2.3.4 - Curing
label | Frequency - Each structure
label | Spec/standard - CIV Spec - S13.4.3.6
label | Acceptance Criteria - A1/A2 Environment: 3 Days
label | ○ B1/B2 Environment: 7 Days
label | Measuring Devices - N/A
label | Reporting Format - QC Checklist
label | HCL - M
label | SC - SUB
label | Consult - R
checkpoint | 2.3.5 - Grouting of Ducts and Voids
label | Frequency - Each Duct and Each Structure
label | Spec/standard - CIV Spec - S13.4.3.7
label | Acceptance Criteria - All voids, and gaps of duct penetrations
label | Measuring Devices - N/A
label | Reporting Format - QC Checklist
label | HCL - M
label | SC - SUB
label | Consult - I
checkpoint | 2.3.6 - Backfilling GAP65 or AP40
label | Frequency - Each Structure
label | Spec/standard - CIV Spec - S13.4.4 Table 4.3 (Earthworks Section)
label | Acceptance Criteria - CIV > 25 Clegg Test corelated to an NDM
label | Measuring Devices - Clegg Hammer
label | Reporting Format - QC Checklist, QVC, Clegg Sheets
label | HCL - M
label | SC - SUB
label | Consult - R
label | Hold Points Sign off - Witness Point
label | Remarks - Engineer to inspect before backfilling
checkpoint | 2.3.7 - Concrete Finish
label | Frequency - Each Structure
label | Spec/standard - CIV Spec - S13.4.5
label | Acceptance Criteria - Formed Structure:
label | ○ Below Ground: F1
label | ○ With Tanking: F4
label | Unformed Structures:
label | ○ Buried Foundations: U1
label | ○ Exposed Foundations: U5
label | Measuring Devices - N/A
label | Reporting Format - QC Checklist, Visual Checks
label | HCL - M
label | SC - SUB
label | Consult - R
checkpoint | 2.3.8 - Concrete Testing Slump Test 4x Concrete Cylinder tests
label | Frequency - Each Batch
label | Spec/standard - CIV Spec - S13.5.3.2
label | Acceptance Criteria - 1x Test results at 7 days
label | ○ 3x test results at 28 day
label | ○ Slump test during the concrete pour
label | Measuring Devices - N/A
label | Reporting Format - Test Results, QC Checklist
label | HCL - R/M
label | SC - SUB
label | Consult - R
checkpoint | 2.3.9 - Grout Testing
label | Frequency - Each Batch
label | Spec/standard - CIV Spec - S13.5.3.3
label | Acceptance Criteria - Test at 28 days
label | Measuring Devices - N/A
label | Reporting Format - Test Results
label | HCL - R/M
label | SC - SUB
label | Consult - R
section | 3 - Post Construction
checkpoint | 3.1 - As built Works
label | Frequency - Each Chamber
label | Spec/standard - CIV Spec - S12.4.10 CIV Spec - S13.4.7
label | Acceptance Criteria - Position tolerance +/- 20mm
label | ○ Level Tolerance 0mm to +3mm
label | Measuring Devices - Surveyor Equipment, Total Station
label | Reporting Format - Certified As- built PDF and DWG file
label | HCL - R
label | SC - SUB
label | Consult - R
checkpoint-no-status | Document Deliverables
label | (The documents listed below shall be completed and compiled during the course of the construction)
label | ○ Results of Compactions
label | ○ Material Certificates
label | ○ QC records
label | ○ EPD Certificate if applicable
label | ○ As Built
checkpoint | Distribution Records
signoff | Signoff
checklist | ITP-CIV-007-2 - Utilities Ducting | itp
section | 1 - Material Compliance (1.1 - Fill Materials)
checkpoint | 1.1.1 - Bedding material PAP 7 for PE pipes AP40 for Chambers
label | Frequency - Per Batch
label | Spec/standard - CIV Spec - S12.3.4
label | Acceptance Criteria - Accept/ Reject
label | Measuring Devices - N/A
label | Reporting Format - Dockets / Material Data Sheets
label | HCL - R
label | SC - SUB
label | Consult - R
label | Hold Points Sign off - Hold Point
holdpoint | HOLD POINT
checkpoint | 1.1.2 - Backfill Material GAP65 or TNZ M/4 AP40
label | Frequency - Per Batch
label | Spec/standard - CIV Spec - S12.3.5 CIV Spec - S4.4.5
label | Acceptance Criteria - Accept / Reject
label | Measuring Devices - N/A
label | Reporting Format - Dockets / Material Data Sheets
label | HCL - R
label | SC - SUB
label | Consult - R
label | Hold Points Sign off - Hold Point
holdpoint | HOLD POINT
section | 1 - Material Compliance (1.2 - Pipes)
checkpoint | 1.2.1 - Pipes: 110 OD PE SDR 17, 160 OD PE SDR 17
label | Frequency - Each Pipe
label | Spec/standard - CIV Spec - S12.3.3
label | Acceptance Criteria - Accept/Reject
label | Measuring Devices - N/A
label | Reporting Format - Dockets / Technical Data Sheets
label | HCL - R
label | SC - SUB
label | Consult - R
label | Hold Points Sign off - Hold Point
label | Remarks - All the PE pipe colors must comply with the respective service as mentioned in S12.3.3
holdpoint | HOLD POINT
checkpoint | 1.2.2 - Bends: Pre-Fabricated HDPE bends
label | Frequency - Each Bend
label | Spec/standard - CIV Spec - S12.4.5
label | Acceptance Criteria - Accept/Reject
label | Measuring Devices - N/A
label | Reporting Format - Dockets / Technical Data Sheets
label | HCL - R
label | SC - SUB
label | Consult - R
label | Hold Points Sign off - Hold Point
holdpoint | HOLD POINT
checkpoint | 1.2.3 - Electrofusion Couplers
label | Frequency - Each coupler
label | Spec/standard - CIV Spec – S12.4.6
label | Acceptance Criteria - Accept/Reject
label | Measuring Devices - N/A
label | Reporting Format - Dockets / Technical Data Sheets
label | HCL - R
label | SC - SUB
label | Consult - R
label | Hold Points Sign off - Hold Point
holdpoint | HOLD POINT
section | 2 - Construction (2.1 - Pre-Condition Assessments)
checkpoint | 2.1.1 - Existing ducts/chambers to be removed
label | Frequency - Each pipe
label | Spec/standard - CIV Spec - S12.4.1
label | Acceptance Criteria - Removed and disposed
label | Measuring Devices - N/A
label | Reporting Format - Photos / Asbuilts
label | HCL - I
label | SC - SUB
label | Consult - R
label | Remarks - Once removed, all trenches to be backfilled to Subgrade level
checkpoint | 2.1.2 - Survey Setout Pipe alignments, Position, Heights
label | Frequency - Each Pipes/trench
label | Spec/standard - CAD Models
label | Acceptance Criteria - Survey Setout Pipe alignments, Position, Manholes Position and Heights
label | Measuring Devices - GPS, Total Station
label | Reporting Format - Setout CSV file, Photos/Visual
label | Remarks - Setout model and CSV provided by HCL
section | 2 - Construction (2.2 - Ducting)
checkpoint | 2.2.1 - Excavation Extents
label | Frequency - Each element installed
label | Spec/standard - CIV Spec - S12.4.2 CIV Spec - S4.5.9 (earthworks section)
label | Acceptance Criteria - N/A
label | Measuring Devices - Rotating level and GPS
label | Reporting Format - N/A
label | HCL - M
label | Hold Points Sign off - Witness Point
checkpoint | 2.2.2 - HDPE Ground Mat
label | Frequency - Each Unit
label | Spec/standard - Note 10 – DP0001- MMD-DRW-UT-F-Z- 3137 - 3139
label | Acceptance Criteria - Accept/Reject
label | Measuring Devices - Photos, Dockets
label | Reporting Format - N/A
label | HCL - I
label | SC - SUB
label | Consult - R
label | Remarks - HDPE ground protection Mat will be installed only in areas shown in the drawings.
label | ○ Single layer, 1m for comms, 2m for HV&LV
checkpoint | 2.2.3 - Bedding, surround
label | Frequency - Per installation
label | Spec/standard - As per drwgs min/ max fill
label | Acceptance Criteria - N/A
label | Measuring Devices - Rotating level / tape / staff
label | Reporting Format - Photos, QVC
label | HCL - M
label | SC - SUB
label | Consult - R
label | Remarks - PAP7 for PE
checkpoint | 2.2.4 - Pipe installation, Connection and jointing Electrofusion weld
label | Frequency - Each pipe
label | Spec/standard - CIV Spec - S12.4.5 CIV Spec - S12.4.6
label | Acceptance Criteria - N/A
label | Measuring Devices - Observation
label | Reporting Format - QVC, As-Builts
label | HCL - I
label | SC - SUB
label | Consult - R
label | Hold Points Sign off - Witness Point
label | Remarks - Caps to be used if lines not complete, All Welding to be performed under controlled Environmental conditions.
checkpoint | 2.2.5 - Weld Testing
label | Frequency - All welding Joints
label | Spec/standard - CIV Spec - S12.5.2
label | Acceptance Criteria - N/A
label | Measuring Devices - Visual Checks for each Weld
label | ○ Peel Decohesion Testing for at least 3 duct weld pieces is recommended
label | Reporting Format - QVC, Photos, Test Results
label | HCL - R
label | SC - SUB
label | Consult - R
label | Hold Points Sign off - Witness Point
label | Remarks - Frequency of testing in line with ISO13954 & ISO13955
checkpoint | 2.2.6 - Tracer Wires
label | Frequency - Comms duct
label | Spec/standard - CIV Spec - S12.4.9 DP001-MMD-DRW- UT-F-Z-3137 - 3139
label | Acceptance Criteria - Tracer Wire to 4mm2 multi-Strand Accept/Reject
label | Measuring Devices - Continuity Test (electronically generated tone and detector probe)
label | Reporting Format - Photos, Test results, QC
label | HCL - I
label | SC - SUB
label | Consult - R
checkpoint | 2.2.7 - Inspection for Duct size, color, spacing,
label | Frequency - All ducts
label | Spec/standard - CIV Spec - S12.4.5 DP001-MMD-DRW- UT-F-Z-3137 - 3139
label | Acceptance Criteria - N/A
label | Measuring Devices - N/A
label | Reporting Format - Photos, QVC
label | HCL - M
label | SC - SUB
label | Consult - I
label | Hold Points Sign off - Witness Point AIAL to inspect (Senior ICT Reliability Engineer)
label | Remarks - Engineer & AIAL to inspect before backfilling
checkpoint | 2.2.8 - Warning Tapes/ marker tapes
label | Frequency - Each Pipe
label | Spec/standard - CIV Spec - S12.3.9 DP001-MMD-DRW- UT-F-Z-3137 - 3139
label | Acceptance Criteria - Warning Tapes must refer to respective Services. Installation heights must follow the typical trench details.
label | Measuring Devices - N/A
label | Reporting Format - Photos
label | HCL - I
label | SC - SUB
label | Consult - R
checkpoint | 2.2.9 - Mag Slabs/Polymeric Slabs
label | Frequency - HV and LV ducts
label | Spec/standard - CIV Spec - S12.3.10 DP001-MMD-DRW- UT-F-Z-3137 - 3139
label | Acceptance Criteria - Installation heights must follow the typical trench details.
label | Measuring Devices - N/A
label | Reporting Format - Photos
label | HCL - I
label | SC - SUB
label | Consult - R
checkpoint | 2.2.2010 - Draw Cord
label | Frequency - Each pipe
label | Spec/standard - CIV Spec - S12.3.8 S12.4.8, DP001-MMD-DRW- UT-F-Z-3137 - 3139
label | Acceptance Criteria - Continuous draw cord and excess to be left at the ends of each duct
label | Measuring Devices - N/A
label | Reporting Format - Photos
label | HCL - I
label | SC - SUB
label | Consult - R
label | Hold Points Sign off - Hold Point – AIAL to inspect (Senior ICT Reliability Engineer)
holdpoint | HOLD POINT
checkpoint | 2.2.2011 - Pipe Cover and Backfilling
label | Frequency - Each Pipe
label | Spec/standard - CIV Spec - S4.4.5 Table 4.3 (Earthworks Section), DP001-MMD-DRW- UT-F-Z-3137 - 3139
label | Acceptance Criteria - Backfilling CIV > 25
label | Measuring Devices - Clegg Hammer
label | Reporting Format - Photos, QVC, Clegg Sheets
label | HCL - M
label | SC - SUB
label | Consult - I
label | Remarks - 12.5.2 of the DP Civil Specification only applies to the trench backfill material and does not apply to duct surround material.
section | 3 - Post Construction (3.1 - As-Builts)
checkpoint | 3.1.1 - As built Works
label | Frequency - Each pipe
label | Spec/standard - N/A
label | Acceptance Criteria - N/A
label | Measuring Devices - Surveyor Equipment, Total Station
label | Reporting Format - Certified As- built PDF and DWG file
label | HCL - R
label | SC - Sub
label | Consult - R
section | 3 - Post Construction (3.2 - Duct Condition)
checkpoint | 3.2.1 - Duct Cleaning and Proving
label | Frequency - Each Duct
label | Spec/standard - N/A
label | Acceptance Criteria - N/A
label | Measuring Devices - Brush and Mandrill
label | Reporting Format - Photos/Videos
label | HCL - M
label | SC - SUB
label | Consult - R
label | Hold Points Sign off - Witness Point
checkpoint-no-status | Document Deliverables
label | (The documents listed below shall be completed and compiled during the course of the construction)
label | ○ Asbuilts
label | ○ Testing Results
label | ○ CCTV
label | ○ QC Checklist
checkpoint | Distribution Records
signoff | Signoff
checklist | ITP-Ele-005-Rev 1 - Pier Underground Ducts below slab | itp
section | 4 - Process
checkpoint | 01 - Delivery inspection of ducts and fittings
label | Frequency - Each delivery
label | Spec/standard - AS/NZS 4130 / Manufacturer CoC 7.3.3.3, 12.3.3, 12,3.4
label | Acceptance Criteria - Correct SDR, diameter and undamaged
label | Measuring Devices - Visual and CoC
label | Reporting Format - Delivery slip / CoC
label | HCL - R.
label | SC - Sub
label | Consult - R
label | Hold Points Sign off - N/A
label | Remarks - Material CoC matches spec; no damage No damaged packing material.
checkpoint | 02 - Welder qualification check
label | Frequency - Before work start
label | Spec/standard - NZ Certifications; standards and industry training
label | Acceptance Criteria - Accept / reject
label | Measuring Devices - Document review
label | Reporting Format - Welder Qualification
label | HCL - R
label | SC - I
label | Consult - R
label | Hold Points Sign off - Hold Point
label | Remarks - Welder certification reviewed and approved prior works
holdpoint | HOLD POINT
checkpoint | 03 - Duct alignment check
label | Frequency - Per section
label | Spec/standard - Project drawings / layout 4.23.2
label | Acceptance Criteria - Installed as per drawing
label | Measuring Devices - Visual
label | Reporting Format - NA
label | HCL - M
label | SC - I
label | Consult - R
label | Remarks - No excessive bends or misalignments
checkpoint | 04 - Inspection of duct cleanliness and joint
label | Frequency - Before welding
label | Spec/standard - ISO 13954, 5.10.3
label | Acceptance Criteria - Ends scraped, dry, and clean
label | Measuring Devices - Visual
label | Reporting Format - Quality check sheet
label | HCL - M
label | SC - I
label | Consult - R
label | Remarks - Free of debris, scratches, moisture
checkpoint | 05 - Fusion setup – pipe end scraping, machine check
label | Frequency - Each weld
label | Spec/standard - ISO 13954 / ISO 13955
label | Acceptance Criteria - Scraping complete, scan barcode
label | Measuring Devices - Scraper / EF machine
label | Reporting Format - Quality check sheet
label | HCL - M
label | SC - M
label | Consult - R
label | Remarks - Pre-weld approved by supervisor before fusion
checkpoint | 06 - Electrofusion weld execution
label | Frequency - Each weld
label | Spec/standard - ISO 13955, 12.4.6., 12.5.2
label | Acceptance Criteria - Parameters met; uniform bead
label | Measuring Devices - EF machine logger
label | Reporting Format - Fusion log / Quality check sheet
label | HCL - M
label | SC - Sub
label | Consult - R
label | Remarks - Fusion data logged. Weld number time and date next to weld.
checkpoint | 07 - Post Weld visual inspection and cooling
label | Frequency - Each weld
label | Spec/standard - ISO 13955 / 13956
label | Acceptance Criteria - Cooled per spec
label | Measuring Devices - Visual
label | Reporting Format - Quality check sheet
label | HCL - S
label | SC - R, Sub
label | Consult - R
label | Remarks - Cooling time respected; weld integrity confirmed.
checkpoint | 08 - Weld traceability and documentation
label | Frequency - Each weld
label | Spec/standard - 7.3.4.9
label | Acceptance Criteria - Barcode and weld ID logged
label | Measuring Devices - Log Sheet
label | Reporting Format - Quality Check sheet
label | HCL - S
label | SC - Sub
label | Consult - R
label | Remarks - Log completed and ID matched field location
checkpoint | 09 - Post Weld inspection
label | Frequency - Project Scope
label | Spec/standard - DP001-MMD-SPC- EL-Z-Z-001, 12.5.2
label | Acceptance Criteria - CCTV footage of below ground ducting, duct contains no debris or penetrations that could damage cable sheath when pulled
label | Measuring Devices - CCTV
label | Reporting Format - Video
label | HCL - S
label | SC - Sub
label | Consult - R
label | Remarks - Submission of CCTV footage before handover
checkpoint | 10 - Electro fusion welder calibration
label | Frequency - Project Scope
label | Spec/standard - As per manufactures specification
label | Acceptance Criteria - Electro fusion welder calibration certificate
label | Measuring Devices - Calibration certificate
label | Reporting Format - Certificate
label | HCL - S
label | SC - Sub
label | Consult - R
label | Remarks - Aconex Field Issue 1262
checkpoint | 11 - Draw Cord
label | Frequency - Each conduit
label | Spec/standard - 12.3.8
label | Acceptance Criteria - 5 kN
label | Measuring Devices - N/A
label | Reporting Format - QC checklist/ photograph
label | HCL - M
label | SC - Sub
label | Consult - R
checkpoint | 12 - Installation of tracer wire
label | Frequency - Each installed duct
label | Spec/standard - DP001-MMD-SPC- EL-Z-Z-0017.3.3.11
label | Acceptance Criteria - Wire securely fixed on top of duct, continuous, accessible at both ends
label | Measuring Devices -
label | Reporting Format - QC checklist Photograph
label | HCL - M
label | SC - T
label | Consult - R
label | Remarks - Tracer wire to be installed above duct, secured at 3m intervals. Ends terminated in accessible pits or boxes
checkpoint | 13 - Pit to Duct Jointing Process
label | Frequency - Each duct at each pit
label | Spec/standard - DP001-MMD-SPC- EL-Z-Z-0017.3.3.12
label | Acceptance Criteria - Manufacturer’s installation guidelines and project specifications
label | Measuring Devices - Secure, watertight connection between duct and pit; no gaps or misalignment
label | Reporting Format - Visual check, QA checklist / photograph
label | HCL - S
label | SC - R
label | Consult - S
checkpoint-no-status | Document Deliverables
label | (The documents listed below shall be completed and compiled during the course of the construction)
label | ○ Delivery Slip / Certificate of Conformance (CoC) - For delivery inspection of HDPE ducts and fittings.
label | ○ Welder qualification checks.
label | ○ Calibration Certificates - For electrofusion welder calibration.
label | ○ Log Sheets - For weld traceability and documentation.
label | ○ CCTV Footage - For post-weld inspection.
label | ○ QA Reports - For duct alignment checks.
checkpoint | Distribution Records
signoff | Signoff