## Sheet1
ConQA Team Notes:
Document Title: |  | ITP-321-CIV-SSO-Lighting-MTM
ITP Description: |  | SSO-Lighting-MTM
Discipline (e.g. CIV/STR/RAIL: |  | 321-CIV
Revision Number: |  | 0
Revision Date: |  | 2024-08-21
ITP created by: |  | VM
ITP approved for use by: |  | Romualdo Magpantay
Special Notes to ConQA Team : |  | ITP for SSO Project
Inspection & Test Plan - Lighting (Supply and Install) - MTM
[9 empty] | Revision: | 0
[9 empty] | Date: | 2024-08-21
Legend: HP: Hold Point, HP* Internal Hold Point, WP: Witness Point, IP: Inspection Point, SP: Surveillance Point
Item | Task/Activity Description | Reference | Acceptance Criteria | Inspection / Test |  |  | Responsibility | Verifying Documents | Date Completed | Sign-off
|  |  |  | Method | Frequency | Category
1 | Referenced Documentation
1.1 | Non Dependent | L1-CHE-STD-059 | N/A | N/A | N/A | N/A | N/A | N/A | NA | N/A
1.2 | Non Dependent | L1-CHE-STD-035 | N/A | N/A | N/A | N/A | N/A | N/A | NA | N/A
1.3 | Non Dependent | L1-CHE-SPE-155 | N/A | N/A | N/A | N/A | N/A | N/A | NA | N/A
1.4 | Non Dependent | AS/NZS 3000 | N/A | N/A | N/A | N/A | N/A | N/A | NA | N/A
1.5 | Non Dependent | AS/NZS 1158.3.1 (2020) | N/A | N/A | N/A | N/A | N/A | N/A | NA | N/A
1.6 | Non Dependent | A9819 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
2 | Preliminaries-Materials
2.1 | Obtain and review manufacturer documentations for the supply of materials | L1-CHE-STD-035 AS/NZS 2053 IFC Drawings | Materials comply with MTM Engineering stadard Lighting and Powerrelevant specifications. All materials shall comply with the standards and specifications shown on the drawings. All structural steel, associated components and welding consumables shall be manufactured by companies that hold quality systems certification to AS/NZS ISO 9001. * Enter: Teambinder Material Approval number [free text box] | Document Review | Each Lot | HP | Nominated Authority | ConQA Hold Point Release
2.2 | Concrete | IFC Drawings | Concrete complies mix complies with VR 400/40. Pile Concrete Grade at 28 days shall be 40 Mpa. * Enter: Teambinder Material Approval number [free text box] | Document Review | Each Lot | HP | Nominated Authority | ConQA Hold Point Release
2.3 | Reinforcement (Cage) | IFC Drawings VR 611.05 | Reinforcement cages shall be according to IFC Drawings Reinforcement complies with VicRoads Section 611.05 (a) & (b), and AS4671 (ACRS) * Enter: Teambinder Material Approval number [free text box] | Document Review | Each Lot | HP | Nominated Authority | ConQA Hold Point Release
2.4 | HD Bolts assemblies | A9819 VR 630.20 | HD bolt assemblies as per IFC drawings All HD bolts are grade 4.6/S, galvanised All nuts and washers to be galvanised * Enter: Teambinder Material Approval number [free text box] | Document Review | Each Lot
2.5 | Inspect supplied items upon delivery | QMP L1-CHE-SPE-155 | Supplied items are to correct spec, class, size and undamaged Luminaires: At the time of delivery, the supplier shall provide three hard copies of the following:  Installation Instruction Manual  Operation Instruction Manual  Storage, handling, loading and off–loading instructions  Test Certificates  Warranty Information | Visual /Site Inspection & Document Review | Each Lot | HP* | SE/PE/SPE | This ITP Attach records required
3 | Preliminaries-Related Works
3.1 | Conduit & pit installation | L1-CHE-STD-035 IFC Drawings | Conduit and Pit Installation works are to be recorded under ITP-183-CIV-SSB-Conduits and Pits-MTM Carpark lighting in addition to Subcontractors Checklist. | Document Review | Each Lot | IP | SE/PE/SPE | This ITP
4 | Pre-Construction Works
4.1 | Survey Set Out | IFC Drawings, | Survey to set out position of piles. Attach: Lot Map | Visual Documen Review | Each bore | HP* | SE/PE/SPE | Attached Geotechnical Report Attached Lot Map
5 | Construction
5.1 | Prepare the footing foundation (Excavation & levels) | IFC Drawings, Manufacturer specifications | Check levels and diameter conform to manufacturer drawings depending on type of pole to be installed. Foundations to be installed as per manufacturer specification and requirements. Pile holes to be inspected by Geotechnical Engineer. Attach: Geotechnical Report | Visual Document Review | Each bore | IP | SE/PE Geotechnical Engineer | Attached Geotechnical Report
5.2 | Installation of reinforcement cage | IFC Drawings, Manufacturer specifications A9819 | cage shall have enough clearance to the bore to maintain coverage as per IFC. Spacers and supports placed at intervals no more than 2m | Measure | Each bore | IP | SE/PE | this ITP
5.3 | Cast in items | IFC Drawings | Cast in items (conduits, hold down bolts, etc.) are installed in correct orientation and position. Hold down bolts have enough projection out side of the pile to accommodate for grout and base plate installation. | Measure | Each bore | IP | SE/PE | This ITP
5.4 | Pre-pour inspection | IFCDrawings MRPA Construction Management plan | Pre-pour inspection to be conducted. Check the reinforcement cage as per manufacturer spec and IFC. Cast in items (e.g. bolts and conduits) positions to be installed as per IFC drawings/manufacturer drawings. Projection of items to be installed as per IFC drawings. Position and projection to be confirmed during inspection. | Measure | Each Lot | HP | Nominated Authority | ThisITP
5.5 | Concrete placement and Compaction | IFC Drawings MRPA Construction Management | The temperature of concrete, measured immediately prior to placing, shall not be less than 10°C or greater than 32°C. All concrete batches are traceable. All concrete batches are from approved mix Concrete shall be placed through either a tremie pipe or concrete pump and not dropped freely from a height exceeding 2m. The initial discharge is pumped to waste until a consistent workable mix is discharged. the ends of the discharge pipe shall not be lifted off the base of the excavation until a 2m head is created, which shall be maintained until the completion of the pour. Attach: Concrete Pour Record Attach: Concrete Dockets | Document Review | Each Lot | HP* | SE/PE | This ITP Attached Pou Records Attached Dockets
5.6 | Concrete Sampling | IFC Drawings | Concrete cast in one continuous operation to be tested at a frequency as shown below: 0m³ to 10m³ = 1 sample 10m³ to 25m³ = 2 samples 25m³ to 50m³ = 3 samples 50m³ to 100m³ = 4 samples + 2 no. VPV cylinders. For each additional 50m³ and additional sample shall be taken. where the time interval between the end of discharge of one truckload of concrete and the beginning of discharge of the next truckload exceeds 45 minutes, the minimum number of test samples shall be one (1) per truckload of concrete Each sample shall consist of 1 no. slump or spread test and 3 no. compressive strength cylinders minimum. Compressive strength cylinders = 1 no. 7 day strength, 2 no. 28 day strength. Note: Additional cylinders may be required for other purposes such as early strength determination of adjacent piles. Record: Required information on the Concrete Pour Record. | Visual | Each lot | IP | SE/PE Concrete Tester | This ITP
5.7 | Pile Integrity Testing | VR 606.07 (a, d & e) AS2159 Clause 8.8 A9819 | Pile integrity testing shall be conducted after the concrete strength has reached 25MPa but not less than 7 days from casting. Cross-sectional area = ≥95% If any test fails, all piles shall be tested. Attach: Pile Integrity Test Report | Document Review | Piles #1 - #6. Reduced to 1 test per 3 piles if the first 6 tests pass | IP | Testing Consultant SE/PE | This ITP
5.8 | Installation lighting pole bases & columns | IFC Drawings L1-CHE-STD-035 | Free standing platform lighting poles shall be at earth potential as mounted in ground or on structure. Light fittings shall be earthed by the earth cable from Concrete and metallic poles at all new installations and station extensions that support low voltage equipment shall be earthed by an underground conductor that is connected to the earth at the origin from which the circuit is supplied in accordance with AS/NZS 3000.9.5.2 Lighting installations shall be LED and comply with L1-CHE-SPE-155 Car park poles shall be located as per IFC Drawings. Pole access hatches shall be orientated to allow unobstructed access. Level formed ground shall be at each pole for access by ladder or EWP. | Visual /Site Inspection & Document Review | Per Pole | IP | SE/PE/SPE | This ITP
5.9 | Assembly of outreaches and luminaires | L1-CHE-STD-035 IFC Drawings | Outreach bracket to be installed to the pole spigot using the clamping bolt assemble - Bracket and luminaire to align at right angles to vehicle path on road |  | Per Pole | IP | SE/PE/SPE | This ITP
510 | Installation of lighting distribution cabinet | L1-CHE-STD-035 IFC Drawings | The switchboard or distribution board shall be designed and manufactured from suitable materials appropriate to the location in accordance with AS/NZS 3439.1. | Visual | Per lot | IP | SE/PE/SPE | This ITP
5.11 | Installation of cabling | IFC Notes | All electrical cabling to be in accordance with the requirements of AS/NZS 3000: (Australian/New Zealand Wiring Rules) - Each pole to be cables from the pole circuit breaker | Visual & Document Review | Per Lot | IP | SE/PE/SPE | Test Certificate This ITP
5.12 | Commissioning & testing | L1-CHE-STD-035 | Upon final acceptance, the Contractor shall switch on the lighting installation at the distribution cabinet in automatic mode, and record the time, date and meter reading for contractual, warranty and power supply purposes and supply this record to the Superintendent within 48 hours | Commissioning & testing | Upon completion of each section | HP* | SE/PE/SPE Services Engineer | This ITP Attach Certificate
5.13 | Labelling of Assets | L1-CHE-STD-035 MTM Standard | Labels fixed to poles as per MTM standard. Pole numbering Labelling of switchboards, distribution boards, circuit breakers, RCDs and all control devices shall be labelled as per Appendix B in MTM standard. Indelible Labelled srawings shall be permanently displayed at the point of supply. Permanent field markers shall clearly identify the extent of the EPZ locations. | Visual /Site Inspection & Document Review | Per pole | IP | SE/PE/SPE | This ITP
5.14 | Grouting | IFC Drawings A9819 | Install 50mm Grout as per IFC Drawings. Grout completely fills void between op of pile and structure by ramming against fixed support. | Visual Measure | Per pole | IP | SE/PE | This ITP
5.15 | Earth electrode or mat | IFC Drawings A9819 | Must be one installed per each lighting and power installation. The minimum distance between Earth electrodes or mats of lighting and power supply systems and rail tracks shall be based on the earthing design but shall be a minimum distance of 3.0 metres from the nearest running rail. Earth mats shall be bonded into a continuous electrical grid using a welded connection in accordance with AS 1554 or approved crimp connection from the MTM Engineering A1215 Remove covered Approved Product List. A certificate of compliance to AS 2832.5 and test results shall be provided for all bonding connections. | Visual | per pole | IP | SE/PE | This ITP
6 | Post Constrution
5.1 | Attached and verify Subcontractor conformance records/signed ITP including relevant verification sheets | IFC Drawing Note | Check conformance report against project conformance criteria | Doc. Review | Each lot | IP | SE/Site Supervisor | Sign ITP Attach documents
6.2 | Compressive Strength Test Results | IFC Drawings Table VR 610.05.051 VR 610.16 (g) | 7 day compressive strength to comply with table 610.051 for early indication that the strength is tracking correctly. 28 day compressive strength (average of the 2 no. cylinders) per sample comply with the design strength. Note: 1 of the 2 no. 28 day cylinders per sample may be as low as 90% of the required strength, so long as the average meets the required strength. Attach: Compressive Strength Test Results | Document Review | Each cylinder | IP | SE/PE | This ITP
6.3 | As-Constructed Plans | IFC Drawing Note | The Contractor shall supply to the Superintendent two copies of ‘As-Constructed’ plans along with a USB drive or other approved storage medium containing the CADD drawing files, and the same shall be supplied by the Contractor to the local distribution company if appropriate. | Document Review | Upon completion/ Work area | HP* | SE/PE/SPE | Sign ITP Attach As Constructured Plans
6.4 | Non-conformance Report (NCR) Closure | MRPA Quality Management Plan | Ensure that any NCRs pertaining to the lot / element / Work area that this ITP covers, have been closed in CAMs. | Document Review | Once, prior to closure of this lot / element / Work area | HP* | SE/PE/SPE | This ITP
Final Inspection
On behalf of Metropolitan Roads Program Alliance, it is hereby certified that the Works represented by the item of work listed have been tested in accordance with the Project Quality Plan and conform in all respects with the requirements of the Contract.
Print Name: Position: Signature: Date: / /