## Resources
Rich Type | Id | Warnings | type | name | values | prefix | postfix | Usage Count | User Addable | Template Name | Template Id
checklist-flat |  |  | checklist | ITP001 - Watermain Checklist |  |  |  |  | Yes | ITP001 - Watermain | 22d819b5-609b-4068-a49d-8f8b52390005
checkpoint-status |  |  | checkpoint | 1 - Service Location
label | ea7c0170-7a67-5b67-a49d-17d0e186feb3 |  | note | Activity Task: Potholing of Existing Services
label | 91c33d94-9ddb-5938-83f7-543ad7b99b7b |  | note | Acceptance Criteria: Excavation of services to be carried out in accordance with service providers recommendations.
label | 8ed03686-4995-57e0-ae01-01829c33247d |  | note | Certifying Documents and Frequency: Pothole records to be kept in spreadsheet form and provided when required. All potholes to be photographed and information picked up by surveyor (information to be supplied northing / easting and RL level).
label | 07479a42-f9ce-5ad7-98b2-2b4bc5ec7827 |  | note | Supervisor, Foreman or Subcontractor: P
label | 4138562a-3258-5363-924f-f7e68d9fe9c7 |  | note | Project Manager or Delegated Person: W
label | 5f12bf76-70a6-516e-91bc-e0dd43e90c76 |  | note | Engineer’s Representative: R
text | 12e6439a-fa86-555a-8ced-c8d0e1f43461 |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | 2 - Route Alignment
label | f875a99c-6016-540e-b17e-3b668b442955 |  | note | Activity Task: Set Out and Mark Up
label | e9e05041-3afc-5c33-9775-36d7a579575c |  | note | Acceptance Criteria: Mark out to be carried out prior to commencement of works – Alignment to mirror construction drawings unless alternative approval sorted and confirmed.
label | 55168607-d7b0-5f5b-8d43-030b96c12a86 |  | note | Certifying Documents and Frequency: Surveyor to confirm alignment of new pipeline, overlay drawing to be placed over the As-built layer to ensure that design is to work.
label | 3c164230-8a75-5b2a-a4f0-16a9888e7eb9 |  | note | Supervisor, Foreman or Subcontractor: P
label | 7ce32ed2-9008-5c98-bc47-f1ef5853250a |  | note | Project Manager or Delegated Person: R
label | 6e5f4149-6037-5590-bdaf-813d14aea919 |  | note | Engineer’s Representative: R
text | e9230e5d-630b-5350-9c3f-97012c0a6fd4 |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | 3 - Construction of Pipeline with Fusion Welded Joints
label | ee21c6d8-bf34-547e-96e1-e9cd661f6f3f |  | note | Activity Task: Butt Welding of Pipes above or below ground (All joints to be welded, mechanical joints can be used where necessary and)
label | 780d6e40-25a3-529a-837c-0fd5af550ff5 |  | note | Acceptance Criteria: All welds are to be fully logged by the use of data logging equipment. All weld parameters are to be recorded for each separate weld as well as the welder, weld number, location, date and time of weld and air temperature All butt welds to be undertaken in accordance with the manufacturer’s recommendations Installation as per Pump & valve Manual
label | ee07683a-81f4-5c1a-a666-89a66231febb |  | note | Certifying Documents and Frequency: Approved Welding procedure Inspection and Test Records provided by Specialist Subcontractor Test Weld to be provided at commencement of the works.
label | d41538f3-e3ee-540c-b4e7-856f0b093120 |  | note | Supervisor, Foreman or Subcontractor: W
label | 5415f89a-594a-5f87-81c1-5c20a8b0cbf9 |  | note | Project Manager or Delegated Person: W
label | f1c2f931-c52b-59dd-810d-87bf72ff8d1b |  | note | Engineer’s Representative: H
text | 0eae78df-8a94-5592-b26a-0bc4628eb2ff |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | 4 - New Watermain pipe in Open trench
label | 2baac78d-6342-5a85-8ccc-d45e59d5c70c |  | note | Activity Task: Material supply
label | d5663f71-c746-5240-881f-7556b4d7144f |  | note | Acceptance Criteria: Certification from manufacturer that materials comply with the manufacturer’s specification
label | fdf3b255-9e68-500b-bc19-06383f018acf |  | note | Certifying Documents and Frequency: Delivery Dockets,
label | 17013dba-c090-5404-b573-8aabf25e2814 |  | note | Supervisor, Foreman or Subcontractor: W
label | 5ed5ecc3-b969-52e7-8617-10226a8e430f |  | note | Project Manager or Delegated Person: W
label | 3db78167-a350-514f-82d3-776cf83f029e |  | note | Engineer’s Representative: W
text | 5ad92e4c-884a-577f-b9b8-f20d3d88fc42 |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | 4.1 - New Watermain pipe in Open trench
label | ddc252de-7883-51d2-b847-db08ae512953 |  | note | Activity Task: Backfilling of open trench
label | 3f0350aa-2a4c-59f0-b703-429797514bd1 |  | note | Acceptance Criteria: GAP 65 or and approved selected excavated material. The GAP 65 is to be covered with ordinary backfill (excavated material), each layer not to exceed 300mm thick No mechanical compaction until the pipe is covered by at least 300mm of material Detector tape to be placed 200-400mm below surface. A detector cable is to be laid with the pipe and tested for continuity on completion
label | 37845cf6-4b57-580f-b935-031e097d9d41 |  | note | Certifying Documents and Frequency: Photos etc as evidence
label | 755924d1-6e80-5f2b-b6bc-25799ff682eb |  | note | Supervisor, Foreman or Subcontractor: P
label | 447ad46b-cb12-5fbd-9139-5a25d17d1caa |  | note | Project Manager or Delegated Person: R
label | 0afa16e6-69a7-50cf-948a-b9bd0e4bd914 |  | note | Engineer’s Representative: R
text | ae1acd16-0f75-5914-803e-03d0fc661528 |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | 5 - Welding of fittings using PE or mechanical connections.
label | e418641c-b2be-52b5-8436-0041e20f45e9 |  | note | Activity Task: Supply of Material
label | 1c2a6e27-9344-5629-ab35-4c848d4a0440 |  | note | Acceptance Criteria: Certification from manufacturer that materials comply with the manufacturer’s specification
label | 1cfc1f6b-8997-52bd-b5b1-51a18eaa0045 |  | note | Certifying Documents and Frequency: Delivery Dockets,
label | 00362a72-12ea-51fa-8334-cd6d806f4d7a |  | note | Supervisor, Foreman or Subcontractor: W
label | d5f93775-41ee-55b4-bd53-40bf99292568 |  | note | Project Manager or Delegated Person: W
label | 753eb62a-c5da-5cf6-b686-c2f8791bde8a |  | note | Engineer’s Representative: R
text | e696e067-a699-5657-9e66-7ce631e8615b |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | 5.1 - Welding of fittings using PE or mechanical connections.
label | 1adcfe22-5b18-5ea9-83cf-03848591bdc6 |  | note | Activity Task: Construction of welds
label | 7ecca80b-b3c3-54eb-bee9-547dc55cf1b8 |  | note | Acceptance Criteria: Test Weld to be sent for testing at qualified laboratory, tests to be carried out. As required.
label | adba9304-1bd7-52ae-ab6f-26f18a4264a1 |  | note | Certifying Documents and Frequency: EF Welding information to be provided with test weld, copy of information to be kept on site in QA folder, Results / Feedback to be supplied to WDC.
label | 45819fb8-4fa4-5f3f-b2db-cd71780d8ed6 |  | note | Supervisor, Foreman or Subcontractor: P
label | dbc2fc3e-36ed-5d0d-94d8-90c87929822b |  | note | Project Manager or Delegated Person: W
label | 2dcdc1e2-351c-50c8-8277-37843e0b9bc8 |  | note | Engineer’s Representative: R
text | 0f00b957-a9a7-5577-b85c-e080b2a185d3 |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | 5.2 - Welding of fittings using PE or mechanical connections.
label | d249a0ba-b496-51f5-9646-ae88d28fcd1c |  | note | Activity Task: Construction
label | dfa2fbbe-ed0f-53a5-b41f-806ba36f2211 |  | note | Acceptance Criteria: All weld parameters are to be recorded for each separate weld as well as the welder, weld number, location, date and time of weld and air temperature All butt welds to be undertaken in accordance with the manufacturer’s recommendations.
label | a8e585c3-20e2-595c-9bd4-fa9d24227433 |  | note | Certifying Documents and Frequency: EF Weld Inspection joints QF037 Approved Welding procedure Welding machine certified and calibrated with data logging capacity. Sub-contractor to supply Data Logger information etc for butt-welding.
label | 64c2183a-8557-5060-ac44-e802ce44dc98 |  | note | Supervisor, Foreman or Subcontractor: P
label | e54223f1-3b03-5d83-a61b-1d438261489a |  | note | Project Manager or Delegated Person: R
label | 0b793278-80ef-50de-9386-e47827a627b6 |  | note | Engineer’s Representative:
text | be757378-28c1-5d8c-bb60-1143a2619c7d |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | 5.3 - Testing of butt Welds
label | 1785ad4f-e574-5ad9-91a3-8bf43d34354a |  | note | Activity Task: Butt Welding Test
label | b1653c4d-b221-549c-9fc3-98e10bc3e770 |  | note | Acceptance Criteria: Tests to be carried out to see Ductile or Tensile Failure as per WDCEES specifications.
label | 0676e5d5-9305-5399-8bd6-1cac3b316387 |  | note | Certifying Documents and Frequency: Test Results
label | bce02059-0e67-5179-a8ce-966e545078a3 |  | note | Supervisor, Foreman or Subcontractor: P
label | ab9ff7db-d665-5474-a13e-c64be0f98dd3 |  | note | Project Manager or Delegated Person: P
label | c691c368-5875-5547-8fb6-468ca2d306a5 |  | note | Engineer’s Representative: H
text | d3f8f43a-cf7f-5eeb-91b8-60d4ee5f2429 |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | 6 - Testing and Commissioning
label | dd49afd2-2644-55c6-8fab-070ef4148a92 |  | note | Activity Task: Testing of the new pipelines and commissioning
label | 64e2a367-348f-5db9-ab0e-75d1cb56f9bb |  | note | Acceptance Criteria: Pressure Tests/ Holding Tests
label | e17fc02f-b7c1-5610-a393-dd5abc659bf7 |  | note | Certifying Documents and Frequency: All tests to be recorded using Check sheet QFH-003
label | 4dcc0169-ce67-5d74-a9e7-adb3877d15bd |  | note | Supervisor, Foreman or Subcontractor: P
label | 02ab105d-2d97-55ab-93de-fd04fb7eec85 |  | note | Project Manager or Delegated Person: P
label | 1ddf5854-3c6d-5283-af69-0e170ab484a0 |  | note | Engineer’s Representative: H
text | 389cd2a2-3e38-5a64-a9b2-6d24a6d3bcd8 |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | 7 - As Built Records & Asset Register
label | d0249d9f-457b-5683-8e4e-c87fb622efc6 |  | note | Activity Task: Compile all Quality Documentation in accordance with the Particular Specification
label | b05f02cc-b565-5df1-8485-222f9b4317a2 |  | note | Acceptance Criteria: Particular Specification As Built Drawings: 1 set electronic pdf format; 1 set of hard copy A3 plans and CAD. Drawings to comply with WDC standards and be certified by the UCCL Quality Manager An electronic copy of the As-builts shall be submitted prior to the Engineer prior to issue of the PC Certificate The Contractor shall complete an Asset Register containing the following details for each new or altered asset; Type, Manufacturer, Model, Serial Number, Date of Manufacture, Date of Installation, Expected Life, Co-Ordinates, and Cost.
label | cfc31230-9c27-53ef-859d-1a6c0334169d |  | note | Certifying Documents and Frequency: As Built Drawings, Asset Information Schedule,
label | eeb11ffc-f1ea-5c88-8714-2d0de2dd48f7 |  | note | Supervisor, Foreman or Subcontractor: P
label | ab68d21d-5848-5b97-b06d-fd01d9908423 |  | note | Project Manager or Delegated Person: R
label | 41b1e290-bbcf-51a1-9f6c-f6dd7f04ac64 |  | note | Engineer’s Representative: R
text | f4d5eb2e-b553-5f50-8d87-eb9f9c90f349 |  | textbox | Date Completed:
checklist-flat |  |  | checklist | Electrofusion Weld |  |  |  |  | Yes | Electrofusion Weld | a6f72d25-8699-47c5-86da-ae52c269582b
checkpoint-status |  |  | checkpoint | Welding details completed
text | c2cd47ea-90c3-5c98-8d21-eabf385289b3 |  | textbox | EF Coupler completed by and recorded.
label | defbb77b-fefc-5374-9745-99c8dfe68b59 |  | note | Fusion Machine Used
text | 0d124e63-d6e8-5006-99f6-87c82a096cb3 |  | textbox | Record EF Coupler Used (Size)
checkpoint-status |  |  | checkpoint | Pipe surface free from scratches,deeper than 10% of the wall thickness ?
checkpoint-status |  |  | checkpoint | Pipe scraped and marked ?
checkpoint-status |  |  | checkpoint | Pipe surface cleaned with Isophrophel alcohol?
checkpoint-status |  |  | checkpoint | Barcode scanned by machine?
checkpoint-status |  |  | checkpoint | Record cooling time achieved?
checkpoint-status |  |  | checkpoint | E.F Coupler Operator Signature Required
select | 7f6533a6-805e-5db7-a91c-8eef51669e2d | DataPoint is missing 'select' values | dropdown | Name
holdpoint |  |  | signoff | Name/ Signature
checkpoint-status |  |  | checkpoint | Post weld checks
holdpoint |  |  | signoff | Post weld checks completed- Request Signoff
checklist-flat |  |  | checklist | Butt Weld |  |  |  |  | Yes | Butt Weld | bebd75bb-17ba-434a-aab4-51ab2276d38e
checkpoint-status |  |  | checkpoint | Weld Details Completed
text | dd3b9e5a-a8f6-5b43-ad43-b78221b5c7d6 |  | textbox | Weld Number
text | 14d95bc9-c415-5f96-af41-e7f0f94de057 |  | textbox | Weld Completed By:
label | 90fb0313-f236-59cb-9bb8-6295bfdad0ce |  | note | Welding Machine #
boolean | e579a7da-b48e-5de8-b65d-8699a41001f2 |  | tickbox | Machine 1
boolean | 9339c47b-1b0d-5bab-a4b3-a15d9eb56cbc |  | tickbox | Machine 2
boolean | 75680e62-2f4a-5420-8085-33b6735b5da2 |  | tickbox | Machine 3
text | d7d17810-0e2d-5aa3-9db0-834d075623bc |  | textbox | Certificate #
checkpoint-status |  |  | checkpoint | Pre-weld checks - Visual Inspection of Pipe
label | a4d28a97-8cf2-5092-bd76-4a4259dccdb8 |  | note | Ensure branding markings correct
text | a7a364a8-46e9-5ea3-b3c0-aabcf4a4bf60 |  | textbox | Record pipe batch number as labelled on the pipe.
text | ebb4b545-29b8-5580-94f2-24d89869c2e5 |  | textbox | Record pipe wall thickness and inspect.
label | 201e9dc8-65ed-5c11-997d-dfd9d344ec14 |  | note | External surfaces are free from scratches deeper than 10% of wall thickness.
label | 23102593-036e-504b-83f4-a55681768872 |  | note | Inspect internal surface of pipe for scratches.
label | 90e718a7-7212-5a49-a0a8-4c6e498a5cf3 |  | note | Inspect pipe for cracks.
label | ce74ae9f-e60d-577c-abc0-0a0f7c1ceeb6 |  | note | Inspect internal ridges or ripples exceeding 0.5mm in height.
label | fee7c0de-718a-5b9c-b08f-006824156da1 |  | note | Clean and wipe pipe with Isopropanol.
label | 9d6f3e0e-070b-5df4-b6e7-aab278740c96 |  | note | Inspect pipe ends are dry from any water content.
checkpoint-status |  |  | checkpoint | Pre-Weld Checks - Weld Machine Checks
text | ecb67442-ff9b-5d22-9f4d-73f8af3e7c46 |  | textbox | Heater plate temperature checks taken and recorded
label | 245f230f-83a6-53ad-b1c7-2098bd6fb2d7 |  | note | Ensure pipe ends are capped, welding area isolated to regulate cooling and prevent airborne contaminants.
checkpoint-status |  |  | checkpoint | Post Weld - Visual Checks
label | 441f62ce-5b8a-5eb7-95ef-1858db94bdfc |  | note | Alignment of pipes is less than 10% of pipe wall thickness?
label | 01491718-b3f4-52e2-9dba-8c5153d20b74 |  | note | Fusion beads symmetrical on both sides of weld
label | 135b576b-0cf5-5eb0-a451-f4c38846ef83 |  | note | Ensure Beads are fully rolled over
label | bae89911-ed06-57ba-b9f1-80a93a53788d |  | note | Inspect for cracks in beads and welds are free of pitting and bubbling.
label | 18e08e1a-92ef-501b-a67a-a3f9fd7b38af |  | note | Inspect for inclusions or other obvious faults present.
label | f4078a3f-7bf7-5f68-b80e-81669bff43e2 |  | note | Internal weld beads removed from pipe?
checkpoint-status |  |  | checkpoint | Weld Records and Inspections
label | 88b7f327-cac7-505b-b8ca-3b276eb4fd9c |  | note | Data logger records printed, checked and attached?
label | 83e79f9c-4833-54b4-8127-7c73b28f27d5 |  | note | Weld completed and completed?
holdpoint |  |  | signoff | Post weld checks completed- Request Signoff
checklist-flat |  |  | checklist | ITP003 - Electrical & Communication Duct Installation |  |  |  |  | Yes | ITP003 - Electrical & Communication Duct Installation | ca0e6e8d-5347-4eac-85cb-562457fd258c
checkpoint-status |  |  | checkpoint | 1 - Service Location
label | 9bd3acbc-a87e-5b49-9c27-b3704881dbd7 |  | note | Activity Task: Potholing of Existing Services
label | 6c174ae6-fc96-559f-9ca2-985287399fe7 |  | note | Acceptance Criteria: Excavation of services to be carried out in accordance with service providers recommendations.
label | 40306689-e161-5e46-9807-2cfbd5b02ff2 |  | note | Certifying Documents and Frequency: Pothole records to be kept in spreadsheet form and provided when required. All potholes to be photographed and information picked up by surveyor (information to be supplied northing / easting and RL level).
label | 7441e0d8-d76c-537a-9bd9-7cdf92bd9cb5 |  | note | Supervisor, Foreman or Subcontractor: P
label | 9c2bfded-7a7f-5fae-8666-cb457658e505 |  | note | Project Manager or Delegated Person: W
label | 8daaa018-b755-5a8a-a374-9084b8c0efa2 |  | note | Engineer’s Representative: R
text | 7b9f921b-5d07-5e2b-bc3b-1707b09c44b7 |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | 2 - Route Alignment
label | 93df5800-0e80-576f-8df0-b1f53d2166ae |  | note | Activity Task: Set Out and Mark Up
label | cc8ea3b7-02c8-55c6-9a67-afec6276112a |  | note | Acceptance Criteria: Mark out to be carried out prior to commencement of works – Alignment to mirror construction drawings unless alternative approval sorted and confirmed.
label | 4a50759c-459d-5edf-949d-b6412e2bfff4 |  | note | Certifying Documents and Frequency: Surveyor to confirm alignment of new pipeline, overlay drawing to be placed over the As-built layer to ensure that design is to work.
label | 0cf18592-598a-593e-be5e-3bc379f081f6 |  | note | Supervisor, Foreman or Subcontractor: P
label | a9d45ad0-7a47-5018-bf92-bc4b546ab7fd |  | note | Project Manager or Delegated Person: R
label | bdcf1ecf-5a20-5c32-baca-3e2f2e11ad9b |  | note | Engineer’s Representative: R
text | 43595fd1-0bbb-56ce-93af-d4cb9b53dcd0 |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | 4 - New Electrical and communication ducts in Open trench
label | f2686962-76d6-54df-af55-2932c6a8ce55 |  | note | Activity Task: Material supply
label | e17c9feb-3906-597f-9568-97c79305e657 |  | note | Acceptance Criteria: Certification from manufacturer that materials comply with the specification
label | a2f183f5-812d-52c2-bf14-38652b0a4de5 |  | note | Certifying Documents and Frequency: Delivery Dockets,
label | 85e1d025-68a7-5588-91e4-3937514faabd |  | note | Supervisor, Foreman or Subcontractor: W
label | d3739d1c-2fcb-529d-951b-fbfda296117d |  | note | Project Manager or Delegated Person: W
label | 241bfb2a-d44c-5dd8-b848-803a43d9cf97 |  | note | Engineer’s Representative: W
text | 674447e2-5e68-52ef-997d-d79b72ed796d |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | 4.1 - New Electrical and communication ducts in Open trench
label | acae0309-61e3-54a1-8d21-3d4a1f634f8a |  | note | Activity Task: Construction
label | 26fc161d-0a50-5d8c-a144-3454d081f157 |  | note | Acceptance Criteria: Installation as per WDC Engineering Specification Location and level of invert +/-10mm or as agreed on site. Trench to be fully lined with GCL as per IFC Drawing 32800-40 E. Compaction of bedding (SAP7) and backfill as per NZS/AS 3725
label | 67b03bd9-cd0f-5e65-869c-0c26c4823056 |  | note | Certifying Documents and Frequency: Pipeline Inspection Sheet QF008-A Trench width shall be Pipe Diameter + 450mm or as Required when there is multiple pipes in same trench
label | 07c04519-9d95-56d8-9ef2-fccac4e79cb3 |  | note | Supervisor, Foreman or Subcontractor: H
label | c8bafa37-888b-5f2b-b716-e2d859b4ac70 |  | note | Project Manager or Delegated Person: R
label | 67611e9e-790c-5fc2-bf21-390e353f9612 |  | note | Engineer’s Representative: R
text | c8d6ee06-13d1-5b7b-9618-7b024fa3824e |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | 4.2 - New Electrical and communication ducts in Open trench
label | 1a90e66c-84a9-5c93-ab0c-1602f6dcbf71 |  | note | Activity Task: Backfilling of open trench
label | 2ce95c29-f307-5261-b6b9-b185c9e08416 |  | note | Acceptance Criteria: GAP 65 or and approved selected excavated material. The GAP 65 is to be covered with ordinary backfill (excavated material), each layer not to exceed 300mm thick No mechanical compaction until the pipe is covered by at least 300mm of material Detector tape to be placed 200-400mm below surface. A detector cable is to be laid with the pipe and tested for continuity on completion
label | 4af09e11-d0c2-5b2d-b596-4c1bee186b0d |  | note | Certifying Documents and Frequency: Photos etc as evidence
label | 40fbddde-a892-5f78-8966-d76eebb6e7f0 |  | note | Supervisor, Foreman or Subcontractor: P
label | 71055383-7231-5f2f-a25f-bd1f6f120a00 |  | note | Project Manager or Delegated Person: R
label | 80b95cd1-9e37-5d62-b4ca-04a265e4fee7 |  | note | Engineer’s Representative: R
text | 603394c8-9766-5600-943c-e5f302107be0 |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | 7 - As Built Records & Asset Register
label | 3415578a-6d6f-587e-bd0e-8fe1c1beb4f9 |  | note | Activity Task: Compile all Quality Documentation in accordance with the Particular Specification
label | 4429f01f-5191-5da6-a2bd-408124e045ee |  | note | Acceptance Criteria: Particular Specification As Built Drawings: 1 set electronic pdf format; 1 set of hard copy A3 plans and CAD. Drawings to comply with WDC standards and be certified by the UCCL Quality Manager An electronic copy of the As-builts shall be submitted prior to the Engineer prior to issue of the PC Certificate The Contractor shall complete an Asset Register containing the following details for each new or altered asset; Type, Manufacturer, Model, Serial Number, Date of Manufacture, Date of Installation, Expected Life, Co-Ordinates, and Cost.
label | ce1ff065-3c32-5fd4-8589-b06f6304cff9 |  | note | Certifying Documents and Frequency: As Built Drawings, Asset Information Schedule,
label | fd87f8b5-5dbb-537f-86bb-cfb8e2c92d02 |  | note | Supervisor, Foreman or Subcontractor: P
label | d813c2a7-9d47-593e-b0d3-94ac3986630b |  | note | Project Manager or Delegated Person: R
label | 395c2870-0487-547b-a343-96a513afda80 |  | note | Engineer’s Representative: R
text | cb035081-a199-534a-bdf3-8a030017f547 |  | textbox | Date Completed:
checklist-flat |  |  | checklist | ITP002 - Sewer Raising Main Checklist |  |  |  |  | Yes | ITP002 - Sewer Raising Main Checklist | d1e97758-fc95-4c00-8650-f576df1f5e6e
checkpoint-status |  |  | checkpoint | 1 - Service Location
label | 1fd272f0-1524-53d0-bde3-51742e97241b |  | note | Activity Task: Potholing of Existing Services
label | 2218f23b-3f56-533b-ab24-73e529507dd1 |  | note | Acceptance Criteria: Excavation of services to be carried out in accordance with service providers recommendations.
label | d7e3d839-25c1-5648-88ae-17e24f45eced |  | note | Certifying Documents and Frequency: Pothole records to be kept in spreadsheet form and provided when required. All potholes to be photographed and information picked up by surveyor (information to be supplied northing / easting and RL level).
label | c547c5e4-732e-5033-a754-3cbf09655f8a |  | note | Supervisor, Foreman or Subcontractor: P
label | 1170a2df-261e-56af-8cd6-9a0941725fd6 |  | note | Project Manager or Delegated Person: W
label | 31986658-ef3c-5623-a6a3-217c31292d20 |  | note | Engineer’s Representative: R
text | 04444a01-9c53-5c0b-811e-8fa808adb762 |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | 2 - Route Alignment
label | 9a37f786-f44a-5e01-b695-93043a715746 |  | note | Activity Task: Set Out and Mark Up
label | f95cfc63-e3f9-5b13-a653-9a602194a4f3 |  | note | Acceptance Criteria: Mark out to be carried out prior to commencement of works – Alignment to mirror construction drawings unless alternative approval sorted and confirmed.
label | 055efbdf-8836-5e91-9f77-c5a405438d74 |  | note | Certifying Documents and Frequency: Surveyor to confirm alignment of new pipeline, overlay drawing to be placed over the As-built layer to ensure that design is to work.
label | 14a0636f-d17e-5fc4-ac96-6ddd591de9bd |  | note | Supervisor, Foreman or Subcontractor: P
label | 1f7f4dff-7f98-594f-85aa-5253fe59f087 |  | note | Project Manager or Delegated Person: R
label | e0655404-458c-5ce9-9367-44da3b3cc6e9 |  | note | Engineer’s Representative: R
text | 961e0f92-c97a-5853-a1d8-d3d65367cc9c |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | 3 - Construction of Pipeline with Fusion Welded Joints
label | 2c76f2cd-9334-54bb-8c72-5c24b9e95c98 |  | note | Activity Task: Butt Welding of Pipes above or below ground (All joints to be welded, mechanical joints can be used where necessary and)
label | 420687d1-99e4-535d-a446-a362c09ff69a |  | note | Acceptance Criteria: All welds are to be fully logged by the use of data logging equipment. All weld parameters are to be recorded for each separate weld as well as the welder, weld number, location, date and time of weld and air temperature All butt welds to be undertaken in accordance with the manufacturer’s recommendations Installation as per Pump & valve Manual
label | 20c9da2c-3ea6-54d8-a036-7ca4dd51ff56 |  | note | Certifying Documents and Frequency: Approved Welding procedure Inspection and Test Records provided by Specialist Subcontractor Test Weld to be provided at commencement of the works.
label | 504e9e34-c790-52bb-aadc-042ced67af01 |  | note | Supervisor, Foreman or Subcontractor: W
label | 73a35fe9-20cc-5dc4-a9b7-f894c007f8a7 |  | note | Project Manager or Delegated Person: W
label | 242e06b4-9ead-5efc-91d4-ee9e2a6acf4e |  | note | Engineer’s Representative: H
text | ec514db6-7b7d-5719-b188-008f35c8d356 |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | 4 - New Pressure PE Sewer pipe in Open trench
label | 0eaead0e-e1bb-5f07-a1f3-69b6516e346d |  | note | Activity Task: Material supply
label | ba59d223-4d16-5139-ab76-4e67a95c6f5b |  | note | Acceptance Criteria: Certification from manufacturer that materials comply with the manufacturer’s specification
label | f8f0d008-e8df-54fb-9ea6-b6cd8e100498 |  | note | Certifying Documents and Frequency: Delivery Dockets,
label | af42159e-7937-58d1-8ddf-05b90379f32f |  | note | Supervisor, Foreman or Subcontractor: W
label | 998c0e88-2f19-563a-90e7-832c7fec11c1 |  | note | Project Manager or Delegated Person: W
label | 666a49d0-2e99-5598-a4b9-96f517bf1732 |  | note | Engineer’s Representative: W
text | 97c6781b-3d3c-5a22-b12f-d09cc47fedf9 |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | 4.1 - New Pressure PE Sewer pipe in Open trench
label | 5067fed3-c574-5bd7-ae50-f13ad36bdc34 |  | note | Activity Task: Construction
label | e03060e0-4c3d-5ae7-b7bd-fa0a75f74e6a |  | note | Acceptance Criteria: Installation as per WDC Engineering Specification Location and level of invert +/-10mm or as agreed on site. Trench to be fully lined with GCL as per IFC Drawing 32800-40 E. Compaction of bedding (SAP7) and backfill as per NZS/AS 3725
label | e3829b9c-db86-56fc-ac0b-bbe9dcd06fad |  | note | Certifying Documents and Frequency: Pressure Sewer Pipeline Inspection Sheet QF008-A Trench width shall be Pipe Diameter + 450mm or as Required when there is multiple pipes in same trench
label | 6b8aa0f1-b648-562a-8b5d-4f27ae1834c2 |  | note | Supervisor, Foreman or Subcontractor: H
label | 4a5ff047-e785-554d-b1f4-6d779728052c |  | note | Project Manager or Delegated Person: R
label | 1f9b6511-8282-5d03-833c-200c20b74844 |  | note | Engineer’s Representative: R
text | c1755ff3-55fc-5da2-958c-dbd20a914597 |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | 4.2 - New Pressure PE Sewer pipe in Open trench
label | 51b7ef08-d589-5bc0-b0e1-c6d583cc3f2a |  | note | Activity Task: Backfilling of open trench
label | be7a5bfa-5876-55ed-98ae-994bac5a7f4c |  | note | Acceptance Criteria: GAP 65 or and approved selected excavated material. The GAP 65 is to be covered with ordinary backfill (excavated material), each layer not to exceed 300mm thick No mechanical compaction until the pipe is covered by at least 300mm of material Detector tape to be placed 200-400mm below surface. A detector cable is to be laid with the pipe and tested for continuity on completion
label | 585f4243-6216-509a-9ddd-b340440402d0 |  | note | Certifying Documents and Frequency: Photos etc as evidence
label | ef29462e-c499-56f4-9f7e-5b0e80a21bde |  | note | Supervisor, Foreman or Subcontractor: P
label | d7176401-7cb7-590e-84cb-28f32e838fe3 |  | note | Project Manager or Delegated Person: R
label | fc166f99-ee8e-55c0-affe-18d25512da3d |  | note | Engineer’s Representative: R
text | 5d76e8f2-19f5-518e-9e3b-346b8a9eb2fc |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | 5 - Welding of fittings using PE or mechanical connections.
label | 4f82f138-f4bc-50ff-8250-43ab126804f3 |  | note | Activity Task: Supply of Material
label | 97d64c69-8817-5a6a-862e-277b7b574f96 |  | note | Acceptance Criteria: Certification from manufacturer that materials comply with the manufacturer’s specification
label | 351466d4-8198-5358-9660-a28e960a2d7e |  | note | Certifying Documents and Frequency: Delivery Dockets,
label | 3b246fd8-dc33-5021-9ee8-93fd8883bb8c |  | note | Supervisor, Foreman or Subcontractor: W
label | 54c7266d-d3a9-519d-8154-bbcdebaf52bb |  | note | Project Manager or Delegated Person: W
label | 0ddcb7a6-4f38-597c-af40-b0a3fc328204 |  | note | Engineer’s Representative: R
text | 2a262608-c8e1-55ad-abaf-9386064f30c2 |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | 5.1 - Welding of fittings using PE or mechanical connections.
label | e82851e2-1cd8-52f9-bf8a-7fba244b0221 |  | note | Activity Task: Construction of welds
label | ab4a1408-a63d-53e8-8e97-892804c69eac |  | note | Acceptance Criteria: Test Weld to be sent for testing at qualified laboratory, tests to be carried out. As required.
label | db0e3121-4336-580f-a971-fab920a94b04 |  | note | Certifying Documents and Frequency: EF Welding information to be provided with test weld, copy of information to be kept on site in QA folder, Results / Feedback to be supplied to WDC.
label | a4c176bc-77c4-52d0-9bc6-57aebcd4b416 |  | note | Supervisor, Foreman or Subcontractor: P
label | 71c9b0a8-d02a-5b4f-896e-af762e75bbda |  | note | Project Manager or Delegated Person: W
label | 96327c0f-429d-52bb-bd90-07158b57d861 |  | note | Engineer’s Representative: R
text | f78b3f94-fb09-5098-8896-e20596c6d120 |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | 5.2 - Welding of fittings using PE or mechanical connections.
label | 47e9ee5c-57c3-5f02-9721-51a175bd28e5 |  | note | Activity Task: Construction
label | 47d0c7e0-d064-5a8e-a0f9-de056e04f96a |  | note | Acceptance Criteria: All weld parameters are to be recorded for each separate weld as well as the welder, weld number, location, date and time of weld and air temperature All butt welds to be undertaken in accordance with the manufacturer’s recommendations.
label | ed61bb8c-b5b9-5064-ae83-c6aa0f5a50a2 |  | note | Certifying Documents and Frequency: EF Weld Inspection joints QF037 Approved Welding procedure Welding machine certified and calibrated with data logging capacity. Sub-contractor to supply Data Logger information etc for butt-welding.
label | 8eb7c728-a70d-533d-a6f4-aee45b658aae |  | note | Supervisor, Foreman or Subcontractor: P
label | 7c77bbf9-e84b-5f90-89a1-d886ced64c1d |  | note | Project Manager or Delegated Person: R
label | 8f56154f-bd7b-5d4e-9a14-61f5b2caef67 |  | note | Engineer’s Representative:
text | 438767b9-e8d5-5ec3-a6f9-216ed9d320f0 |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | 5.3 - Testing of butt Welds
label | 73b06fe9-cb89-5bec-8202-6539bcf1f47d |  | note | Activity Task: Butt Welding Test
label | cd6b7fae-7ec7-5caa-88a4-6f9de5df90b4 |  | note | Acceptance Criteria: Tests to be carried out to see Ductile or Tensile Failure as per WDCEES specifications.
label | cee24651-b5c2-5bc5-9460-d8e566ef2003 |  | note | Certifying Documents and Frequency: Test Results
label | 690babd0-fad4-57a0-9aa0-41f7166cc2ef |  | note | Supervisor, Foreman or Subcontractor: P
label | dda62e02-f36b-569f-a966-d38a012d740d |  | note | Project Manager or Delegated Person: P
label | 99ca9bca-dac7-5c8e-a833-ffe3c4441785 |  | note | Engineer’s Representative: H
text | 735be6e9-9f74-5485-887e-c59305eef9a8 |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | 6 - Testing and Commissioning
label | 3808a0fd-b092-5f30-b84b-8857ef8696ab |  | note | Activity Task: Testing of the new pipelines and commissioning
label | f5e6b7f7-5aa6-55b7-9108-dfcd8685e728 |  | note | Acceptance Criteria: Pressure Tests/ Holding Tests
label | d692dd1c-8f02-5437-a79a-709db2c07d0f |  | note | Certifying Documents and Frequency: All tests to be recorded using Check sheet QFH-003
label | 737ccf43-ef98-50f3-90a9-d4250a397d11 |  | note | Supervisor, Foreman or Subcontractor: P
label | e334d504-31fd-51c4-a5ed-e39b72df6592 |  | note | Project Manager or Delegated Person: P
label | 625f5d49-df33-5438-93c8-79f94bdc0587 |  | note | Engineer’s Representative: H
text | 1b4f8ccd-ab4e-5467-ab91-394f2e333d88 |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | 6.1 - Testing and Commissioning
label | fcb9c674-31fe-5fec-947c-f33f45641375 |  | note | Activity Task:
label | a07dd0eb-0964-54b6-a66f-b41a9bd0d36b |  | note | Acceptance Criteria:
label | 0df6a2e8-ff97-541d-883d-259056799cac |  | note | Certifying Documents and Frequency: Engineer invited to witness testing while test is to be carried out. Data logger to be attached, all data to be exported and provided to WDC
label | f5f503ed-d14a-5d55-b013-cb396c5cd0ca |  | note | Supervisor, Foreman or Subcontractor: P
label | f635bdeb-7f92-5bdf-acab-5b0c5d154941 |  | note | Project Manager or Delegated Person: P
label | c929baa1-b9d0-5296-b711-2abd9f9c11ec |  | note | Engineer’s Representative: H
text | 2bd6e54a-d003-5e27-b80e-b65e3d87d125 |  | textbox | Date Completed: