## Master List Templates
Id | Type | Name | Values | Prompting Name
87dbf723-3c96-462d-bf66-e455fedf5f06 | checklist | ITPS-209 Deluge Commissioning |  | ITPS-209 Deluge Commissioning
8eea13d2-6902-4b58-986a-3c9ed55875f7 | section | Details
7817e386-1f03-4300-b563-044adf24669d | checkpoint | 1. AREAS PROTECTED
0f26962a-7b53-515d-b6b3-22f5c1ae0bbc | note | CIBSE W5.2 State of the System
f6c8df84-0587-588f-a3c6-5fb3d4f3a162 | note | AS2118.3
579b67c5-1d15-5b2f-bfaa-4893198ed8bd | button | Have you ensured areas protected do not exceed 300m/sq per valveset? | Yes, No
69a0a452-eee7-5400-b4c3-1d18d8f626f5 | note | Add Photo
e13b2f41-965d-47fe-b293-b669ac827608 | checkpoint | 2. PRESSURE TEST
b77b8a3d-9734-5cad-b586-4c6c8f11065c | note | CIBSE W5.4.1 Pressure Testing
b5dd3634-0e61-5e2b-a53d-78f9fd902b38 | note | AS2118.1
088ba1e8-65f5-5bab-b519-e8d61450a0f6 | button | Have you completed a pressure test as per ITPS-203 for each deluge system? Note: Where open sprinklers are used ensure all heads are plugged prior to pressure testing. | Yes, No
b4e01887-62fb-5ccb-9378-5e7c57b095e0 | note | Add Photo
1ae11dd8-82e8-4a6a-9c03-a5c7b3ce35dc | checkpoint | 3. EQUIPMENT TESTS - SYSTEM FLUSH
728f2aca-b05d-5e3e-89ac-d818871303ea | note | CIBSE W5.5.2 Flushing Procedure
0851b159-f1c6-5973-977a-cb3586eb9363 | note | AS2118.1
543b63ae-49e1-55ad-b2ff-593c4e0fb7af | note | Complete the following PER valveset and open sprinkler head:
ec26301e-47b5-50d4-972e-b4d24505bd78 | note | 1) Flushing of each open sprinkler head to ensure debris is removed.
9c12745e-e70d-59ce-abb7-ac762de00e99 | note | 2) Setup filtration mesh and water bin at each open head off each system (is there are a large number of heads then separate system by plugging each head).
1903c679-9e94-5e4a-8788-0686e90ca55f | note | 3) Let water flow through pipework onto filtration mesh
29b7d2ca-0540-5357-b85d-d2214726c8f2 | note | 4) Once water is clear from debris shut off water and return system to normal.
79de03cd-4a66-53e9-a70f-2b83859bb91b | note | Take photo per deluge head and record deluge head/s location:
c62db6fb-5360-49e9-b201-c73c7170ea52 | checkpoint | 4. TRANSIT TIME TESTING
c61592c5-2057-5eaf-873e-fdc3c8791cd9 | note | CIBSE W5.6.2 Mechanical Checks: Automatic Control Valves
655f698f-f7f9-5633-8f34-22bd130f6610 | note | AS2118.3 Cl 2.9.1
dca9d2ad-e275-576e-b1fe-5f22044bf59a | note | Complete transit time testing
24da5ecf-6c2c-59bf-886c-e935fd082ba3 | note | Test of the deluge valve to ensure the transit time does not exceed 30s from the valveset to the remote deluge head.
ca7a5928-1b84-55d6-9e89-7a1559ca7660 | note | Add photo of results of transit time.
3a04b841-ac9a-4574-b21d-5e715db680a8 | checkpoint | 5. RETURN TO NORMAL OPERATION
0a93862e-2b51-5279-931c-3b3f60087f9c | note | CIBSE W5.6.2 Mechanical Checks: Automatic Control Valves
83d068c2-f166-5a5a-950f-7dba0ba9b53f | note | Are all open sprinkler heads re-installed where previously plugged?
eb006e7b-ed6a-56f8-8e5a-e7b3b4e19414 | note | Have system valvesets been returned to normal condition (or approved condition where construction still occurring)?
b0c22b87-45d6-5de6-a6c7-d46ea7ff4bc3 | button | Have water filled bins been emptied as per principle contractors requirements? | Yes, No
e3e5c507-051b-5c83-9f98-b95a7e82ef8d | note | Add Photo
f4e4ad9b-dd6e-4b4c-9955-2e35567b6483 | checkpoint-no-value | GM Fire Sign Off
8b042243-f6a4-4082-8826-804c333eb1ce | signoff | GM Fire Sign Off
44ef14c4-0907-4701-b770-28081a0f23f3 | checkpoint-no-value | Principal Contractor Sign Off
85d7a163-ece4-4347-b7b8-2cd6e059e22b | signoff | Principal Contractor Sign Off
287159ad-2b09-44b6-9445-76962cf3474e | checkpoint-no-value | Consultant Sign Off
0531c335-d3e4-4752-a6dc-20e7e02a75ed | signoff | Consultant Sign Off

## Project Checklist Templates
Id | Type | Name | Values | Prompting Name
c5dc7d7c-df99-5ec2-a589-b436df406a75 | checklist | 010SAF_08 SWMS |  | 010SAF_08 SWMS
a1c9d02b-1fdf-5e00-bcb7-56aeec761826 | checkpoint | 1. INDUCTION - Attach your signature to confirm you have completed the Principle Contractor's Induction.
d39621b2-57eb-545c-b19b-913b988ebada | signoff | By signing I confirm I have completed the Principal Contractors induction.
93e7a6a9-2417-5a63-a628-5bbbe7c40d86 | checkpoint | 2. ALL STAFF
cbaa5304-d926-5145-abea-643403fc7075 | note | 003G Using Platform Ladders
4c0dcfe7-d8a0-5008-bd8b-d7bc54f1ac2a | note | 004G Inhalation of Respirable Crystalline Silica
1117a6d0-9a4c-5b98-b403-d22a7b5ad3a6 | note | 005G Working at Heights
68979298-f5d8-548e-baec-8741d208ed87 | note | 006G Working at Heights Rescue Plan
1e1b9f0c-d012-59f5-9748-6f1fbc413551 | signoff | By signing I confirm I have read and understood ALL the SWMS documents listed above. I have reviewed these documents onsite with my supervisor and I have signed the hard copy.
d3e29984-ceb2-515c-9230-7a6de1161462 | checkpoint | 3. WET FIRE TECHNICIANS
b4e0d11c-383a-5193-a4d8-06886c652d7b | note | 019T Pressure Testing of Pipework
543f3f86-57b8-5b16-b786-9b1a07dba3bc | note | 020T Sprinkler System and Associated Pump Test
e8307916-4807-52bf-87e5-102669e43c3f | note | 021T Hydrostatic and Flow Testing of Pipework
b9ed5514-0cad-5767-9bc2-787d09c4b91b | note | 022T Fire Rating
3eda0a35-e17c-5ffa-8f13-550cbe45fa28 | note | 023T Fire Alarm and Emergency Warning Systems Testing
6a966737-d7b0-592b-adaf-4fd6c5c1ce28 | note | 024T Commissioning and Testing of Hydrant System and Booster Area
ec96f917-5f59-57b4-b51e-789fed1bc3e7 | signoff | BY SIGNING I CONFIRM I HAVE READ AND UNDERSTOOD ALL THE SWMS DOCUMENTS LISTED ABOVE. I HAVE REVIEWED THESE DOCUMENTS ONSITE WITH MY SUPERVISOR AND I HAVE SIGNED THE HARD COPY.
cb6326be-0982-5008-a0f6-df63d2b7f5a8 | checkpoint | 4. SWMS - DRY FIRE TECHNICIANS
5d11d398-a985-5a6c-aeb6-18ee293dc7c2 | note | 008I Removal of Existing Fire Alarm Systems and Devices
92d6eeb4-8277-5022-83a0-fc89644f8bed | note | 009I Removal of Pipework Fittings
52103321-2daf-5ff5-83c8-2ade86fd2490 | note | 010I Fire Alarm and Warning System Rough-in
8205c84e-07ea-575b-bae8-d3015acb0b02 | note | 011I Fire Alarm and Warning System Fit-off and Installation
884a1c0d-249f-5a69-b8f2-2e03f9760652 | note | 012I Installation of Fire Alarm and Warning System Cabling
61c0ba51-1491-512b-936c-ac2c0f143740 | note | 013I Installation of Pipework and Fittings
c29e79e2-249c-55ba-b869-187073053c35 | note | 014I Installation of Fire Control Panel & Emergency Warning Systems
12c89be3-5c80-51bc-be0f-9f94b3c520b4 | signoff | BY SIGNING I CONFIRM I HAVE READ AND UNDERSTOOD ALL THE SWMS DOCUMENTS LISTED ABOVE. I HAVE REVIEWED THESE DOCUMENTS ONSITE WITH MY SUPERVISOR AND I HAVE SIGNED THE HARD COPY.
d9fadd81-64e2-558b-bb97-5297d52972c4 | checklist | ASSESS-001 Risk |  | ASSESS-001 Risk
8111ace1-1386-5c1f-8290-3df28e3c8d3f | section | Details
1c657631-910b-56b0-9af0-2d9a539b2537 | checkpoint | Assessment Details
c5de9c41-d1f8-560c-8ad2-fbc0b3413782 | note | Use this form to document the risk management process for a single generic hazard.
005d1f0d-2484-50cb-baf9-eb4eb1a44015 | textbox | Work Area:
10e81421-8b3f-590c-8e71-407a29ad32c6 | date | Date of Assessment:
d5709b78-6e7a-5e77-bed0-726b44d8cdef | textbox | Name of Assessor(s):
d7031743-0b91-57c4-b35f-f17efd3658cc | textbox | Position(s):
115c97b5-8445-5541-916c-66b0b8ebdc28 | textbox | Incident Ref. No:
270f8fc3-f5f3-5606-80eb-fc2c80ae4f95 | checkpoint | Hazard Identification
77da4f53-d3a7-5107-9fbe-117e16f13ca8 | textbox | Describe the Hazard:
bfd5195d-87aa-5c40-ac91-f0b3a6ea86bc | checkpoint | Risk Assessment
04604ad8-d203-5403-9f28-7e35a2d550ea | textbox | What harm could the hazard cause?
951d2f55-2fe0-580d-ae7b-639c96cc5b90 | textbox | What is the likelihood of this happening?
daaa7575-ae9a-5135-a5e1-8342676e6e23 | textbox | Persons at risk:
629736c9-e046-5570-9786-06b903ddd8eb | textbox | Existing control measure:
23757a9a-d67e-536b-a993-f90edc47ae86 | textbox | Consequence:
f6b0f80e-5ff0-5a13-b299-a1cb8c38c115 | textbox | Likelihood:
881ee5cb-4d01-572a-bfea-cffd30972fbd | textbox | Outcome:
32563b01-0feb-5e94-999f-2bc4f92e2c20 | checkpoint | Control Measures
b86eaa2b-7e40-5506-b229-0816cf867368 | textbox | Elimination:
65051202-a0d1-57a2-9ffb-98b560a04d5a | textbox | Substitution:
9c57ed7f-108c-5aab-ba42-06cd18c7e0c9 | textbox | Isolation:
cfab3bb1-2c1a-5925-b496-c1f0fbb110be | textbox | Engineering:
8274926c-9d7f-5e6b-ba59-e8a93b9ab844 | textbox | Administrative or PPE:
3e1b8770-840e-520b-b2c7-2d4b303132c3 | textbox | Preferred control option:
71245745-e635-5d28-b0f1-51a28405fcc8 | checkpoint | Implementation
ad015995-80d6-51c6-8c5e-87c4860e5b3b | textbox | Associated activities:
15660b94-9774-5ae3-bb4a-2f71331fd267 | textbox | Resources Required:
9b882b1a-4757-53d1-960c-25880c5cd18c | textbox | Person(s) Responsible:
ff0f7a4b-5f46-5471-b1df-4283f24beb0d | date | Scheduled Review Date:
7717528b-ba68-53aa-a357-393c48e0a282 | signoff | Signature
dc6cb437-46cb-507c-892f-0515049a836f | checklist | ASSESS-002 Manual Tasks Risk |  | ASSESS-002 Manual Tasks Risk
8111ace1-1386-5c1f-8290-3df28e3c8d3f | section | Details
1c657631-910b-56b0-9af0-2d9a539b2537 | checkpoint | Assessment Details
9fc17e11-c766-5d8e-a0a1-595e2727693c | note | This assessment identifies how to manage the risks associated with hazardous manual tasks and control the risks of workers being affected by musculoskeletal disorders as per the code of practice under section 274 of the Work Health and Safety Act 2011 (the WHS Act). Use this form to help identify and manage risks of hazardous manual tasks.
f9a1401e-9b7d-54a3-a5f3-1a5ec1b36faa | date | Date of Assessment:
85d05fde-c553-5de5-b958-85f266fe8a06 | textbox | Name of Assessor(s):
6d6b2491-8d75-500e-be86-08b6e2339ca3 | textbox | Position(s):
db403942-7a06-5fae-844b-fb5598a0d878 | textbox | Incident Ref. No:
58267725-2c6f-55fe-83b6-0579eb36ea4e | checkpoint | STEP 1 What is the Manual Task?
1ed84ad7-7ec3-5db1-ab77-3256292a12f2 | textbox | Relevant worker(s) to consult:
fd511a02-656a-5e17-afb8-0967720a5f57 | textbox | Name of task or activity:
22132838-2ef5-58b7-943c-b8ce04be8f8e | textbox | Location where task occurs:
54ec76f5-56bc-52b1-915e-89a86091bd77 | textbox | Who performs the task:
4a688ff5-309f-5da2-90ce-b7f62b4ac2b7 | textbox | General Description:
bf2b5766-0a58-58a5-9304-cb818f3230f5 | checkpoint | STEP 2 Is the Manual Task hazardous?
62fe4a6c-5bb4-5593-94dc-4143605d07c4 | note | Hazardous manual tasks can result in musculoskeletal disorders (MSDs) such as sprains or strains. Work through the following to determine which postures, movements and forces of the task pose a risk.
c059cd34-2879-5458-bf1d-e0cf42a327f8 | note | 1. Does the task involve any of the following risk factors?
f2f32f92-4f32-57e8-be72-6bac9b1f2ee5 | button | Repetitive movement | Yes, No
b2d039ea-e557-5406-bc9e-2dfa9f6dd3e1 | button | Sustained or awkward postures | Yes, No
e137775e-03ca-5eb6-b90c-a028c49d5461 | button | Repetitive or sustained forces | Yes, No
4f284663-da7c-5bca-9046-8ad48e4bc7fc | note | 2. Does the task occur over a long time?
79837c5f-a3ad-53bb-bcfb-2313a7fb3e26 | button | More than a total of two hours over a whole shift? | Yes, No
66c0e6a2-a128-5caf-8631-f98b0dac3061 | button | Continuously for more than 30 mins? | Yes, No
382fe9ba-ee00-5826-a9fb-284301486a74 | button | 3. Does the task occur over a long time? | Yes, No
d89decc6-45ec-5668-be06-c86a12733756 | button | 4. Does the task involve vibration? | Yes, No
8628cbcb-f8f2-5530-8eb9-ca6666961676 | note | 5. Is there a Risk? The task involves a risk of MSDs (e.g. sprain and strain) if you answered ‘yes’ to either:
262f25de-296a-5b7f-8056-23ada1febde9 | tickbox | Question 1 and 2 (above)
52982c8a-0d6c-51f7-8391-abf77aa8975e | tickbox | Question 3 (above)
97201e8e-1b96-5812-b3c8-07d6c3859270 | tickbox | Question 4 (above)
b60d13f6-556e-57ec-aa9d-1515d35a2438 | note | If you ticked anything in question in Question 5, continue to Step 3.
8425d4a8-c62a-549b-99ba-b19517badde3 | note | Additionally, if you answered ‘Yes’ to Question 4 the task may be a risk and will require further investigation.
43bb97fe-9131-5be9-be82-2660ffb39a19 | checkpoint | STEP 3 - What is the source of the risk?
848cab31-3f09-50df-8896-1d00a71bbb0e | note | These are the things that are causing the risk and may be changed to eliminate or minimise the risk.
9ce694ef-7cda-52c0-bd0e-795ab075087d | tickbox | Work area design and layout: workspace available; design of workstation, furniture and equipment.
24531638-1275-5996-9ad1-d56ddfc2f645 | tickbox | The nature, size, weight or number of things handled in performing the manual task.
5ae9f162-adeb-518a-9432-8df53a873352 | tickbox | Systems of work (e.g. pace and flow of work; resources available; maintenance).
73cd5602-d778-5858-86b0-de4464293911 | tickbox | The environment in which the manual task is performed (e.g. flooring; obstructions; lighting; hot/cold/humid environments).
75306ffa-8cad-5fb5-8c60-4770efcfbc4e | checkpoint | STEP 4 - How do I control the risk?
f1034ca2-31f7-56a8-bc18-820bea142cf3 | button | Can the task be eliminated? | Yes, No
28ec483b-bfdf-5378-9f90-b3808a8a487e | button | Can you change what is causing the risk (the source)? (e.g. change the work area; alter the size of loads; use mechanical aids; manage environmental conditions; use adjustable equipment; implement preventative maintenance program). | Yes, No
e00c64b8-eb68-55e2-8797-9442fb48c3de | textbox | If 'Yes', provide detail:
e6a359f7-d5d3-5889-afd0-a3ea528f6a73 | button | Is training needed to support the control measures? (Training needs to be task specific, noting that training in lifting techniques is not effective as a sole or primary means to control the risk of MSDs.) | Yes, No
90124d3d-701b-5037-baad-ecb2d73325b0 | textbox | If 'Yes', provide detail:
249717bf-db57-5fb4-b61b-9f7678983512 | checkpoint | Implementing Controls
27131080-4c86-5176-bf68-a92efdc1237a | textbox | Name of Responsible Person:
1dcc6c1c-6b77-5d0f-8eb5-8daa5776273e | button | Responsible for: | Approving, Implementing
5ab0ac1f-d347-5504-88e7-34c413ffeb0c | textbox | Name of Responsible Person:
b25c3136-843c-5b64-9e93-9ec063c57ff8 | button | Responsible for: | Approving, Implementing
762070cc-4ad8-5366-b50e-34949b5ee185 | textbox | Name of Responsible Person:
bfa37730-efd5-5fe8-bc8b-fbf8fc413e9f | button | Responsible for: | Approving, Implementing
4d12691b-3420-53b1-8f7d-09963f0de2eb | textbox | Name of Responsible Person:
43957d02-ee05-59db-b939-654283487548 | button | Responsible for: | Approving, Implementing
89334ebf-57ec-5f05-8b4e-750b91a0dc81 | signoff | BY SIGNING I CONFIRM I AM AWARE OF MY RESPONSIBILITIES AS OUTLINED IN THIS RISK ASSESSMENT
1ac85fbd-c1e0-52f8-a16f-a7d8e29a8854 | checkpoint | STEP 5 - Review the Controls
defe51c9-b5b4-5c58-83a5-6464c75f2a87 | date | Evaluated on(date):
9b252f75-c796-523c-a3a9-0325117bc88b | textbox | Name of Assessor(s):
2fec0e86-b3b2-5b66-b40d-e93944944a37 | button | Consultation undertaken with relevant workers and others? | Yes, No
b54e729a-c715-5ce3-84c8-b35ad6b661a8 | button | Have any other risks been created by the controls? | Yes, No
e7c0364a-0b94-5388-9485-894ef6280a09 | button | Have the controls implemented reduced the risks? | Yes, No
f68dd399-de50-5948-bea1-758fa0255115 | button | Can further controls be implemented to minimise the risk? | Yes, No
1f79f722-3177-55f3-9a29-259b2c38a80b | checklist | ASSESS-003 Hazardous Chemical/ Dangerous Goods Risk Assessment |  | ASSESS-003 Hazardous Chemical/ Dangerous Goods Risk Assessment
8111ace1-1386-5c1f-8290-3df28e3c8d3f | checkpoint | Details
682b1c68-be13-59ee-8fbd-c82abe59e3a5 | textbox | Hazardous Chemical (product name):
074cc89c-0b59-53cd-b7a0-d81e117aca2d | textbox | Hazardous Chemical Reg Item No:
6b29d30d-519d-5115-9dd8-4850919b5258 | textbox | Use:
eec44df0-883b-5db0-a668-e111f5465eb4 | checkpoint | Nature of Hazard:
70c4f5bc-f5f1-5818-aa2a-7ce50dfed36e | tickbox | Toxic (Poisonous)
a29ecaa7-310d-5bf2-a493-0239f6f16f57 | button | Route of Exposure: | Eyes, Skin, Inhalation, Ingestion
a0e3032c-bcf4-5a7c-9c35-af1773d480b4 | tickbox | Carcinogenic (Cancerous)
af1f85fb-adde-56c5-a072-ca183475da96 | button | Route of Exposure: | Eyes, Skin, Inhalation, Ingestion
d9ced72d-d387-55f1-b6a0-cfc04cd346df | tickbox | Teratogen (Harmful substance that could affect abnormal prenatal development)
2b9fc4de-da6e-5233-9003-4c2adaa70b7c | button | Route of Exposure: | Eyes, Skin, Inhalation, Ingestion
554ddd9a-f357-50ea-9d69-bc7a8e3e6d77 | tickbox | Sensitiser (Reaction to an antigen, such as pollen)
a6b6fa74-c3a8-5da1-a82e-fbc337a07288 | button | Route of Exposure: | Eyes, Skin, Inhalation, Ingestion
fd9b4ad7-86c7-522f-8b8c-83cdac3a34b1 | tickbox | Mutagenic (Capable of mutating DNA, such as radiation)
8e9eab69-eb8e-5142-a173-092a5212890c | button | Route of Exposure: | Eyes, Skin, Inhalation, Ingestion
bdd1e751-1e9e-554f-a6d8-cd05dcf89a94 | tickbox | Irritant (Inflammation of the skin, eye or respiratory system)
56baa314-e83b-5a19-9ccb-2040dbe49233 | button | Route of Exposure: | Eyes, Skin, Inhalation, Ingestion
f01be884-1f36-564f-83ed-a6a11029ffd0 | tickbox | Flammability (The ease of which a substance will ignite, causing fire or combustion)
fdc51005-b1e5-5cb7-8fea-b25ec86bf664 | button | Route of Exposure: | Eyes, Skin, Inhalation, Ingestion
c5299fc2-0138-5c3e-9df0-fdb6f6a23c55 | checkpoint | Risk of Injury
91e7ea8c-b187-5693-99c7-6bfd82f09900 | button | Risk of Acute (Short term) Injury: | High, Medium, Low
faec8d40-70ad-56eb-980d-0257dd577b1d | button | Risk of Chronic (long term) Injury: | High, Medium, Low
6adca422-e108-5631-9168-8f36735799d3 | checkpoint | Controls and Requirements
0cdc26cb-cc3c-5d53-903e-e3f7799703aa | textbox | Control Measures to reduce exposure i.e. change to a safer product, ventilate area, (P.P.E.):
73baf6dd-879d-56cb-917d-a4c1dd24e0f1 | textbox | First Aid Requirements and Storage Requirements:
42c21dbd-9bff-5051-bd1f-f936237b2320 | checkpoint | Signoff
f6e6ad58-755a-5ec6-ac1a-b3db6c24bfc3 | signoff | The persons listed below have been consulted in this risk assessment, understand the hazards associated and agree to use the control measures identified above to carry out the works safely and in a manner which protects themselves, others and the environment.
7a2e19d4-a232-5ccb-9e9b-f9c2132fc0a5 | checkpoint | Assessor Signoff
d0aabc79-7a66-528f-976e-31f5a7db0456 | signoff | BY SINGING I CONFIRM I WAS RESPONSIBLE FOR CONDUCTING THIS ASSESSMENT
733ea029-88c9-5283-953b-73307084165f | checklist | ASSESS-004 Plant Risk |  | ASSESS-004 Plant Risk
8111ace1-1386-5c1f-8290-3df28e3c8d3f | section | Details
5011c755-395d-598c-bc65-ea69efabb143 | checkpoint | 1. Competent Peron(s)
6008f508-f090-5c75-8d82-342c8741b05d | note | This familiarisation checklist should be completed by a Site Supervisor or Site Foreman to verify that the workers involved in the operation of Plant Equipment/ Mobile Elevated Work Platforms (MEWP) can demonstrate their ability to understand and operate the MEWP functions in accordance with the manufacturers operating manual. This familiarisation checklist must be verified by a competent person who holds the equivalent licence/ ticket required for the type of Plant Equipment/ MEWP to be operated (e.g. Boom lift/ Scissor lift)
a0108c45-98bf-5be2-8de2-e004e81c889f | textbox | Your Name:
ec798eea-f0e3-5a69-8c7e-a4673dbb3de9 | note | Your Licences / Tickets:
2068ee3b-a82e-5bbb-9746-4a219bce44a9 | tickbox | WP High Risk
7a31d89d-62f8-589e-b54a-37d01613bae8 | tickbox | Boom Lift
1c7b47b7-76c1-50cf-bfa8-faf15ce1535b | tickbox | Scissor Lift
e79442f8-935e-5d23-8f62-7ecd22f488ab | tickbox | Vertical Lift
9ce8c9e8-8e1a-5d54-96b2-1b67f53e3bbf | tickbox | Other
dd85d513-ed0e-5967-886f-09fe09edc053 | textbox | If 'Other" please specify:
c06fe721-a6e8-585c-ad93-6752e11d8265 | checkpoint | 2. Plant/ MEWP Details
efe2f773-44ba-5241-bb6d-548c08a1e716 | textbox | Make and Model:
d659d638-696c-56fc-9c93-9e50b3befdf1 | textbox | Type (e.g. BL>11m, BL<11m, SL, VL):
6b0e5610-cf37-5886-aa78-b8bc2aea3ba0 | checkpoint | 3. Employee Competency
c4d0cc42-7690-5ca6-80bc-61758bbe80dc | textbox | Name:
4843e054-50a0-56e2-ba84-61e1b03a6906 | note | Role:
89737976-6efc-52c0-bc3a-3f19b2a2d506 | tickbox | Operator
06d156fe-0579-5334-ae67-6eb760055bfa | tickbox | Spotter
775a5b4a-e605-5b9f-a786-803904f49126 | note | Licences/Tickets Held:
6d2a222f-80c5-5a3d-a892-1f2a17b0f0b7 | tickbox | WP High Risk
a45e7b44-2675-525e-bfa1-8bbd0d93f70c | tickbox | Boom Lift
df02dde4-9f96-5eed-8026-1cae025cbb2d | tickbox | Scissor Lift
e9609037-2a55-5d22-888a-ade8915f8581 | tickbox | Vertical Lift
06ebc66d-119e-58a4-8c6d-3668b83861ad | checkpoint | 4. Employee Competency
f28a3aad-8fd2-57ec-a107-b922f319121f | textbox | Name:
ea2efec7-5206-5deb-8a5a-a1b23da965d3 | note | Role:
0ebf6c74-2e86-5fb3-b0c4-24e114c4da13 | tickbox | Operator
d1b97ff0-d5fb-5520-91ea-209a06a7f48e | tickbox | Spotter
2cdb2167-0f98-599d-b35e-cb50ba4f92b8 | note | Licences/Tickets Held:
62b101db-568a-5f7f-8d9d-7409539693b5 | tickbox | WP High Risk
a80da644-ff1e-5a6d-9b82-dfa8680bfafc | tickbox | Boom Lift
3e439241-a650-5f7f-af0e-70745bb2b7f6 | tickbox | Scissor Lift
2b9ec7e6-a1f0-55d4-9cd3-29260b8ef428 | tickbox | Vertical Lift
3ef8e758-7384-5d13-8fa3-292a5f04a9d8 | checkpoint | 5. Employee Competency
75dc3649-1aa9-59b9-983a-127639717ca9 | textbox | Name:
8b1aeb6f-23ea-5fcb-9672-016fc7ee3ea0 | note | Role:
2ac2daed-d68c-5a44-b140-1334c63fc2ca | tickbox | Operator
2a68994a-f21c-54e5-ba51-7ebd10965134 | tickbox | Spotter
bcc2d129-a6cd-5d0b-9cbc-355ecfcd5c07 | note | Licences/Tickets Held:
c6c6dfcc-597f-591b-a66f-b26b5f0d77df | tickbox | WP High Risk
e48f4801-fa3f-5dac-b4c3-54b413a34cb3 | tickbox | Boom Lift
eb3e4533-243e-5340-8c41-8b2b149f446f | tickbox | Scissor Lift
27f3cc0b-5823-5a7c-9740-688d8500fda9 | tickbox | Vertical Lift
0db35e59-5266-54bd-bc6b-7ababdb43cef | checkpoint | 6. Declaration (to be completed by competent peron(s) noted in Section 1.
cdf15557-25cf-5a50-8885-40242a2ebb29 | button | All 'Operators' hold the appropriate licence/ ticket for Plant/ MEWP | Yes, No
7ab43cd6-82eb-565e-a480-419b1b307561 | button | All 'Operators' understand the operational controls and emergency functions | Yes, No
f82c6da8-a20b-55fd-a181-ab576becb15e | button | All 'Operators' are aware of the logbook and pre-start requirements | Yes, No
3f0a42fa-fc1d-547d-80f8-d00c0d969ad8 | button | All Ground Support understand the emergency functions | Yes, No
6abf61e9-cb4b-5f47-ae38-70ed2a8b2fdc | button | All GM Fire employees on site have participated in an emergency drill | Yes, No
8345e406-faa6-5d37-be16-d60307803e44 | button | All GM Fire employees have signed onto applicable SWMS | Yes, No
9899d9ec-b306-5aed-bbc5-b1347ea6537c | signoff | BY SIGNING I CONFIRM I HAVE ALL PERSON(S) LISTED ARE COMPETENT TO OPERATE THE LISTED PLANT/ MEWP ON THIS SITE.
01393b7d-fb14-536d-a598-0ba8a2dd5293 | checklist | ASSESS-005 Confined Spaces Risk |  | ASSESS-005 Confined Spaces Risk
8111ace1-1386-5c1f-8290-3df28e3c8d3f | checkpoint | Details
37b6bb45-8b12-56ae-8f7c-06cfe607308f | note | Use this form to document the risk management process for a Confined Space.
d23b264c-b4fc-5feb-bfdc-85b28ed9fb2e | date | Date of Assessment:
835eed32-0c8e-5e96-a1aa-7599ce2d8e7a | textbox | Name of Assessor(s):
0903b9d0-901c-52ff-971a-b68cc0860625 | textbox | Position(s):
270f8fc3-f5f3-5606-80eb-fc2c80ae4f95 | checkpoint | Hazard Identification
48db7c9d-d247-58f4-925b-7d350519ad04 | textbox | What Hazard/ Risk is associated with the task?
94b108f3-39f6-57df-b939-b28b28b68f4c | textbox | Planned control measure to remove/ minimize hazards/ risks
56676e03-ce74-56fd-b183-43c573f5ff4f | textbox | What Hazard/ Risk is associated with the task?
5357fc2d-8e16-534b-8a3a-c657f07dbaf0 | textbox | Planned control measure to remove/ minimize hazards/ risks
54945473-1059-541a-a50a-17ce6cc6cc5a | textbox | What Hazard/ Risk is associated with the task?
7070b842-061d-58f7-94db-4e60845c53a8 | textbox | Planned control measure to remove/ minimize hazards/ risks
37b9fc21-61d9-5619-94db-39fe61338a34 | textbox | What Hazard/ Risk is associated with the task?
d6d2c5a2-1d5a-5904-b6a3-78c381e9689e | textbox | Planned control measure to remove/ minimize hazards/ risks
821a9c8a-949c-59d7-86cf-6a9f93c97f38 | textbox | What Hazard/ Risk is associated with the task?
657faf9a-c4cc-52d9-ac9d-2ec8554283ee | textbox | Planned control measure to remove/ minimize hazards/ risks
520f3973-2a3e-554c-9da3-fcd0d6905a7f | checkpoint | Review
53d51c99-e2be-5550-86a6-99fe6ed28def | button | Does the Risk Assessment Identify that confined space work is involved? | Yes, No
42684e86-a4e8-5ecb-9abc-26f5d938dca2 | note | If YES the Confined Space Work Permit MUST be completed
e1700a0b-d345-5121-92d9-d5c9ab6cc16f | note | NOTE: EMERGENCY & RESCUE PROCEDURE: Where an accident occurs which requires that an emergency rescue be attempted, the standby/ rescue person is to immediately contact EMERGENCY SERVICES on 000 for assistance.
7a2e19d4-a232-5ccb-9e9b-f9c2132fc0a5 | checkpoint | Assessor Signoff
075bc9a7-5792-516f-8e66-fa5783e63bc2 | date | Scheduled review date:
946f9c2d-1950-57b6-981a-43e43c738227 | signoff | BY SINGING I CONFIRM I WAS RESPONSIBLE FOR CONDUCTING THIS ASSESSMENT.
39765b41-0baf-523a-97b1-810de6665326 | checklist | ASSESS-006 Job Safety |  | ASSESS-006 Job Safety
5e25be48-4354-51fa-a917-1881487cb8a0 | checkpoint | Client Details
80bd7a51-a4a7-5780-a8f5-9fe17ffe8a52 | textbox | Client: i.e. Principal Contractor
c2857398-ad6c-50a4-96c9-3c52f23a56bc | textbox | Client Contact Name: Responsible Person(s)
a7d7df66-c625-5bff-b247-22212d4f0e64 | textbox | Client Contact Phone:
b13b3304-ffe0-5ae7-aaf8-edc9cd138706 | textbox | Client Contact Email:
bad8a559-d874-55eb-a218-4243f23c1f05 | checkpoint | Job Safety Analysis Details
a469947d-2b3a-5f33-ab44-b9b4c69ea6c0 | textbox | Work Activity:
905ccc21-6021-5239-b384-ce635906b5f6 | textbox | Location:
f7415c33-244e-520c-aa67-d500d8462829 | textbox | Who is involved in the activity?
d3e89825-380c-546b-bc9e-6bf4a989d47a | textbox | Plant and Equipment used:
9ecacf20-f268-5ac9-b799-d5c0514a6fa1 | textbox | Maintenance checks required:
24a90a79-f140-5fa1-beb7-898f715e5ec2 | textbox | Tools used:
d7752dc5-7792-5e83-85a2-2f755be77b58 | textbox | Materials used:
ece19453-cb90-52cd-9876-7d0c27c41dc9 | textbox | PPE used:
6bb36893-2014-5bf4-952d-0f70fb3768d6 | textbox | Certificates, permits and/approvals required:
162b772e-9fd6-546e-8ea2-775953e4d1ef | textbox | Relevant legislation, codes, standard MSDs etc. applicable to this activity
f948400d-3b6d-5037-a27e-a1da8d06232a | signoff | This JSA has been authorized by:
df68f526-1e94-59d2-832e-1b4bc4eb113c | checkpoint | Job Safety Assessment
cf688ca6-79f7-5725-beae-bbb986ea808f | note | Refer to the attached Risk Ratings table to complete the following..
518f8c17-4d86-5802-8ac3-eff5f5e3e04e | textbox | Job Step Details:
6992fa52-dea4-5713-84bb-25bb72ba0267 | textbox | Potential Hazards:
170af513-7c4e-58f9-82c1-42e002c4f9e6 | textbox | Name of Person(s) Responsible for work:
441de0fc-7b8b-5d41-a660-e67788b9af79 | button | Risk Rating: | Low, Moderate, High, Critical, Catastrophic
14fbe82a-5cf5-56ee-9a93-4773e6b44185 | button | How to Control Risks: | Eliminate, Substitute, Engineering, Administrative, PPE
6a6d2b9e-2883-5f6b-a805-500282b8e409 | textbox | Job Step Details:
e3e3f2a8-1e9e-519d-86db-d0ce85cedc3b | textbox | Potential Hazards:
493a06ff-81e8-582a-81ce-c4cef7fdacf8 | textbox | Name of Person(s) Responsible for work:
7e3c6315-640b-59c3-8f82-3b22df845571 | button | Risk Rating: | Low, Moderate, High, Critical, Catastrophic
6b86c4a5-f3fb-54c1-90d2-f82140454b05 | button | How to Control Risks: | Eliminate, Substitute, Engineering, Administrative, PPE
801a71e8-668c-5a21-a6c2-af5c69dbad86 | textbox | Job Step Details:
2363a798-0025-5ec9-92eb-65b8a2a365c2 | textbox | Potential Hazards:
421845c0-c4a7-5a27-9477-fc28cefc3957 | textbox | Name of Person(s) Responsible for work:
267a0ea0-9c62-53b1-ac4e-a29251822f3a | button | Risk Rating: | Low, Moderate, High, Critical, Catastrophic
c22b32e4-7bf8-5a3f-98b1-7a8559bb4c18 | button | How to Control Risks: | Eliminate, Substitute, Engineering, Administrative, PPE
42c21dbd-9bff-5051-bd1f-f936237b2320 | checkpoint | Signoff
9c249912-b3c0-5116-b8ec-aba0ea058e1e | signoff | This job safety analysis has been developed through consultation with our employees and has been read, understood and signed by all employees undertaking the works:
930a3e43-5647-50d1-87f2-966cce2343da | checklist | CHECK-002 Site Inspection |  | CHECK-002 Site Inspection
7604d349-3c9d-59ec-8769-a0cfe4110d87 | section | 1. Administrative, training and risk management requirements
b646b6a2-68d2-5b04-925e-0e13a9bb914a | checkpoint | 1.1 - So far as reasonably practicable, all workers carrying out construction work on the project have been made aware of the content of the WHS management plan, including any updates, and their right to inspect the plan.
6ba63d7d-3b3f-5c31-9434-f4939b574a87 | checkpoint | 1.2 - All workers carrying out construction work have received the general construction induction training.
b9691151-2ecd-5ee2-8ec8-b533204f2fd9 | checkpoint | 1.3 - Workers have been informed of the site-specific health and safety rules.
60ac4aca-7460-564d-ba14-2d3d98bfd234 | checkpoint | 1.4 - Suitable and adequate information, training, and instruction has been provided to workers in relation to work they are carrying out.
66bab419-a393-57f6-9c97-758d79271510 | checkpoint | 1.5 - Personal protective equipment (PPE) is being worn in accordance with the projects requirements.
2ab82d7a-cc3c-56a0-a89c-ba9e4252acc3 | section | 2. Safe work method statements
c145e282-9bf0-58ac-8a85-4500302a4c6e | checkpoint | 2.1 - A safe work method statement (SWMS) has been prepared for each high risk construction work activity that is underway or about to commence.
fe929405-eae8-5ca8-8783-fd58e2de54ac | checkpoint | 2.2 - Workers have reviewed and signed off on the relevant SWMS
7934e80d-dec5-5f41-be0b-42bbfcdd01e2 | checkpoint | 2.3 - High risk construction work activities are being carried out in accordance with the relevant SWMS.
8f0ef03e-318f-5cf3-b827-93b54c1df497 | section | 3. The work environment
e6018bbf-c8f1-5f07-b149-1bf83ae3ef97 | checkpoint | 3.1 - The work environment has been maintained such that it is clean and in a safe condition.
79bdc24c-1c00-5acf-983d-ebaa5ce5fad4 | checkpoint | 3.2 - Work areas are clearly identified and separated as necessary so that work can be undertaken safely.
1825c9fa-24bb-50ad-8b3b-a1e424e13ba5 | checkpoint | 3.3 - Lighting at the workplace is sufficient to allow:
f8272eb3-01c5-5337-a307-f72286a48c32 | note | ○ Each worker to carry out work without risk to health and safety.
1be19c4f-a82e-522b-98e5-e5aa656efb60 | note | ○ People to move within the workplace without risk to health and safety.
aef67d61-2c29-5ed8-9db6-bcf3ceacb0db | note | ○ Safe evacuation in an emergency.
e6860137-88a0-51f5-bab0-d6de14d63cb6 | checkpoint | 3.4 - The workplace has sufficient ventilation to enable workers to carry out work without risk to health and safety.
4ff74d5f-cec6-5c19-bd25-e6838e8f1c56 | checkpoint | 3.5 - The entries, exits, and access ways in the workplace are kept clean and clear of materials and waste.
48066b16-7c21-5768-945d-e4a5cf766b0b | checkpoint | 3.6 - A safe system has been implemented for the collection, storage, and disposal of excess or waste materials.
0b615730-4ffb-51cd-bfb3-02fcfc4435d7 | checkpoint | 3.7 - Sufficient area has been allocated to safely store materials or plant for the construction work.
8dca0770-d2f9-575c-9e8a-bc6b57a4f871 | checkpoint | 3.8 - Protruding objects that are a hazard have been made safe (e.g. exposed nails, vertical reinforcing steel).
b201c421-5b2c-5c48-9704-05cf6113c44a | checkpoint | 3.9 - Adequate facilities have been provided for workers, including toilets, drinking water, washing facilities, and eating facilities.
c51929b0-8776-5f5d-9a2c-3ebcffee0dad | checkpoint | 3.10 - First aid equipment has been provided for the workplace and is accessible to each worker.
18a4e767-8b1d-5672-a5a5-274690a036b4 | section | 4. Confined spaces
2825d9b2-da10-596a-9ce0-b40fcc56a1cc | checkpoint | 4.1 - For each hazard associated with a confined space, a competent person completed ASSES-05 Confined Spaces Risk.
0a584ab9-a5b3-52a1-b882-f4b9709cc8db | checkpoint | 4.2 - Prior to commencing the works, FORM-003 Entry Permit Confined Spaces has been completed and approved.
89309c03-7f35-5362-a583-36791c1dba8a | checkpoint | 4.3 - Appropriate signage has been erected for all confined spaces.
d0a6d31c-65a4-5bf4-bc31-672ba9175665 | checkpoint | 4.4 - First aid procedures and rescue procedures to be followed in accordance with POLICY-006 Confined Spaces Rescue in the event of an emergency in a confined space have been developed and practiced to ensure they are efficient and effective.
ded5ed0a-e444-5b8a-bb7f-fdbe7f8fb660 | checkpoint | 4.5 - Workers required to work in or around a confined space have been provided with information, instruction, and training in relation to the:
bed85791-cdf2-5734-99e5-42eabe40f212 | note | ○ Nature of all hazards relating to a confined space
be7ccc94-3134-5b95-8b20-72fefb415b43 | note | ○ Need for, and the appropriate use of, control measures associated with those hazards
b110c5ef-6275-5bf5-a856-5a63e44d03ea | note | ○ Selection, fit, use, wearing, testing, storage, and maintenance of any personal protective equipment
1a99ce71-7f11-5eeb-a21b-b350ded8d8c3 | note | ○ Contents of any confined space entry permits that may be issued
b0c02c77-ff62-5a00-8a01-e40663b3102c | note | ○ Emergency procedures.
e81da6f2-b7fb-5d0c-920d-ac0985916342 | section | 5. Working at heights
e2a6047c-3469-57d7-a1ee-63a6d2ce1e6a | checkpoint | 5.1 - A SWMS is available for all high risk construction work that involves a risk of a person falling more than 2m that has commenced or is about to commence.
c2fb3d08-8253-53dc-a912-7762ad36b3c3 | checkpoint | 5.2 - Where a risk of fall of less than 2m exists:
15a0bb70-25a2-55ce-8391-f9705261ae79 | note | ○ Each hazard that may result in a fall or cause death or injury if a person were to fall has been identified
098e60b1-4049-5b81-9802-dc44b50477cb | note | ○ The risk of death or injury that may result because of the hazard has been assessed
d8e17ce6-5b0d-5d71-adcb-c9012baa2fa9 | note | ○ Any control measures necessary to prevent, or minimise the level of, exposure to the risk is used.
98b57a94-c6a8-50d7-bb1c-2783d46d3990 | checkpoint | 5.3 - Where a risk of fall of at least 2m exists, control measures have been used which:
df712649-e072-54fe-b908-fe63884b915b | note | ○ Prevent a person falling any distance
28993959-da47-509e-a241-bb45845a83ee | note | ○ If prevention is not practicable:
55b684af-87ab-5194-82b6-3e644dbb1a7b | note | – arrest a person’s fall
7575aa24-7d52-5200-8719-e639552c447b | note | – prevent or minimise the risk of death or injury to a person when the fall is arrested.
6a7044d6-a81e-5157-bf4a-f5cbc210f31d | checkpoint | 5.4 - Ladders are not used to support a weight greater than that for which they have been designed.
d81daed7-0057-50a6-9fe9-8aece2cab495 | checkpoint | 5.5 - Ladders are used where the:
d8458251-f7d1-554a-bcc3-372ab76e7d8a | note | ○ Bottom of the ladder is on a stable surface
c8fdd838-d4e2-5652-83e9-9bc5b3b6145b | note | ○ Rungs of the ladder are approximately level.
3f3316e4-f01d-5a03-a2af-4637d940f52b | checkpoint | 5.6 - Scaffolding has been erected by appropriately licensed workers.
e8760cac-e387-5620-9ab6-470830ad9fb6 | checkpoint | 5.7 - Scaffolding is or has been erected and/or dismantled so as to eliminate or minimise the risk of falling at least 2m to people carrying out the work, in accordance with the regulations
faed25a7-0d74-5c49-bf12-7d35d9c1c221 | checkpoint | 5.8 - Safe access to and egress from scaffold has been provided during erection, use, and dismantling.
06596e0e-a7d6-5ec1-ae87-b458bc352bec | checkpoint | 5.9 - Written confirmation from a competent person stating that the construction of a particular scaffold has been completed, has been obtained prior to the use of that particular scaffold.
a1cf7634-7b7a-503b-98b6-a44b1401c2de | checkpoint | 5.10 - REGISTER-007 Plant and Equipment is up to date and includes all mobile plant in use.
92665bac-aa8b-572e-82c0-08a5392f0bfe | checkpoint | 5.11 - CHECK-004 Pre-Start Plant and Equipment has been completed for all mobile plant in use on delivery to site.
3dd77402-8a87-529b-8183-9c072abbce8a | checkpoint | 5.12 - CHECK-005 Regular Plant and Equipment has been completed for all mobile plant prior to commencing operation of the plant that day.
26a08f78-359d-5909-8059-66675eee2c23 | checkpoint | 5.13 - Mobile plant operators hold the appropriate high risk work licence.
23b709bb-1735-5ef2-90a2-edf28c5eaf62 | checkpoint | 5.14 - Where there is a possibility of powered mobile plant colliding with pedestrians or other powered mobile plant, a warning device has been fitted.
a556791d-1316-51ef-8b5c-74f5158d5808 | section | 6. Electrical
b2dcd8ef-695d-5a07-a1c9-d7a4c42cb637 | checkpoint | 6.1 - Electrical leads are arranged to avoid damage.
d2a5d551-016e-5c24-aaed-9a6546efb65d | checkpoint | 6.2 - Electrical equipment has been inspected, testing, and tagged in accordance with AS/NZS 3012 Electrical installations – Construction and demolition sites.
a3dea501-b49e-52a0-b686-be4f3b199e32 | section | 7. Hazardous substances and dangerous goods
28f006f5-6133-536c-83c5-e5fd046e9474 | checkpoint | 7.1 - All hazardous chemicals that are used, handled, or stored at the workplace are correctly labelled.
d9654d68-e223-5e2a-a924-23ef86d304da | checkpoint | 7.2 - A safety data sheet (SDS) exists and is available for inspection for each hazardous chemical used, handled, or stored at the workplace.
569fad8c-3f02-54bb-9e8d-8a513e63a228 | checkpoint | 7.3 - A register of hazardous chemicals used, handled, or stored at the workplace has been prepared in accordance with the regulations and is kept at the workplace.
73d14d34-271c-5e50-a0cd-036c9275e063 | checkpoint | 7.4 - A spill containment system has been implemented in each part of the workplace where there is a risk from a spill or leak of a hazardous chemical.
a5f93861-409f-57a4-9892-aad365d82b0e | section | 8. Corrective actions
a3895f4e-c7f0-509b-ac43-872a6873bc7e | checkpoint | Corrective actions
fefdfa68-8ae7-5784-8f52-ff31386b2624 | section | 9. Inspection sign off
19075f73-f3d6-5581-b9a9-39135e1c7056 | checkpoint | This workplace inspection checklist has been completed by;
4b32712d-5eb5-5f21-8318-9f10d9fee1e3 | textbox | Name:
8f6f1e26-c9d1-5d5c-beb5-fb775c1e28a2 | date | Date:
75e3ab6c-26b3-5c04-9c56-ec536230e4ac | signoff | Signature
690502ea-7da5-5119-ba91-b2aa394089de | checkpoint | I hereby certify that all corrective actions as identified in the above checklist have been completed;
be7ee8f6-2fdf-5e61-aee6-adf9bbb71704 | textbox | Name:
f58dc23b-c6d5-59c2-9d2a-57694b8eff87 | date | Date:
3e494399-cc9e-5e9f-964d-deff12bc6678 | signoff | Signature
7bd28543-904f-5683-acd7-cdd9184635f4 | checklist | CHECK-003 Site Establishment |  | CHECK-003 Site Establishment
8111ace1-1386-5c1f-8290-3df28e3c8d3f | section | Details
0b4ad232-5674-51d3-9408-aef0b58a609d | checkpoint-no-value | Details:
a9f0eb07-3912-523a-be5f-a802d6ff641b | textbox | Project Number:
be704f51-8345-5d07-82ad-4691b8d46bd7 | textbox | Project Name:
55438198-cfca-5417-84b8-414b08417475 | textbox | Project Manager (PM):
cecfc96f-5250-5907-bbf1-e0562cea155d | textbox | Project Address:
71a86034-b956-5203-b873-8d6f798b33ad | textbox | QA Platforms used:
d76c3f2b-8320-5708-a9da-38fbd066c69d | checkpoint | In house, FER & Specification Numbers
62d9c92d-c1ab-5446-89b1-bf80cbc0d1a4 | date | DATE:
087bf1f2-2a91-5ac0-811b-92888709522d | checkpoint | Site visit & survey
9d598589-23f2-5739-abd1-38084d2be5a8 | date | DATE:
f40bf70e-7c03-562e-9e73-8fbcd929c861 | checkpoint | Review Drawings & print for site
767f52ec-aec3-5775-a064-7229f459323b | date | DATE:
86a71627-b83a-5fe5-827a-1173c7cec5b0 | checkpoint | Review Fire Engineering Report
0d7909f1-54e9-5c90-92e6-074eee42c7aa | date | DATE:
eb035cf3-e47b-505b-b522-f71e191c12e9 | checkpoint | Allocate labour
0a895642-a262-5e46-a17d-2bd265707331 | date | DATE:
dae330e6-ef9c-57c6-9197-103abfd54f8e | checkpoint | Review Principle Contractors (PC) proposed baseline program
1692f978-f249-5f30-958a-396ff70c258b | date | DATE:
a55f05f2-ebad-534b-8cbf-1758e22f0184 | checkpoint | Create Fire Services Proposed Programme
07f60850-c8ec-5c07-8cb3-4760f7a199c5 | date | DATE:
7a356f7b-71e1-5c53-87a9-49ac25d117b8 | checkpoint | Upload to ALL necessary QA platforms
b5b18c80-8662-5430-9ca2-81c6feb62800 | date | DATE:
e81b739e-4825-5367-841f-3db753c333bf | checkpoint | Save softcopy in GM Dropbox
c65d94ba-f3ef-5124-bde6-1efbcc2ca74a | date | DATE:
c2e6bd69-c405-5afe-b004-c8b107fec18d | checkpoint | All employees have attended Induction
f2578d06-522d-52c8-91f5-609e406fe43b | date | DATE:
2630ff26-4768-5012-85c8-d89b8e40b4dc | checkpoint | All SWMS soft copies signed & hard copy printed & filed in the ‘on site’ paper folder
ccf4434e-fcc7-5408-8a54-c9b9b3f5816e | date | DATE:
5674c7a7-848b-557d-a867-52fce0b2bfd9 | checkpoint | PM Signature:
1ec883e5-6967-525b-ae22-80125604b1fd | date | DATE:
c87607a0-8578-5433-aab2-734b6f931e89 | signoff | PM Signature
e99a43c5-ae7a-5389-a273-198cfe9f7825 | checklist | CHECK-004 Prestart Plant and Equipment |  | CHECK-004 Prestart Plant and Equipment
8111ace1-1386-5c1f-8290-3df28e3c8d3f | checkpoint | Details
2e1d344c-ab73-54bc-b5e4-3444d8a9fc6e | date | Date:
3b5c5bec-2350-54b6-b713-c43ac58771f8 | textbox | Time:
4c1669d5-99a9-5e81-8a5a-161d62c69891 | textbox | Location:
59f00d22-104d-5160-b5b8-1d8cd709c20c | textbox | Supervisor Name:
0b454d7c-2ee3-5e46-a2c9-e543b923b322 | checkpoint | Plant or Equipment
f48d9eaf-9c67-565e-924d-11040d5b582b | textbox | What Plant/ Equipment is being used?
4584d21c-5e70-598e-a54f-9fc2afb46204 | textbox | Person operating today:
17a865dc-071c-56c8-b98d-4e49e8487bac | button | Is this person competent and licenced (if required)? | Yes, No
3a31577b-592d-559f-8dda-040ed9e28266 | button | Is the operator under the influence of alcohol or drugs? (If 'Yes' please explain in comments and find an alternative operator) | Yes, No
4f612611-4c0b-53d9-b178-9769ce369780 | button | Is the operator tired? (If 'Yes' please explain in comments and find an alternative operator) | Yes, No
7a491fa8-88d2-52b3-ab74-9aef8c85c2bd | button | Have you added this to REGISTER-007 Plant and Equipment (located in Dropbox) for this project? | Yes, No
baeae166-9daf-5b1f-90ba-a65637b23aa1 | button | Have all relevant SWMS been completed? | Yes, No
f9910de1-77f1-541c-876c-35b08d530ef7 | checkpoint | Plant and Equipment Checks
b45d2951-984d-5ce0-a5fb-26b81c80083c | note | As per WHS Regulations 2011, s206 the person with management or control of plant must ensure the plant is used only for the purpose it was designed and ensure that all safety features and warning devices are used in accordance with instruction. Please check the following:
ea5a1590-dbfd-5b88-b86c-3a03878dda58 | tickbox | Electrical switches, traffic indicators, front and rear lights are working
aa3cb88a-42fb-563b-b0ab-b91932ff10d7 | tickbox | Guarding is of solid construction, unable to be bypassed or disabled, is appropriately fixed and operates correctly (check latches/ locks and interlocks if fitted)
07fe5b08-28ea-5c01-9274-dc54ca2dfd72 | tickbox | Engine, fuel and lubricating systems are as per manufacturers specifications
730ebd88-f70f-5716-8480-43a0edc42738 | tickbox | Tyre pressure is as per manufacturers recommendations
367664b4-fa95-5261-8420-eecfc2d1a663 | tickbox | There is no risk to the plant colliding with any person or thing (i.e. workers, other vehicles or plant, energised powerlines)
a73d9251-65b6-5162-befa-3c38958f6bb0 | tickbox | There are no mechanical or other failures (e.g. hydraulic failures, release of hazardous substances)
28845e83-9f0d-5ec7-bbc0-4df352ca47a4 | tickbox | Seatbelts are available
c32cdd8c-4d62-5f96-b6fa-069e138360bd | tickbox | There is no damage to switch gear and controls and that controls can be locked off
894e2d46-f258-58b5-ae3c-c29202a15ba9 | tickbox | Emergency stop controls are marked, accessible and coloured red
85ca053a-3f8d-5ae8-a155-87cc7a942f68 | tickbox | Warning devices are positioned to work effectively
7c0cbce9-f240-5892-9790-fa6fc956e329 | tickbox | There are no hazards to the operator (e.g. things that could fall on the operator)
b4b2b9f2-8a04-5488-9964-80134904a506 | tickbox | There is no hazard or risk that could caused the plant to overturn
7cd527d9-908c-53cc-9e1a-7c5525d1d59f | tickbox | Maintenance and inspections have been carried out
2bcc0a89-8c1f-5fe5-958d-a1f1ba7233a4 | checkpoint | General Notes
d7295a42-11dc-51c1-80d1-cf9ed24c9857 | checkpoint | Operator Signoff
c685b88b-9455-5eaa-8271-b512fa65c130 | signoff | By signing I confirm I have participated in this prestart and understand my duties. I know what PPE I am required to wear whilst operating, the load limits and I am aware that it is my responsibility to leave plant not in use in a state that does not pose risk to others.
cc546369-bca4-51b6-ab24-8e4406ba760e | checkpoint | Supervisor Signoff
411f2708-55c2-5469-af77-82675a4393a8 | signoff | By signing I confirm I have conducted this prestart with the operator (above).
020b5712-d163-5c95-8358-2126970f6904 | checklist | CHECK-005 Site EOD |  | CHECK-005 Site EOD
8111ace1-1386-5c1f-8290-3df28e3c8d3f | section | Details
e7f3c29e-5e50-58c0-b5bc-209b95434737 | checkpoint | KPIs
2c117555-88dc-5d84-b712-b75ef2c33f03 | textbox | What area did you work on today? Specify level(s)
f7157fb9-994b-569c-9b04-62912b73fa90 | tickbox | Detection - In Slab Conduits
b1f61c85-ca69-5564-b369-551a80cf82a0 | tickbox | Detection - Rough In
dec18ba7-4149-5df2-a089-725a06968a7c | tickbox | Detection - Fit Off
1c541e4d-6623-5b54-b58b-602cc3a96091 | tickbox | Sprinkler - Rough In
f307cb6a-f521-5c07-89fb-6b9111ae5f3a | tickbox | Sprinkler - Fit Off
5991e66d-c07e-59fa-9561-cd7d0e3f6ba2 | tickbox | Wet Weather Stand down (List names and duration of stand down per person in comments below)
7560a99a-7fbb-53cd-8dcd-85b4ad832446 | tickbox | Safety Stand Down (List names and duration of stand down per person in comments below)
9576c040-03a2-5204-94c2-4123d27bbc88 | tickbox | Industrial Action/ Techs chose to leave site (List names and what time they left in comments below)
d6aa768d-18cb-5397-9287-98d25f058d4d | checkpoint | Productivity
46a96d36-7ed0-58f3-b1e1-c72696abe519 | textbox | In terms of production, did the team meet the site goals today? | Yes, No, Partially
530118c0-f0a4-5848-ad74-fee96a1ab03c | button | If 'No', what hindered the progress? | Time management, Lack of training, Fatigue, Equipment issues, Other
c0c390e6-0f69-5194-8688-7408f2af6512 | textbox | If 'Other' provide detail:
0da64418-8a08-5008-a58c-e5368b811be6 | checkpoint | Clean Up
555717e4-fdda-54a0-b7ab-a8be7b3bb56c | button | Is your work area tidy? | Yes, No
e203acc8-4d56-5755-a28a-53385dbf6798 | button | Have Chemicals used today been returned to secure storage? | Yes, No
f2f8656b-d5fe-59ab-9523-4e476f4bf5f3 | button | Have all tools been returned to toolbox? | Yes, No
94b5aaa5-fa5d-5f01-9a3d-822f681d037e | button | Are all tools (including site iPads) charged and ready for tomorrow? | Yes, No
f9f381b8-84ad-588b-b25e-f6d953254146 | button | Have you completed all necessary QA paperwork for today? | Yes, No
de3e2a82-2f4d-54ad-a987-e72c5df5cb97 | button | Are all employees aware of where they are working tomorrow? | Yes, No
9a083b17-de77-531b-ad18-c5ea724d4f5c | note | If 'No' contact management now
7f42cb68-a742-5487-9caa-f5a76b9f85fc | button | Were there any incidents, injuries or near misses on site today? | Yes, No
57405e7b-2cd6-522f-a8ed-d5e73678888f | note | If 'Yes' complete the necessary reports
42c21dbd-9bff-5051-bd1f-f936237b2320 | checkpoint | Signoff and CLOCK OUT
5d29489d-1335-55db-945d-fe7621bce49f | signoff | This EOD has been completed in consultation with our employees and has been read, understood and signed by all employees on site at the EOD today.
47a05a8f-01d6-5308-b319-09c8bfef63a9 | checklist | CHECK-006 Daily Prestart |  | CHECK-006 Daily Prestart
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
af98ba3f-7105-4c3e-be07-e2ab6454306d | checkpoint | CLOCK IN
c58e65ab-a72b-4fed-85ca-080ec1fa3336 | signoff | Sign here to CLOCK IN to your shift
0b4ad232-5674-51d3-9408-aef0b58a609d | checkpoint | Details:
c67a5ad6-470a-5e2f-997a-f5f60b5e37f6 | date | DATE:
be60c24b-9584-50b3-85e7-c97aac850d9f | textbox | TIME:
5309490c-3518-5494-8898-6b41003721aa | textbox | SUPERVISOR NAME:
694414d8-1e1b-5f09-a0ec-7b8d590ad762 | checkpoint | Issues
29d3d625-f08c-54b1-bf3c-b22dfa3fbd75 | button | Are there any issues arriving from yesterday? If YES, detail in comments below. | Yes,No
88bc1641-daee-577f-b7e3-efc84c9a3236 | note | NOTE: If this requires a change to the SWMS then please ensure this is captured and relevant personnel inducted.
0662f670-ac3d-5439-af86-c1336a2b3861 | checkpoint | PLANNED WORK ACTIVITIES / TASKS
89e3b170-750e-51d8-a682-a426806358d3 | textbox | ACTIVITY / TASK
63009163-b71f-5d74-88ab-182d0339fbec | note | SWMS that relate to today's task/s
3217cd42-d7b4-5c06-8925-f508bd3b2eb4 | tickbox | 001 – Working with elevated work platforms
4e6ff252-595a-527a-99b7-8b0d317de7fb | tickbox | 002 – Wiring Rough In Minor
cd7e73e3-d703-52b7-9d32-c59cb15791e0 | tickbox | 003 – Fit off fire alarm system
b8ad95df-8b35-52b0-9faa-5efb930c096d | tickbox | 006 – Installation of pipe and fittings
2fc333ec-8649-5094-9bac-e7db22722260 | tickbox | 007 – Manual handling
793477a1-ebab-528d-ac0f-4cf5e41a28fa | tickbox | 009 – Pressure testing of pipework
abf682f7-668c-584c-add3-69603f01ffe9 | tickbox | 051 – Using platform ladders
aab532fe-44ab-58ce-84b2-320c641c1eca | tickbox | 060 – Inhalation of Respirable Crystalline Silica
55efd7fe-fc29-5217-af4c-3858f7a3124e | tickbox | 061 – Working in Major Area of Concern
774a66c3-3fea-5200-a769-32e4e0d72e01 | tickbox | Task-specific Safe Work Procedure
23c8da75-1795-5395-a9d2-b738a880bbe9 | checkpoint | Is a SWMS in place for ALL high-risk construction work and work procedures in place for all other works?
018251a3-fdc4-5187-821b-085ee9060fc3 | note | IF NO, STOP AND DEVELOP!
ebf4ce4a-0774-58f0-a144-522ec96b5a15 | checkpoint | Are you subcontracting out any works today and will you be interacting with other trades?
95fe8c17-73e5-5a12-84ab-0e88db6ce7aa | textbox | If YES, please list
279dbae7-8c1f-5553-98d3-d60918e8eade | checkpoint | Permits
ccbee4d0-b0fc-50f9-aba7-187627b00d3a | button | Isolation Permit | Yes, No
e9e5dd68-707a-5644-8f38-af984c59f3e6 | button | Have conditions changed since permit approval? If YES, please note changes below. | Yes, No
498988e2-fa90-543d-abe2-62bbc0b59d3d | button | Hot Works | Yes,No
49f83c80-5eec-5445-acf1-c5c9e01af072 | button | Permit to cut or drill | Yes,No
26129dde-acee-57f3-b54c-c083077e591c | button | MAC Permit | Yes,No
1d20b088-7c9c-5436-8f27-c1ecd33f79fd | note | Please list Permit numbers with description below, and upload photo/ attach file if available.
cae12b06-72bd-55e9-a701-9b47a7fdd5d7 | checkpoint | Environmental Risk
d043a4ae-8752-53fc-bcd7-920e72521388 | note | What controls are in place to manage environmental risk on site, specific for today; e.g. Wash out areas, maintenance of sediment fences and drains, monitoring of dust?
be468b16-df19-537b-854e-46bbd3df7b89 | tickbox | Clean up the general area
03b3f67c-e939-50e1-8cb2-87e19dbe9fd7 | tickbox | M-Class vacuum
054df62a-5657-559a-8159-5ed36c7947b6 | tickbox | Fit test and appropriate fit mask
3640b7ac-10ad-5ec3-ab6e-ae1284393ae1 | tickbox | Spill kit onsite
9bbc93b8-7fb5-5515-8c51-902ff1a50612 | tickbox | Other - detail below
903e1008-c734-5d92-8e65-be1215f53964 | checkpoint | Checklist for Activities
f1e2b79e-aefd-53e7-bcd3-7868bdf06e49 | number | Number of people in your Work Group
57c8c5eb-69d5-5928-bcc8-b3fe0690aa3a | button | Daily Risk Assessment Completed | Yes,No
d198e689-340f-595d-aa6c-5796b9e55eea | button | Qualifications/training of staff adequate for work activities | Yes,No
a89c730d-f0a5-5583-9141-f6861600debc | button | Plant and Equipment on/off site | Yes,No
c2abc099-5048-5862-be7e-69276e515d47 | button | Equipment safe to use | Yes,No
c35b1cc8-2353-5462-9376-b66fbffbe2eb | button | Work area inspected and safe for staff to enter and work in today | Yes,No
446e2139-b3e3-5032-b3b7-4b2ecf6682f2 | button | Appropriate and adequate PPE supplied to work teams (SWMS/SDS) | Yes,No
1297b9fc-83fc-5f03-8c96-a7ef0df8cad5 | button | Weather conditions for work to be conducted assessed | Yes,No
50775e4c-331c-5bcf-9d61-90de79b49eb6 | number | How many workers have been allocated for today’s clean up?
31b028e3-39b4-5b10-96c0-301d4210e7d4 | button | Pre-start communicated to all work teams including all trades & subcontractors | Yes,No
00d26647-1805-5512-8e68-9d14a06237f7 | button | I acknowledge that all Plans on my Dropbox shared file are up to date and I have confirmed this with management | Yes,No
f21451ba-8bea-5c8f-a381-24f716ce840c | checkpoint | Builders Briefing Notes
96ad1a92-eed7-5574-b446-3263c628aa29 | note | Attach a photo of the builders brief
2bcc0a89-8c1f-5fe5-958d-a1f1ba7233a4 | checkpoint | General Notes
80eec9fa-fcc6-471c-83bd-753fa6302d43 | checkpoint | Mental Health Check-in
cd31bf4e-e2d5-5d58-b35c-fd75f58de3c1 | note | Prior to commencing work, ask your fellow workers: Are You OK?
0c6ae895-4776-5618-ae00-20be5d041a11 | note | Mates in Construction 1300 642 111
bd2c90e5-3cd6-5a5f-aefc-f4f34c1caf48 | note | Beyond Blue 1300 22 4636
3ecf9d4d-a367-5b79-a67e-d473daee966d | note | Gambling Help 1800 858 858
065e825a-d2be-5f52-accd-f30095264611 | note | Drinkwise 1300 858 584
462a3bfd-f982-5f3f-95bf-2a3e5632bbde | note | GM Fire Management 07 3519 7573
42c21dbd-9bff-5051-bd1f-f936237b2320 | checkpoint | Signoff
ad0d0126-8a7e-5cc0-84b3-32f1ee14e2ef | note | Remember to clock in and out of your shift.
2c27aaf3-a648-56ea-92c9-e1e22f200a26 | signoff | By signing I confirm I have have partipicated in this Prestart and I understand my roles and responsibilities today.
44e20f5c-ba00-4343-9dd8-8ddba179af6b | checklist | Communication (empty) |  | Communication (empty)
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
d85bed27-1ca9-433b-aaad-de24efe11860 | checkpoint | Communication
dd27004f-d3a4-5386-a27b-8c66417c0853 | note
536efed5-eb83-5ff8-80db-a4ce80c31179 | checklist | FORM-001 Tool Box Talks |  | FORM-001 Tool Box Talks
0e50f726-5e25-5b32-be5e-0af50c2a4fbb | checkpoint | Tool Box Talk
e3272aff-5ad7-5584-9f05-601db13efeff | note | Project: TPCH
c4982672-0b0f-5087-ad36-2079a30053d4 | textbox | Tool Box conducted by:
b862c72d-bb88-5890-9585-9eb1d66d73f3 | date | Date:
201ee0d5-9875-55e5-a6b4-cf9a175f45ee | textbox | Attendees:
272ef767-b0f9-5d40-860f-37667165b540 | checkpoint | Electrical tools Tagged & Tested
de358699-2ee1-5f01-a52d-02e78a8f5dcb | note | ACCEPTANCE CRITERIA: Completed Onsite
9031bd57-1d4e-547c-b0ec-b6fb0b1da5db | date | DATE:
605677f5-661a-5bc3-a836-02384d30df5c | checkpoint | Tools checked for wear & tear
d34b0a75-d62c-564d-93ac-a1912bd32f6b | note | ACCEPTANCE CRITERIA: Completed Onsite
8aa8c1f1-8235-59cf-9f29-b950ab07c005 | date | DATE:
acfc8acb-9e64-5733-af2a-b8ca4ea1ea81 | textbox | Items for Discussion:
eabcda0d-be6f-512a-b32a-8bddf5fcbc83 | textbox | Items for Review and discuss at next meeting:
95cb37b4-7a6f-5ffc-99b0-5d11fbc535e8 | signoff | Signatures
01a075b1-2660-5cc2-b2a0-a2f68974c58c | checklist | FORM-002 Tool Box Talk Platform Ladders |  | FORM-002 Tool Box Talk Platform Ladders
106e79f1-1888-598d-99d2-b5a1def7ffd3 | checkpoint | Tool Box Talk - Platform Ladders
887bab57-3216-58e7-9dd5-6974b3a623f9 | note | DO NOT use platform ladder unless you are familiar in its safe use and operation.
ac68153f-7547-5f9f-b14c-f8801309e330 | note | Always complete as much work as possible at ground level before using the ladder.
3271903a-2c15-5d14-ac31-800aa151f93c | note | Make sure the platform ladder is stable before climbing.
5c4a49ee-d931-5509-bdad-bc64c1ca1617 | note | Project: TPCH
00a320e9-986f-593f-bfe8-d25f2931da45 | textbox | Tool Box conducted by:
d0208122-f03a-5610-bde4-6bcb1a760f97 | textbox | Attendees:
da9865ac-d3b6-579f-bb6b-472d8b97b3d7 | date | Date:
fe834967-5fae-5142-ad41-d9de6147f88c | checkpoint | Potential Hazards
3674f2b7-e39a-58bf-b062-1209a407d5a0 | note | The folllowing potential safety hazards and risks have been explained to attendees:
5ea57c24-c9ef-5ac2-aae7-14b6543b15e5 | tickbox | Falls from height
e35ecb4b-a22f-5bcd-833f-fe852d10554a | tickbox | Falling objects
a3d70cbf-4729-5583-aee4-bcf73f29102e | tickbox | Awkward posture
016ab889-7fd8-5c55-95e3-1cf5f8ca44c5 | tickbox | Duration of task
674a0483-b78e-5388-ad6a-db7ac2554b1c | tickbox | Repetition of movement
3f4946f8-8fdd-526a-bb60-7b0d27db4098 | tickbox | Sprains/strains
a6af3874-9657-5afa-ac7b-5c30211f6885 | tickbox | Over-balancing
75d35ab2-1c77-568c-80f3-d9d45ae93ef3 | tickbox | Slip/trip/fall
4a7ce000-11b4-5942-9d59-57beec09de90 | tickbox | Electrical hazards
70790ef5-6074-57a2-b56e-987747b11967 | tickbox | Climbing with loads
1bd92719-b7cf-583c-a096-9b04e390c7ae | checkpoint | Pre-Operational Safety Checks
6ffbd377-bf17-5fba-98aa-8caef52856d1 | note | 1. Familiarise yourself with the safety instructions on the ladder.
a2ea6641-1eb7-56a0-a6e1-7e49d7e16115 | note | 2. Wear slip-resistant footwear. Never wear sandals, high heels or flip-flops. Wear appropriate clothing (e.g. no loose or flapping clothing, or clothing that restricts movement when climbing
aaf65bc0-57d6-5a03-b04a-8610a6416a50 | note | 3. Do not use if affected by a medical condition or medication.
2ba95fdc-b818-55eb-8e98-76f82b92f60b | note | 4. Keep ladder clear of live wires, electrical hazards and ceiling fans.
2c22d256-80a1-5046-8b5e-69ef43b328e9 | note | 5. When transporting your ladder check for overhead power lines, live wires, service cabling or electrical hazards.
93412ad9-195b-58ad-a5cc-688db75dd770 | note | 6. Carefully inspect your ladder to ensure there are no worn parts or damage before climbing:
ffc562ba-2d4e-5c0c-923b-aee111b51e69 | note | • joints between steps and side rails tight, all fittings secure, moving parts operate freely
639c69e6-a3c5-5051-a7d0-e2ca755bc18b | note | • rungs and platform are free of paint splatter, grit, oil and grease, welds are intact, and
5dc33034-ebb6-5e46-8386-62410b6d7321 | note | • all components of ladder intact including side rails, rungs, platform, feet, hand grip.
c1ec81fc-3779-5bbb-99e7-d74bdce4d420 | note | If any component is found to be worn or damaged, rectify any faults before use.
b6eb527a-c4c7-5a69-bb85-a66da835bc7d | checkpoint | Operational Safety Checks
df307b10-6066-5dfe-b2be-ccdabe4b711c | note | 1. Complete as much of the task at ground level as possible.
50ceb36d-3a89-51e0-a79d-8e7534c96b76 | note | 2. Ensure the ladder is placed on dry, firm, level ground/floor. Uneven footing may cause the ladder to rock. If this occurs re-position the ladder until all feet have firm contact with the floor. Always check there is no rocking movement before climbing the ladder.
2b10f449-9e31-58fa-8e70-0fe01b8c3789 | note | 3. If castors are fitted to the ladder, ensure rubber feet have firm contact with the floor when the springs are depressed.
37b91bc5-cb01-56fc-9108-0102c7c4058a | note | 4. Ensure the ladder is fully opened and the spreader bar is locked into position. Check for overhead obstructions before climbing.
7cac46ae-5fc7-5ee4-994f-75dd2980ea6f | note | 5. Only light work is to be undertaken on the ladder. Always face towards the ladder when climbing, and always maintain three points of contact with the ladder. Use a tool bag or tool belt to help to keep hands free.
64f23374-768a-5597-b8a4-9427fc451328 | note | 6. Only one person is permitted on the ladder at any time. A second person may stand alongside the ladder and help to steady it, or pass materials/tools up if required. Do not lift heavy weights that unbalance the ladder.
cea9f832-60c9-5a6a-8373-7c2c02db8309 | note | 7. Never stand or sit on the top cap or use the rails around the top as a step. It is not designed to be used as a tread/seat or step. Always stand in the centre of the platform.
c5338561-5326-55d2-8865-025c5fc7aa76 | note | 8. Do not over reach whilst using the ladder. Maintain the majority of your body weight inside the perimeter of the platform.
6a5bcd9f-5002-5193-afd2-5687e1f860a2 | note | 9. Do not ‘walk’ the ladder while on it. Always get off to shift position.
19c1d6b4-49ea-5f94-9658-6f1b832f0141 | note | 10. Before moving a ladder, take care to ensure that all tools and other items have been removed.
2d257990-358a-561e-bc89-f01924822341 | note | 11. Be mindful of your concentration and fatigue level. Avoid becoming overconfident when using ladders during repetitive tasks.
9d5b0bf0-53b6-5af8-a766-a7d78d594580 | checkpoint | Housekeeping
b7b52c7c-7b6c-5b22-8666-70b57f43c8ee | textbox | Items for Discussion
5c711e95-86eb-5f70-9f58-45404bea1e34 | textbox | Items for Review and discuss at next meeting:
0d24abf6-09a7-54db-913a-af58fcfdb176 | note | All attendees have been made aware they should:
fdb2ffa5-48c5-5b86-a475-b5e212b244b3 | tickbox | Return ladders to secure storage in a clean and in safe working order
ac8f4780-7d87-5234-98fe-0fee60585788 | tickbox | Regularly check ladder feet for excessive wear.
61838543-8502-5082-8baf-f0fa703ab465 | tickbox | Enter any maintenance in an equipment maintenance record
3015ae9e-0d1b-58a3-bfcd-57a87f411d9a | signoff | By signing I confirm I atteneded this ToolBox Talk.
702cae8b-c1ef-42a5-abc1-ec37fdf53678 | checklist | ITPS-100 Cast In and Penetration Installations |  | ITPS-100 Cast In and Penetration Installations
897f6bf9-7fc3-4196-9b80-a394d8032dd2 | section | Details
67d391d1-c295-4af1-8349-acd02446dfb9 | checkpoint | 1. LOCATION - ENSURE
299befda-778c-5a7b-895d-e237fe13b5c5 | note | CIBSE C5.2.2 Set Points
2bd36271-f49f-5a1a-9a40-1ad71e9d1dbe | button | Is the device setout correct and accurate as per RCP and installation plans? | Yes, No
8ef6ebf4-c6eb-589a-bb39-a4986e5b09aa | note | Add Photo
be2564ba-b133-4050-b4af-d346658f47bb | checkpoint | 2. CONDUIT INSTALLATION - CHECK
4cd6d7c8-e9bb-51fe-984c-2965c5fd886e | note | AS1670.1, AS1668.1, AS1670.4 and AS3000
3e335bce-677f-586d-afcd-8e7169221bbe | textbox | Drawing Reference and Revision Number:
a65ddbe4-2468-5c7c-8d67-ab1f7df865db | note | CIBSE C5.2.2 Set Points
935fecfc-0675-5dc2-a338-0181facdc0bb | note | Are Conduits routes are correct as per IFC Drawings?
c0aa72c1-07c1-5733-971c-6b581cb26f05 | note | Are Conduits are joined correctly and glued using approved PVC piping and glue?
e0dc532a-2714-5d2d-a3d6-4edd8fb53402 | button | Are Conduits are tied in properly to prevent movement and damage? | Yes, No
a4544a37-e0ed-569e-b1c3-18817878089e | note | Add Photo
73a9b7b9-8485-4f1b-a1d8-1cca6d420edd | checkpoint | 3. SLEEVES AND PENETRATIONS - CHECK
fb0692a9-3b2c-5dcc-9b77-8c8cd256bab3 | textbox | Drawing Reference and Revision Number:
f5e3f257-e242-5179-a729-5c8321f8a531 | note | CIBSE C5.2.2 Set Points
aa5887eb-e4b5-599e-9711-43ee4be10ad7 | note | Are sleeves the correct type, size and quantity as per penetration drawing?
22e84bc3-656b-5c8c-8895-2e0ebdae154b | note | Are sleeves routes correct as per IFC Drawings?
2deafbe5-350d-530d-a9a0-1696e6b022b7 | note | Are conduits joined correctly and glued using approved PVC piping and glue?
1bc935d8-63dc-5eec-89a3-a056ab1400ad | button | Have sleeves been tied in properly to prevent movement and damage? | Yes, No
ba85a673-701f-5ad6-87d3-0acf1c73028f | note | Add Photo
3654f318-04c3-4e66-bc31-eb5b10865d57 | checkpoint | 4. PRINCIPLE CONTRACTOR - CONFIRM
0535be51-d18b-5f19-8b28-946a7d6aa12f | note | CIBSE C5.2.2 Set Points
be0f15f7-59af-5ae5-a7c8-507f05483c9f | button | Is the Principle contractor's sign off required prior to pour? | Yes, No
5626ea1a-4bb1-5857-a849-64ab0d46c73e | note | Add Photo
46aaca8b-f5a5-454f-8fc9-ef6defcf501b | checkpoint-no-value | GM Fire Sign Off
171e99ec-a589-4ce0-93de-53bba0d079e4 | signoff | GM Fire Sign Off
b99c82f6-8d9d-4220-801f-51512d07782f | checkpoint-no-value | Principal Contractor Sign Off
b926f1c8-ace8-4ba2-9b5c-e1230ba9d94b | signoff | Principal Contractor Sign Off
b77d7cc0-a7a6-4652-a210-26ae615b2c3e | checkpoint-no-value | Consultant Sign Off
26840bf5-163b-4ea9-8325-424e9c04e6fb | signoff | Consultant Sign Off
cf5735a6-a1fd-4091-9e0e-7bfd68be87c1 | checklist | ITPS-101 Fire Alarm and EWIS Rough In |  | ITPS-101 Fire Alarm and EWIS Rough In
82869a9e-cccb-477b-83e4-431334fa36cf | section | Details
d16d6dca-5593-4a93-a138-47d7438aa364 | checkpoint | 1. CABLE - CHECK
08b3bf8f-88b4-5625-ab5d-65c62ea35497 | note | CIBSE C5.4.0 Wiring
0aeac70d-70ba-5ee6-a2e1-10ba4c2e0ac7 | note | AS1670.1, AS3000
2b2ffee4-2fee-51ac-96ac-33eaf7d9fba0 | note | Is cable installed the correct size and type?
b3702c14-6fcc-5bfc-831f-f5b09310044f | button | Is cable secured at regular intervals? | Yes, No
bce190a4-e2cd-5972-b57a-7115dfb434cb | note | Add Photo
8e7b2e3a-4494-5918-b76f-21325047c735 | button | Have you attached a photo of cable markings for Green Star Compliance? | Yes, No
ab583e11-1516-5003-a25c-1a722163ceae | note | If no, stop and attach now
bf483e41-b441-4dbc-ad5d-e2e5d86dde10 | checkpoint | 2. FIRE RATED CABLE - CHECK
52fb4fe3-8237-5a15-82b8-b594e4973cb2 | note | CIBSE C5.4.0 Wiring
ed6c87fc-1d77-5982-b1d9-ef258e3a1c4e | note | AS3000, AS1760.1, AS3013, AS/CA S009
6a41fd28-ee1b-5c9c-9e6c-e0ff5864c56e | note | Have fire rated cables been secured with fire rated fixings at a minimum of every 1200mm?
454837f4-7cd4-50a4-bb4f-7473845781cb | note | Have compliant fire rated cable and fixings have been used for required circuits?
ffdc570b-5638-5cf6-b5ef-3e970e047430 | button | Are fire rated cables installed as the highest circuit? | Yes, No
5b522aa3-bb0a-52b3-a064-cd763d391173 | note | Add Photo
b4db684c-60e1-47d8-afdf-53e3b0e15009 | checkpoint | 3. CONCEALED SPACE DEVICES - CHECK
9f13b612-e0f1-5742-a551-565240b0662c | note | CIBSE C5.6.0 Sensors/Detectors
b8282d6f-ea0e-5a50-a99f-131d23145dcb | textbox | Drawing Reference and Revision Number:
39e02404-bcd6-5bb3-8371-891773733649 | note | Have all concealed space devices been fit off?
febde04c-4fd4-5164-985d-872f8c89fb98 | button | Has remote indicator cable been left with adequate length? | Yes, No
8fd6fc67-a5b9-50f3-935d-935491255b85 | note | Add Photo
89312fbe-315f-4cda-b423-380c5a2de1b6 | checkpoint | 4. ROUGH IN - CHECK
80a2c820-e9ec-567b-9957-ca55f6a3c902 | note | CIBSE C5.2.5 Control Loops
d31c67b9-0b2b-5409-8c43-5cb5be87e847 | textbox | Drawing Reference and Revision Number:
1541c248-1719-592c-b5a2-5e905a6b9ea3 | note | Have all devices been roughed in?
aa835f01-266c-5794-a3c1-923acbfc361f | note | Is there adequate length left for fit off?
70dbcae1-9bdc-5de5-bb4a-87dc250cfede | note | Are device locations accurate as per the latest RCP?
0b22b1c0-5c6d-5ae0-9842-783c81cf439f | button | Have circuits been metered for continuity? | Yes, No
7e9fbf0e-830a-5a7e-888e-d9b1f300c8fb | note | Add Photo
342a7f3f-4b9f-49dc-8e3c-7dc1650b1ffa | checkpoint | 5. MAG DOOR HOLDERS - CHECK
5e6bb3d5-9ea5-5cd3-aa15-dfff37d4632d | note | C5.2.2 Set Points
fe553799-d68c-5c2e-be67-66def2cb2bd0 | note | Have wall noggins have been installed?
12196024-9c66-56e4-8c61-fc9a9c5e6666 | button | Are cables roughed in to the correct location in wall? | Yes, No
4107e4ef-3ae8-44a4-b3e2-85d013d393d2 | checkpoint | 6. SEGREGATION - CHECK
6f613927-c5bc-5724-88f1-0a0da7c1c189 | note | C5.2.2 Set Points
fa750c66-b336-52b6-aba6-1b185fe57657 | note | AS3000
c6613836-cc2c-5461-b07e-711fbdde9923 | note | Is there a Minimum of 25mm from water & gas pipes?
6f2fe35b-a140-5230-9ce4-4a53db5902cd | button | Is there a Minimum 50mm between ELV & LV installation or a physical barrier? | Yes, No
304c8fe4-58a9-489b-9f7d-e5c3e3c617d4 | checkpoint | 7. AS WIRED DRAWINGS - ENSURE
92084bf5-2159-504f-9d0d-26696ec4b828 | note | C5.4.0 Wiring
83282257-0596-54a5-a2a9-1c14aa1f9270 | textbox | Drawing Reference and Revision Number:
26e731e3-ffd7-5a95-9c97-0e6658c39fa1 | note | Are As-wired drawings complete and accurate?
95ba7999-be57-56dd-a8b5-2e10b2d7d7e4 | button | Have photos been uploaded to Dropbox? (as well as below) | Yes, No
63f5c05f-1451-57ee-855f-554ef6563aa4 | note | Add Photo
671c63ee-a6e4-4aeb-a751-4e3ecd06f626 | checkpoint-no-value | GM Fire Sign Off
dae03841-ce7a-41ec-9c8f-080bba2ee6c2 | signoff | GM Fire Sign Off
8f4b5d5e-feb5-4286-bd5c-cf16a1607be4 | checkpoint-no-value | Principal Contractor Sign Off
cf227b05-d67b-4ce2-bc6f-a32e54c0abc2 | signoff | Principal Contractor Sign Off
d3678be3-cbb0-4af9-b056-e171ecef1a5a | checkpoint-no-value | Consultant Sign Off
025044be-3313-4391-9019-f9b887aea61f | signoff | Consultant Sign Off
34ce4387-b3e9-4406-9509-15fc75adb644 | checklist | ITPS-102 Fire Alarm Fit Off AS1670.1 |  | ITPS-102 Fire Alarm Fit Off AS1670.1
3c4e88fb-1514-4611-867c-ca83aace27ec | section | Details
65d192b5-a8ed-45a5-9109-8672a4b426c9 | checkpoint | 1. DETECTOR TYPE AND LOCATIONS ARE AS PER THE LATEST RCP
13d0b7c7-e37b-56a3-b162-86781ebae491 | note | CIBSE C5.6.0 Sensors/Detectors
dc980132-5655-539f-bea1-faceb4e41744 | textbox | Drawing Reference and Revision Number:
0fbfd951-b390-5339-92fc-cb0bcbd1cc24 | note | Add Photo
613d54c0-0dc5-4610-9cce-2a344d41f331 | checkpoint | 2. DETECTOR ADDRESSES ARE MARKED ON AS BUILT DRAWINGS
3dc655f6-09ec-5c9c-957a-746a746ed2af | note | CIBSE C5.2.2 Set Points
e16f6fc2-a7db-51ab-afe0-6163b4de2ab9 | textbox | Drawing Reference and Revision Number:
e691a66a-5baa-569c-8727-9f416f22e7af | note | Add Photo
0884e8e9-3143-4167-b229-30ee8cef1734 | checkpoint | 3. DETECTORS MAINTAIN MINIMUM CLEARANCES FROM WALLS, PARTITIONS & AIR SUPPLY OPENINGS
1d812e13-42e1-5182-8e2d-ffc71a0f3ca4 | note | CIBSE C5.6.0 Sensors/Detectors
428c3e41-596f-50c4-b380-2affd5493ebf | note | As per AS 1670.1 - 2018 - 5.1.4 & 4.1.4;
39f5edfe-c05a-5bf5-b5a2-282141f9c159 | note | Is there a minimum of 300mm from walls & partitions?
ca87a1d7-ce27-57bb-a77a-f879882e3289 | button | Is there a minimum of 900mm from air supply openings for smoke detectors & 450mm for heat detectors? | Yes, No
7e44452a-e7aa-5fc8-98fa-03b65252055a | note | Add Photo
c0276521-3a3a-49a7-a72d-4f9f635f86bc | checkpoint | 4. DETECTORS MAINTAIN CLEAR SPACE AROUND SAMPLING POINT
377d5abb-9608-5509-bff9-e46b83d38c97 | note | CIBSE C5.6.0 Sensors/Detectors
9de1383d-fe28-5d02-992b-68d92c46451b | note | As per AS1670.1 - 2018 - 3.27.1;
726d9b81-417c-587e-b67c-e14e101b859d | button | Has a clear space of at least a 300mm radius and 600mm depth been maintained from the sampling point? | Yes, No
54eef5d6-1def-5a82-94b8-9cc2548152e9 | note | Add Photo
54d71ee0-4c61-4e7c-b36d-6250ab2d35a5 | checkpoint | 5. PROTECTIVE CAPS ARE INSTALLED ON ALL DETECTORS
f8ab18f3-7965-5cdb-9fa7-39d3c627c50e | note | CIBSE C5.6.0 Sensors/Detectors
512be44d-d3bc-510a-b273-6fa3469cfb62 | button | Have dust caps have been installed on detectors to prevent contamination from construction work? | Yes, No
c99aaebb-6e9d-5038-a599-e35149d71258 | note | To be removed once dusty works are complete, or at commissioning.
56128399-2115-500f-810c-4085b70a4a25 | note | Add Photo
44fe7045-17b4-43a4-9fd5-cb8a1bc7df63 | checkpoint | 6. MANUAL CALL POINTS INSTALLED AS PER LATEST IFC DRAWING.
8cca1e37-f94d-5166-af2f-3d5a55ab0a85 | note | CIBSE C5.10.0 Manual Call Points
3ce71944-d2f1-5b3d-9c3a-cd8f54c81a1e | note | Have MCPs been mounted between 750mm & 1200mm above floor level?
2110e973-ea95-5f48-9a79-cd0736ff518e | note | Is there a clear space of 300mmm on both sides?
36daaec0-d49a-5633-8049-3cabbe3b6633 | button | Is there a 600mm arc directly in front of the MCP? | Yes, No
6d85f267-0258-5bdf-916f-a29eb4ca5215 | note | Add Photo
7efd7ed0-fecc-4cd7-b30a-81635d401e1e | checkpoint | 7. MANUAL CALL POINTS SPECIFIC LOCATIONS
aa59cafa-ce83-5248-948b-df7657b933e4 | note | CIBSE C5.10.0 Manual Call Points
45f7c03f-12bd-514a-b124-25d174ef7352 | note | As per AS 1670.1 - 2018 - 3.14.2;
c9e429ec-22ca-5756-b2ab-adcec93ad6ad | button | Is at least one MCP installed in a clear and readily accessible location in the circulation space of the main entrance of the building? | Yes, No
8b9d0f50-fc65-5a26-b4e7-17f9c684d941 | note | As per the NCC2022 - S20C4;
88dd6bc0-a965-53b0-8b92-cb4da695c468 | button | If in a Class 9a building, have you ensure MCPs are located in evacuation routes so that no point on the floor is more than 30m from an MCP? | Yes, No, N/A
e524b044-8390-5ae0-a75c-a06344cd2ec8 | note | Add Photo
6c28d0ef-17a9-4c50-87e5-2f321613be61 | checkpoint | 8. FTRS
9423040f-f7e0-5f7f-887c-8872094d6928 | note | CIBSE C5.8.0 Modules Input/Output
8a71f568-3ee6-531f-b56e-befa636d4d6d | note | Have all FTRs been installed in correct locations as per latest drawing?
979bd9d2-caa0-5ce0-93cb-0930b9b734a5 | button | Have the right quantities been installed to ensure correct operation as per the fire & mechanical matrix? | Yes, No
c88ac9a9-377c-5587-8ada-2a550d5b450e | note | Add Photo
d7f7e900-6f32-48b1-8267-7eefdfe54c07 | checkpoint | 9. MAGS
22edb6e4-9c1b-53f4-b418-2b5fda9b0550 | note | CIBSE C5.8.0 Modules Input/Output
4e5c081d-b68c-50f4-a1b4-a7673847301d | note | Have the mag door holders been secured properly to withstand the weight of the door?
07298bc5-7946-5471-849e-16ce557f453d | note | Have they been installed at a uniform height on each door leaf?
55291f7f-cec9-5aff-bfab-b2c2c390c57b | button | Has a release switch been installed? | Yes, No
e9e17578-423b-578a-ad11-b2344eb94da3 | note | Add Photo
82c9b622-69a1-42b3-9f3b-fac1a35a49d3 | checkpoint | 10. MASDS
8d627330-6342-5306-83e1-3106a5197470 | note | CIBSE C5.6.0 Sensors/Detectors
d828e6a0-1abe-56e7-9011-b06aff9b325b | note | Has all pipework been installed in line with the Aspire calculation & design?
35ef01ef-3d65-5d9c-9240-3cb25fc63344 | note | Has all pipework been glued?
8018a7eb-e67b-5df2-a5d1-56b1154bad4f | button | Is the head end unit installed in an appropriate location? | Yes, No
451b9f11-be23-5a5b-8071-b78746425b4e | note | Add Photo
cf6d6282-bad6-4ed8-bbc2-26d20f6183ae | checkpoint-no-value | GM Fire Sign Off
aa3801d0-3f1f-421e-861e-450659c09c97 | signoff | GM Fire Sign Off
78dd17c0-b12d-4e37-a0d8-03e921f6746a | checkpoint-no-value | Principal Contractor Sign Off
bbb14b8a-150f-4266-9310-1f3333e883a5 | signoff | Principal Contractor Sign Off
a8058543-7f07-4582-b695-084f82185650 | checkpoint-no-value | Consultant Sign Off
8813b4f2-cfc2-4a54-9e37-c630696ecdc8 | signoff | Consultant Sign Off
ea05c0f3-3e6d-40be-99d4-fe1b15d4b36a | checklist | ITPS-103 Ewis Fit Off AS 1670.4 |  | ITPS-103 Ewis Fit Off AS 1670.4
22e6ecf1-ad5a-4514-9236-b0c8580ee206 | section | Details
1b056cf2-43b6-4ff9-b6a2-d58d67c1f59d | checkpoint | 1. WIP
f4e2ae0b-9e62-5078-a6e7-7e4136b13641 | note | CIBSE C6.2.8 Warden Intercom Phones
0df03bb2-b86f-5372-9d4b-9aa143fb3ccc | note | Are the Warden Intercom Phones mounted at a height of not less than 1200mm & not more than 1800mm?
464bb649-70b2-5179-b88f-d015dc46095a | button | Is there one WIP per EWIS zone installed within 4m of the exit? | Yes, No
2ece6e3f-5a39-539b-896c-7b612128d992 | note | Add Photo
5ebcadad-ffd7-47a2-bdf3-c92387a652d1 | checkpoint | 2. SPEAKERS
d77df70b-1ad4-5475-9aac-84fe581ea06a | note | CIBSE C5.2.2 Set Points
a8126eeb-9a59-5972-94ae-e06714f44e5a | textbox | Drawing Reference and Revision Number:
aa5c8fdc-330f-5a40-9aac-6fa6395d9a4d | button | Have all speakers been installed to the latest RCP? | Yes, No
bfd45b2a-6a96-55f0-a9d5-51f8cb454316 | note | Add Photo
155e1549-eda6-4e2a-bd51-a6ef3e8b742b | checkpoint | 3. STROBES
d359fd77-5ccb-5551-b0b5-4bf7c2d4fc3d | note | CIBSE C5.2.2 Set Points
ae0084ee-84c9-5dbd-97e1-e49133de2ae8 | note | Have all strobes been installed to the latest RCP?
0bdc277e-17a5-524b-9d5a-1dae8980efec | button | Have all strobes been labelled "EVACUATE" with 25mm lettering? | Yes, No
51af4ef0-0c9d-5994-a62e-c89c664892c2 | note | Add Photo
8acc6dd2-983c-4710-94b6-0d026ee4b7f3 | checkpoint-no-value | GM Fire Sign Off
7de57835-cee0-4cc6-b691-780bcdc166eb | signoff | GM Fire Sign Off
0b60acdd-78f5-4b8e-b927-7dce6f3ef727 | checkpoint-no-value | Principal Contractor Sign Off
6d48c8c2-ce5a-4bda-8ac0-4ab960990a81 | signoff | Principal Contractor Sign Off
5b3b8164-81fe-4274-9521-6ee08426c636 | checkpoint-no-value | Consultant Sign Off
caa0561b-7b14-4e99-8c4d-a5426c79811d | signoff | Consultant Sign Off
3e04c6ef-316c-4f82-89f2-8a2427bf78eb | checklist | ITPS-104 Fire Alarm Cable Tray |  | ITPS-104 Fire Alarm Cable Tray
790aa243-80d9-4687-a91e-044179764839 | section | Details
892834d1-7672-4539-9cbf-31ca86fb56c9 | checkpoint | 1. LOCATION & INSTALLATION
c28ffba6-8439-520b-9765-b25fdb150eca | note | CIBSE C5.2.2 Set Points
5c745f52-878b-569f-ad18-b80e2c07fd0a | note | Is the tray as per drawings and model?
6bb52098-87e1-5db4-b73f-f7bc337cd79e | note | Have all sharp edges have been removed to prevent injury or damage to cables?
f47c76c2-7075-5624-83f2-4fa3794955fd | button | Is the tray supported at intervals of no more than 1m? | Yes, No
433a48b7-18af-5a44-ad6d-fe311cc32e2a | note | Add Photo
1ca872e6-98b8-410e-a8aa-d1f2765739b7 | checkpoint | 2. FIXINGS AND FITTINGS
acb9c3de-5a3f-5f84-9f31-2a44b94c1b20 | note | CIBSE C5.2.2 Set Points
eb35db05-2cdc-5608-ab24-06d39041e683 | note | Have the appropriate fixings and fittings been used (for indoor/outdoor use as applicable)?
cd67fcfd-3e00-5361-95b4-ce13f5e75f7a | button | Are Seismic fixings as per the design documentation? | Yes, No
7763fdb1-20f7-5487-8a87-970b085e5f05 | note | Add Photo
0dbf1e3c-e49f-4c97-92ba-3d5eb4fb8da9 | checkpoint | 3. CABLE SPACING
226455db-86c8-5816-ac0f-92b80f178608 | note | CIBSE C5.2.2 Set Points
70fa22b5-a0e5-53b4-b36d-61a4b848fe6b | note | Generally, where possible install in the following groupings:
8d17924f-0d6c-5373-af51-d972e65da2ad | note | Detection Cabling & 24v Cabling
4406d6f1-1a6e-50a5-9954-f2e3039bfed0 | note | EWIS/OWS Cabling
d37b22b3-5a9b-55f2-a89a-57ac52235f62 | note | WIP Cabling
9cc4f180-14a8-5866-a5f2-e5375858a5c6 | button | As per AS3000, 3008, and S009, is the segregation of ELV and LV cabling at least 50mm? | Yes, No
bb119b8e-2722-5e61-903a-f35acbe9da23 | note | Add Photo
2788d841-4444-4a64-a814-00dc72849964 | checkpoint | 4. SEISMIC
be570996-834a-54ba-8459-04ddacee8e25 | note | CIBSE C5.2.2 Set Points
732cc7b5-9891-5227-b657-c2e26505ccd0 | button | Has the cable tray been installed as per the seismic drawings provided? (Use of stablity strut or catenary wire may be required) | Yes, No
2c87e873-48ff-523a-b19b-3050c14fb7d5 | note | Add Photo
de06c25d-bed7-422d-ba99-d6252d2d3a45 | checkpoint-no-value | GM Fire Sign Off
fdda0778-114a-4da7-aa5d-7d8138f3d9e3 | signoff | GM Fire Sign Off
34e5b550-ace9-4680-b170-a06078a991c1 | checkpoint-no-value | Principal Contractor Sign Off
cba8dae7-5cfb-4557-ad53-8d88ccfe5494 | signoff | Principal Contractor Sign Off
4a151ccf-8eb8-45c2-bda7-0aef6ead6f3c | checkpoint-no-value | Consultant Sign Off
5643af28-028e-4161-86b9-436cd59deb62 | signoff | Consultant Sign Off
f5dad4b7-1171-4d3b-acc0-da6839fd7a75 | checklist | ITPS-105 Fire Indicator and EWIS Panel Installation |  | ITPS-105 Fire Indicator and EWIS Panel Installation
47d785d8-7575-4af2-92d3-ccba393b8f5f | section | Details
5ae29c27-b976-497f-98e8-b08d19e11fd9 | checkpoint | 1. LOCATION
ffd80ea4-c84c-545f-a52f-9697b8bce1f8 | note | CIBSE C5.2.2 Set Points
0a619343-f589-5676-a03d-5ccca9b82694 | note | AS1670 (Section 3.9)
341ab759-114d-5967-9cd9-0d67299a2b6e | note | Do you confirm the CIE is:
d821be8d-8b0a-50ed-bfde-861539dfa7b2 | note | Not in an area used for storage of combustable material; and
f0bb949c-31d1-5eb5-8419-a2c9684f9a4a | note | Not obstructing evacuation of the building; and
c8f39ed0-144d-513c-8295-38eaf90b7446 | button | Not in a room containing sprinkler valves, pumps and motors? | Yes, No
9403d1d9-f716-5bf1-a82a-4c894d751684 | note | Add Photo
3c32158b-5065-41c3-a578-8a946c73bc39 | checkpoint | 2. LOCATION
a1a69f0d-2b0c-582f-a041-9e6f7f1446a7 | note | CIBSE C5.2.2 Set Points
740441ca-5685-5d8b-bfbb-92e407c7775c | note | AS1670
03c90b54-3c9d-54d3-884a-b28b58afc48c | note | Has a minimum clearance of 1m in front and 0.5m to each side been maintained?
8d9a922f-7554-5335-a3b2-1bfbb20e89e9 | button | Where obstructed by a door, are the words "FIRE PANEL" in contrasting colours? | Yes, No
559e2413-fff0-53dc-9f5d-b3d68114a22e | note | Note - Where the door reduces the sounder, an external sounder may be required.
b5f01517-a744-538e-aa90-c5e242c1f2b8 | note | Add Photo
13004747-844e-4c0c-b6b0-21510b574b95 | checkpoint | 3. CONTROLS AND INDICATION
09c7a8d1-e58c-5d04-8280-fcbbc699aa53 | note | CIBSE C6.6.0 Brigade Interface – FFCP
04e0ee78-097b-5145-b619-bc4441360a52 | note | AS1670 (Section 3.9)
8e58d972-0436-5ef8-a5ea-40c9a94dacb2 | note | Do you confirm CIE has controls that are:
6f667e1c-4e03-5925-96f9-0c8fcc00d458 | note | Not less than 750mm from floor level; and
a6efb808-6a06-511c-97fd-b4ed4e3eb5f5 | note | Not more than 1850mm from floor level; and
045f6193-26bf-56b1-967b-18b9845fbc11 | button | The access to controls is not obstructed? | Yes, No
317b58de-3fbb-5fd5-96b9-62b2363583dd | note | Add Photo
a58637ea-6d07-4799-ab5c-708cfb9aef76 | checkpoint | 4. CLEARANCE
be3706c4-1009-564d-b196-cf490593e6e5 | note | CIBSE C5.2.2 Set Point
f7937cdb-57c4-5b72-967c-af524cf535c9 | note | AS1670
a4956600-14f2-5411-bed8-ee2d7a326f05 | button | Is there a minimum clearance of 1m in front and 0.5m to each side? | Yes, No
101d8073-c2c2-51b9-879c-a2b1f6b1ba48 | note | Add Photo
3453922a-f354-44b9-b744-100cfa3c81dd | checkpoint | 5. EXTERNAL ALARM
561e2a60-4435-525f-b973-eda5d14ff9fe | note | CIBSE C5.2.9 Alarm Functions
09276b07-74d3-597c-975b-1c69616d8029 | note | AS1670
df8b63f7-4477-551f-bd28-7dfdb418b58e | note | Is an external wall mounted VAD is located on the front façade no more than 10m from the DBEP?
83aaff64-1fb8-504e-b80b-fcb04fa7c058 | button | Is it visible from at least TWO directions, and mounted with the words "FIRE"? | Yes, No
6ff9d1b7-d707-5380-b802-d509aebf734a | note | Add Photo
bd6ed336-9f05-4690-bd09-6e7be7b21133 | checkpoint-no-value | GM Fire Sign Off
6371681e-3e5c-40c2-88ba-ad9f271b70b2 | signoff | GM Fire Sign Off
3b89d488-deee-4637-bd42-766ab8ba8b50 | checkpoint-no-value | Principal Contractor Sign Off
e1d149a0-d3a6-4da1-948c-c971bf20eb94 | signoff | Principal Contractor Sign Off
46469e54-5eb2-48dc-81f8-3cb5012d40fc | checkpoint-no-value | Consultant Sign Off
1339872e-c08f-459f-ac87-ac0e239d4c78 | signoff | Consultant Sign Off
732abbbf-a490-4c9a-a842-d5064c65544b | checklist | ITPS-106 Sprinkler Pipework Rough In | itp | ITPS-106 Sprinkler Pipework Rough In
4080fbe1-aa4e-4626-96b0-214aa131dc2e | section | Details
b4357025-8133-4e84-8393-6ec5808ba75e | checkpoint | 1. PIPE LOCATION & HEIGHT
e4df8b3c-0ebb-51a2-af5e-c9496168a14c | note | CIBSE W5.2 State of the System
4cdcefc5-e000-58f4-8553-4a1cf8163290 | note | AS2118.1-2017-Section 14.14
05f7b7db-9d01-5c86-9137-34501bca8c8c | textbox | Drawing Reference and Revision Number:
05f57b0f-9e68-57ab-8857-aac6892cbaed | button | Have you reviewed the Fabrication Cut Sheets? | Yes, No
822758a7-8457-5ff7-b2dc-71064ee0a966 | note | Is Pipework setout as per dimensioned install drawing?
095b234f-6306-5dd2-8ef1-4aba0193f5f4 | note | Are Pipe heights correct?
093f0661-c0f5-531e-8c76-1da59dccd28e | button | Have Pipework alterations been approved and recorded for as-installed records? | Yes, No
f4a36429-6a75-5129-b752-d1b940ffe619 | note | Add Photo
15608975-d36a-4128-a922-232e49ec8041 | checkpoint | 2. PIPE SUPPORTS
5542f81b-9424-5089-8a53-dd21a19b77cd | note | CIBSE W5.2 State of the System
a57a0819-f69c-5e18-9e92-d489cec14253 | note | AS2118.1-2017 - Section 7.8
f02f45cf-469b-5744-b0a7-221e4a8811f7 | textbox | Drawing Reference and Revision Number:
8f63d219-ae83-536a-ba35-de84837c1bf1 | note | Is the Pipe hanger type as per the install drawing?
e8aba75b-6e71-563c-a245-68f54394f059 | note | Are Hanger fixings as per the install drawing?
6d0d9f5f-0582-50e3-b46c-26ef156a95d7 | button | Are hangers spaced correctly? (not exceeding minimum spacing) | Yes, No
cc3c52db-4dc9-5695-bdd4-ebb4f6c2347f | note | Add Photo
3d5535d8-4d60-4555-9977-9d79bd4249ba | checkpoint | 3. CHECK GROOVES DEPTHS
d3f393d2-3b11-527f-a22f-07ec384397b9 | note | CIBSE W5.2 State of the System
955a8d81-0c81-56ea-8074-bac9797f5203 | note | AS2118.1-2017 - Section 7.1
3b1dd1d7-a096-5f10-97e2-a513c559a7ab | note | Are groove depths within tolerance?
a667fc7d-9586-5f0d-b3b2-ab719b98b986 | note | Are pipe heights are correct?
ecadb78e-ccbc-5fef-91ed-aa04fb4f1239 | button | Have any pipework alterations been approved and recorded for as-instaslled records? | Yes, No
835821d0-471f-5190-83ca-a64df2ff5a58 | note | Add Photo
70d875ae-cbf3-4ed8-a6cd-8f4cf68910be | checkpoint | HOLD POINT
49af548b-6fbc-5c34-9bf6-27422c994b89 | button | Confirm Safe to Proceed | Yes, No
ec3afbf1-903c-47a9-972f-aa57863251c0 | signoff | GM Fire Sign Off
0323e211-b2fa-4535-bd58-a8b121e558df | checkpoint | 4. VICTUALIC COUPLINGS INSTALLED
fe09fb72-673f-5342-a2ad-e0cbcc79e3a7 | note | AS2118.1-2017 Section 7.10.2.2
90e04b72-4635-51af-978f-cab5c0c0668c | note | CIBSE W5.2 State of the System
e378c955-c872-537e-816c-818e90757e4e | button | Have ONLY Victaulic brand couplings been used? | Yes, No
49a6d28b-c79d-545f-8e2a-02bc70435ef0 | note | Add Photo
f4d93121-f173-4880-b1a9-befbaeb94296 | checkpoint | 5. CONCEALED SPACE SPRINKLER HEADS
719c6323-f7b2-56ce-8ff9-29ee8d9851cf | note | CIBSE W5.2 State of the System
091b2238-ac2e-5f00-80ab-4e6005513c03 | textbox | Drawing Reference and Revision Number:
c16506ed-d313-5728-896c-6b4126eb37cd | note | Have ALL concealed space sprinklers been installed as per dimensioned install drawing?
b74ad09b-92ea-58bd-a457-53515d53f351 | button | Have the correct sprinkler types and temperatures been used? | Yes, No
6fab9e4d-0ef9-56c7-9b67-fb05e44f4a7a | note | Add Photo
38bafccc-5f98-40c4-a119-2c18abaf244c | checkpoint | 6. EXPOSED SPRINKLER HEADS
a395f727-6b67-5d20-ba6c-5288f0b6b711 | note | CIBSE W5.2 State of the System
6892d3b1-d176-5ba4-8e36-6fd943f62f79 | note | AS2118.1-2017 - Section 5
72633a00-815b-5e8f-9cd9-d8e6d37561c6 | textbox | Drawing Reference and Revision Number:
f1f9d305-6e10-5992-84f5-06ba999e1e4b | note | Are exposed sprinkler heads installed as per dimensioned install drawing?
5c9e5987-17db-56a5-bfab-07cae5545209 | note | Are sprinklers clear of obstructions?
64f73f1c-6fea-5484-b3a5-81a9b666db9f | note | Have the correct sprinkler types and temperatures been used?
6f2c3068-6900-5e48-810c-5b7a7e9cc721 | note | Confirm sprinklers do not exceed the maximum distance from the soffit?
cb738600-1baf-5fdc-a56e-11926feb0f98 | button | Have sprinkler guards been fitted where risk of damage exists? | Yes, No
6cb8c1c8-bf3b-574d-8a95-2664ad976433 | note | Add Photo
ecde7812-0990-49b9-92b5-e86431cd4b36 | checkpoint | 7. FLEXIBLE DROPPERS
391068d5-1241-5c46-888d-3615bdc366a2 | note | CIBSE W5.2 State of the System
5611fb14-d9b6-5158-b391-0968e39b300a | note | AS2118.1-2017 – Section 7.6
1e44c5d7-4bc7-5c6a-9e49-e7eb2367ba41 | textbox | Drawing Reference and Revision Number:
e3e8175d-7413-5d5a-a742-096a152ca028 | note | Is flexible dropper installed in correct location?
e7a5c121-791f-563b-a6e5-40420c8d9244 | note | Correct sprinkler type and temperature?
da6df5b2-161c-5a45-b6d4-b836e659172e | button | Is there sufficient length to reach on-ceiling location? | Yes, No
f8af0084-cd0f-5b8d-9a13-f21104b6c8d6 | note | Add Photo
151826d9-d239-4280-b0bb-331d9509892e | checkpoint | 8. SPRINKLER INTERFACES - VALVES, & MONITOR SWITCHES
75d3a337-9534-5171-8054-1530e2dd3620 | note | CIBSE W5.2 State of the System
85c73b56-b463-55c2-9399-01aba66f52d8 | note | AS2118.1-2017 – Section 8.13.5
94e50a3a-48c1-5d86-8b12-9c1e91dbe1c6 | textbox | Drawing Reference and Revision Number:
b292a215-2e96-5efe-93c6-0780fcbac791 | note | Have Isolate valves & flow switches been installed?
10021679-2a82-5c96-a205-3b2c3779709a | button | Have labels been installed? | Yes, No
6c5e63a6-84fa-5277-88a2-fe48dd81edb0 | note | Add Photo
f0b52c78-c12d-4b25-aea0-619e9c207d53 | checkpoint | 9. REMOTE TEST DRAIN
9054040c-cd71-5797-90eb-3dc4153aa1b1 | note | CIBSE W5.2 State of the System
e04abd0a-5828-542f-a473-3c2c1723fe32 | note | AS2118.1-2017-Section 8.14
122008c4-eb73-5d52-913f-3bd9166888a2 | textbox | Drawing Reference and Revision Number:
44201be4-d512-52f2-a4e4-e42c650ad808 | note | Is the Remote test valve installed as per dimensioned install drawing?
d122d434-1f77-5d49-aade-4bf5fa23be29 | button | Restricted orifice installed? | Yes, No
c4da093e-bef2-531c-bd19-a605d8d6b53f | button | Have labels been installed? | Yes, No
d47a6bee-0837-5ec4-8bbc-4937cda53a35 | note | Add Photo
b26458e6-4184-4fac-ace7-ff355e3741b1 | checkpoint | 10. SEISMIC
5f3794d6-a16d-5f4c-8900-b9b455e810ac | note | CIBSE W5.2 State of the System
fe4a0208-48f6-518e-a130-0d2635b8f483 | note | AS1170.4-2007 (R2018), clause 5.4.6 and section 8. AS1170.0-2002, AS5216-2018 & ETAG 001 PART 6, ANNEX 1.
af5c7aee-5ab2-5359-8fd1-a9a44e85ca6f | textbox | Drawing Reference and Revision Number:
6b7e8886-bb27-5d46-a567-fc9cedc0200b | button | Are Seismic braces installed in accordance with Engineered drawing(s)? | Yes, No
94a0e2ed-ff3c-5688-8771-0100b93f5073 | note | Add Photo
0f1dc728-71e5-5a2c-af33-7e21eabe7180 | note | CIBSE W5.2 State of the System
3d799606-5b89-5d6c-8c89-838a33f61af1 | note | AS2118.1-2017 Section 7.9.6
73b926f3-8148-5a9f-a435-4af6409162a8 | note | Has painted pipe been inspected for damage?
031a9387-8d81-5137-a7ee-4e239afad3e0 | button | Have Repairs to paint been completed where required? | Yes, No
de88f9ec-14ec-5196-bb49-32c6a6c3940d | note | Add Photo
801e57c7-0aac-4be8-bc8b-7a21f7d1e1ad | checkpoint-no-value | GM Fire Sign Off
76a7254c-0c2b-4316-9f33-92e339efa97c | signoff | GM Fire Sign Off
b26bb77f-7305-4311-9bc2-357977d49377 | checkpoint-no-value | Principal Contractor Sign Off
b8b3cc13-457c-495a-bb41-484380a32b89 | signoff | Principal Contractor Sign Off
69d70d43-c1b9-4f78-9157-f89065e515d8 | checkpoint-no-value | Consultant Sign Off
5e59d6cd-7756-4f1b-b93e-14ed5164b5e7 | signoff | Consultant Sign Off
8f68f480-3312-47f0-b45d-4ffd19dc8589 | checklist | ITPS-107 Hydrant Pipework Rough In |  | ITPS-107 Hydrant Pipework Rough In
19b6ceed-69ab-4979-9442-c997fe3b5ebe | section | Details
f784d5f7-a01e-4829-be14-19e11845b7c0 | checkpoint | 1. PIPE LOCATION, HEIGHT & SIZE
af0b910f-1f9f-5184-938a-692cb9dd54cf | note | CIBSE W5.2 State of the System
9a283cc8-5b3b-558d-a753-d3fbfa91fcab | note | AS2419-2005 Section 2
6e53ee5a-bd2b-5cdb-8d5c-4ed2f50b8484 | textbox | Drawing Reference and Revision Number:
1e2cd43e-5a3e-520d-b185-cfa7afcf69ae | note | Is pipework setout as per dimensioned install drawing?
344c16d7-5c20-564f-beba-1e377ddd280a | note | Are pipe heights correct?
d80a4cb4-d282-5780-935b-22849dd2ca61 | button | Have pipework alterations been approved and recorded for as-installed records? | Yes, No
08fcbf71-2887-546e-9f9b-b6d7add006e1 | note | Add Photo
31efe896-2e6a-4ade-a356-2bd0706ed1e7 | checkpoint | 2. PIPE HANGERS
7c314af6-6022-57b7-ba6a-99da0d62ae71 | note | CIBSE W5.2 State of the System
b71a8923-0d9c-5815-b4ce-1c2596a5fef4 | note | AS2419-2005 Section 8.7
7a01b913-b541-5391-87c7-af184e4cf80c | textbox | Drawing Reference and Revision Number:
c27ffc46-12d7-53d5-9e1b-c11d958f1606 | note | Is the Pipe hanger type as per the install drawing?
606d04ca-5756-5934-b390-2db4c4bf04dd | note | Are Hanger fixings as per the install drawing?
fa16670c-d6d0-5d58-9509-113c51c45296 | button | Are hangers spaced correctly? (not exceeding minimum spacing) | Yes, No
3246b777-85ee-5451-9385-cc5e66856e25 | note | Add Photo
b77b7470-b7d0-4142-8cb2-aa24a2a2dfeb | checkpoint | 3. CHECK GROOVES DEPTHS
f3a4b805-00ec-55c7-9837-701636a393d4 | note | CIBSE W5.2 State of the System
b43a6036-7147-53a6-9624-689c2d4f01ce | note | AS2419-2005 Section 8
8d52f4ff-2dcb-519a-b22c-ca19dc8aa591 | note | Has Victaulic Groove Tape been used?
e4b0ad5f-d231-5c7c-96f4-16fd9e0c7826 | note | Are Groove depths are within tolerance?
e05a4e9a-2b3c-5a61-bbb0-8efdb4c2f4c0 | note | Are Pipe heights correct?
f6dc99b9-a192-598d-aeeb-73240af4658c | button | Have Pipework alterations been approved and recorded for as-installed records? | Yes, No
07cc05b8-1728-5a53-b414-663b00b1d27c | note | Add Photo
bc70e791-23a3-4107-bdbc-9e26a9173621 | checkpoint | HOLD POINT
f5ec7699-e17f-5e95-8013-7eb6f1b444d7 | button | Confirm Safe to Proceed | Yes, No
bc751c21-2ba2-41a5-820c-ac9fba627491 | signoff | GM Fire Sign Off
997e94b6-d8d2-4264-85c8-7210dfdcf87e | checkpoint | 4. VICTUALIC COUPLINGS INSTALLED
5fc771eb-ba88-56dc-8e3c-55bd0e491871 | note | CIBSE W5.2 State of the System
95ec94d0-30b9-5e57-afa0-68d715b87034 | note | AS2419-2005 Section 8.3.2
977f740b-fec1-5ce4-9a30-1ec16d99c16b | button | Are Victaulic brand couplings the only couplings that have been used? | Yes, No
05387bad-d2fa-53e4-9c63-86ab0fd32b64 | note | Add Photo
81719eeb-a205-4095-a20e-54866bc25f77 | checkpoint | 5. ISOLATION VALVES INSTALLED
7eb640d0-4498-5168-a40b-9c867b2fc3c5 | note | CIBSE W5.2 State of the System
db2c5363-c68a-5dfb-8453-5f54cf04d911 | note | AS2419-2005 Section 8.5.8
60e4df9a-aa07-5972-8be1-13fef52bf1c0 | textbox | Drawing Reference and Revision Number:
b5e8b952-3c36-55aa-b47c-2de3d618567b | button | Are Isolation valves installed as per install drawing? | Yes, No
cdcc3ded-7e33-5a31-a223-00d2cccee39c | note | Add Photo
696b1fd2-dc02-4d47-bd94-99d47fd227dd | checkpoint | 6. SEISMIC
8eb97168-469d-584b-9a84-b30d13f792ad | note | CIBSE W5.2 State of the System
3b4ba4c3-1829-5c8d-b704-7718737aaf64 | note | AS1170.4-2007 (R2018), clause 5.4.6 and section 8. AS1170.0-2002, AS5216-2018 & ETAG 001 PART 6, ANNEX 1.
fd624e91-4133-5942-98ad-459892daf8e0 | textbox | Drawing Reference and Revision Number:
1524e240-a2a9-5934-a801-f9d6df5fdce5 | button | Are Seismic braces installed in accordance with engineered drawing? | Yes, No
0487eca0-8e50-5364-ad19-bf4f872995e3 | note | Add Photo
5269ca2d-c6de-4dde-ab8b-921f655186d1 | checkpoint | 7. CLEARANCES
2642bab9-57e6-5b75-81d0-80a09b80f0c0 | note | CIBSE W5.2 State of the System
c1a620c2-7a30-59bd-adf5-fd8734c14b4b | note | AS2419.1-2005 – Section 3.2
fbb62c2b-bf21-59f5-b032-4bc57d990b5c | button | Is the Hydrant positioned so it does not obstruct required clearance for egress path? | Yes, No
e6a6986d-292c-53c6-aa6c-f96c234cac30 | note | Add Photo
886b8d12-8f74-4cfa-8bdd-76a7dc211441 | checkpoint | 8. LANDING VALVE FIT OFF (CLEARANCE HEIGHT/ ANGLE)
d51e4012-794d-522d-bade-e49f438f3ba3 | note | CIBSE W5.2 State of the System
e543652a-dea8-53df-b07d-7cce29772670 | note | AS2419-2005 Section 3.5
18875e70-bec0-5c8c-a382-8102c08e3dd2 | note | Have you checked:
7512da06-fd16-504b-b12a-a7c85e9748f6 | note | Landing valve height; and
40b846c8-72ed-5e91-a73d-69155370651e | note | Landing valve is at the correct angle; and
4549632b-00a7-5a40-a4a2-73fb55c00548 | note | Coupling angle and orientation is correct; and
f1e5f0cc-5117-5a2e-86f3-cf7a8f418921 | note | Required clearance for the handwheel has been maintained; and
18c17bc3-b45d-56a5-91ed-3d6d306f2d4c | button | The required clearance for the nozzle has been maintained? | Yes, No
40314cef-c497-5672-8373-97be5d7bf7e2 | note | Add Photo
204c86c3-7cbd-460a-8d2a-f9fcf62b5958 | checkpoint-no-value | GM Fire Sign Off
9c524d12-1ec7-44c4-8bab-7abf8e330fb8 | signoff | GM Fire Sign Off
e0f81b0b-25cc-4a42-a1e5-a060fe158f57 | checkpoint-no-value | Principal Contractor Sign Off
e16f063b-44c2-4ca2-9f66-7fa3344a852f | signoff | Principal Contractor Sign Off
2035cb13-2836-4c84-a6a4-f649f26510af | checkpoint-no-value | Consultant Sign Off
46d8493c-851f-43ab-92ce-98a55374ec40 | signoff | Consultant Sign Off
122cd6ee-2c68-4560-92dd-7e4e193d6649 | checklist | ITPS-108 Sprinkler Fit Off |  | ITPS-108 Sprinkler Fit Off
b503fd3d-69fe-467c-968e-6c56f5c18ca8 | section | Details
7a9770fc-9314-4cc2-938c-ac125f2fc525 | checkpoint | 1. SPRINKLER LOCATION
dac70f2e-e833-5e86-a88f-03ceedabbe9f | note | CIBSE W5.2 State of the System
f8038c9d-22aa-5368-aae3-d1dcd049fcda | note | AS2118.1-2017
99a3b993-a581-553f-a7ad-3bb393aa8955 | textbox | Drawing Reference and Revision Number:
e0b7d0ec-3ba5-5700-8613-16d1d52432dc | note | Is the location as per dimensioned reflected on the ceiling plan/ install plan?
b6771a53-ba7b-58d5-945e-02a2c4186b1f | note | Are the Sprinkler temperatures and finishes appropriate for the environment?
8ecfbdc8-c820-5ceb-9e1b-93f06704a790 | note | Maximum spacing from walls is not exceeded
f9a1fd23-76c3-5dc8-99d6-7b4990e57cb4 | note | Is the wall spacing within requirements?
a5008352-ef33-5a5d-a459-348a42ae3b09 | button | Is the spacing between sprinklers within requirements? | Yes, No
f3915efa-f2da-50de-a08d-6b82dfd46649 | note | Add Photo
db7d4c09-f136-4532-9042-ed3e2896c4b3 | checkpoint | 2. SOLID SPRINKLER DROPPERS
e633a7b4-6b13-5ce8-a97d-291f54890a10 | note | CIBSE W5.2 State of the System
b5d0d82e-3c5c-5f19-b8ce-f884b7175464 | note | Is the arm piece supported by hangers?
bd7fb1a7-8700-532d-9aff-e5b3ea1fc732 | note | Is Dropper square?
7b049efa-96ac-5d09-822c-ed251f72ad7e | button | Is the finished sprinkler height compliant? | Yes, No
c59a421c-b486-532d-8cb4-e84991073437 | note | Add Photo
c8119f05-0d4d-46e7-b724-ce7798e7b5fe | checkpoint | 3. FLEXIBLE SPRINKLER DROPPERS
554b5896-3934-5be1-aee4-4e0e4e3d8710 | note | CIBSE W5.2 State of the System
a7ccf36e-9a0c-568a-9c62-8736553a7598 | textbox | AS2118.1-2017
410b6de1-603a-5f04-8494-a6f94e1c3bc9 | note | Has the appropriate lengthed dropper been used?
2952ac1c-1956-5bbf-9c64-d1090b9fb6ae | note | Are Sweeping bends within tolerances?
1fb6c46e-a954-54a3-801f-64d65a6d4594 | note | Was the correct bracket used to secure nozzle?
5d9f77bf-8d8c-56af-a7e1-37b6c3874224 | button | Is the finished height compliant? | Yes, No
00dc5a1b-e3f7-55fe-ac27-ab0c395d7fe3 | note | Add Photo
33b2f51b-99f0-44e6-acea-cbd8aad7e7df | checkpoint | 4. OBSTRUCTIONS
c3140703-0771-5673-8263-ce8aabf2246f | note | CIBSE W5.2 State of the System
97730376-4e8f-5f73-af44-21e11c71f8ed | note | AS2118.1-2017
ac868ca2-e28f-5d52-8800-1cd8e5280459 | note | Has minimum clearance been maintained for 'On Ceiling' obstructions?
d1efb6fa-0b56-5791-98ad-d34f64dffd1a | button | Has minimum clearance from sprinkler been maintained for 'Below Ceiling' obstructions? | Yes, No
5a3036b8-18a9-57b7-a36a-ae502df155eb | note | Add Photo
22eef1d6-d118-4839-aa93-978b1d5f4a78 | checkpoint | 5. ESCUTCHEON PLATES
83244d82-1d86-554a-9371-3c970b66dde5 | note | CIBSE W5.2 State of the System
9a121dc9-c9b2-528c-bba2-40419c5512a1 | note | AS2118.1-2017
72cd0b60-fa9e-582a-bed2-22c297242394 | note | Have outer escutcheon plates been fitted?
bf52ec7f-5943-571f-b892-73871a1fcfc9 | button | Is surrounding ceiling clean? | Yes, No
0f389df7-d6c5-5e84-aceb-241fa789b97f | note | Add Photo
00f82dfd-5c3e-4164-b260-71ee63de9986 | checkpoint-no-value | GM Fire Sign Off
9846dbf5-fae5-436f-8b62-11ed3c6c649c | signoff | GM Fire Sign Off
f56b34ed-9f8f-436c-b719-fc051d3a1878 | checkpoint-no-value | Principal Contractor Sign Off
7161e3c2-d09b-4af5-aad5-955b8690e690 | signoff | Principal Contractor Sign Off
176bb996-ec14-4937-9e7f-e89e9c60f203 | checkpoint-no-value | Consultant Sign Off
828550d4-3eee-48c5-884b-44fc15fa915c | signoff | Consultant Sign Off
55a1e78b-f41f-41c8-acf1-dd6da6480dc2 | checklist | ITPS-109 Portables Fit off |  | ITPS-109 Portables Fit off
bae71d29-d728-4dd0-bf72-1a86cdc15492 | section | Details
38308eef-a9d1-4381-ab66-8843565a60a8 | checkpoint | 1. FIRE EXTINGUISHERS - GENERAL LOCATION
bd702e4f-9570-5e0f-9da7-9919de13ff19 | note | CIBSE C5.2.2 Set Points
a1c71886-9353-5402-8644-ba40bff50ed3 | note | AS2444-2001 - Section 3.2 states extinguishers shall not be located in positions where access could present a hazard to the potential user.
bb7edc6a-e61c-553c-8336-76140e75823e | note | Is each extinguisher located in a conspicuous and readily accessible position?
9780d046-8ecb-5eaf-93e9-b9379c2a4b3b | button | Where practicable, are extinguishers located along normal paths of travel and near exits? | Yes, No
522ae07b-4551-5053-be2d-1f6cf49ec538 | note | Add Photo
ae97aad0-beff-4c33-ba6a-01a0b11ac8d3 | checkpoint | 2. FIRE EXTINGUISHERS - MOUNTING DETAILS
8f71c931-1b28-5e76-920d-09817138b789 | note | CIBSE C5.2.2 Set Points
40a8f570-452d-5ab6-90bc-f86dcc763b6e | note | AS2444-2001 - Figure 3.2
7f5e469e-e8f7-5045-ba52-ad4b7ccc1018 | note | Have Location Signs been installed at a Minimum of 2000mm off the FFL?
8e06f351-3917-57fc-b34c-1169946915a8 | note | Are extinguishers installed at a maximum of 1200mm to the top most part of the extinguisher?
7451648d-b30f-5ae2-89fd-014502fba881 | button | Are extinguishers installed at a minimum of 100mm from the FFL to the bottom most part of the extinguisher? | Yes, No
2c940e95-c017-5a11-9c16-bf6c74b40925 | note | Add Photo
13dad942-4d3d-43c5-9b14-c3249ef6dcc7 | checkpoint | 3. FIRE EXTINGUISHERS - VISABILITY & SIGNAGE
4067ed47-72a8-5006-bf68-20c8c729122d | note | CIBSE C5.2.2 Set Points
282e2104-03a5-5e25-83b3-6a52a6f06ac7 | note | AS2444-2001 -Section 3.4
623433e3-c4c7-55b4-9965-4e039b50cffd | note | Are extinguishers, or extinguisher location signs, visible from a distance up to 20m in all directions?
f258aad9-8a92-5e6c-b045-d950506400ce | button | Are the location and type of extinguisher signs installed as required? | Yes, No
832e6237-49aa-558c-a22d-a162d5786907 | note | Add Photo
12dae432-a2a4-4064-a3bc-4461937b74ac | checkpoint | 4. FIRE BLANKETS - GENERAL LOCATION
af045d53-d679-5cbf-8f34-f8f5794361d1 | note | CIBSE C5.2.2 Set Points
aa91b5b0-2ee4-59c9-b791-b30c52285b10 | note | AS2444-2001 - Section 6
b9016263-19af-5ed7-88dc-1f4c58f95982 | button | Are Fire Blankets installed in a readily accessible position, and not in a location where access could present a hazard to the potential user? | Yes, No
cffc9694-8831-5357-b821-281cb12f08d5 | note | Add Photo
7eaa53c4-c3bd-48c6-b549-a706c633b2b4 | checkpoint | 5. FIRE BLANKETS - MOUNTING DETAILS
767ef4f6-a379-56ce-8335-bf35c6eef86a | note | CIBSE C5.2.2 Set Points
aca2cfb8-1809-5fc0-80fe-16b81c7e57a4 | note | AS2444-2001 - Section 6
17d2adac-857e-5126-beb2-93c5a70ca234 | note | Have Fire Blankets been mounted to withstand the loads imposed when removing the fire blanket from its container?
82318112-f546-5ab9-9d44-bef418c47b40 | button | Is there sufficient room so that fire blankets can be quickly removed without impedance from nearby obstructions? | Yes, No
6b896f05-b570-58dc-9234-8b97c34ef420 | note | Add Photo
2ed3edda-ff40-42c6-bc6b-08f9da6f1d93 | checkpoint | 6. FIRE BLANKETS - SIGNAGE
94acd923-b177-59b2-b136-06d8c78cea1c | note | CIBSE C5.2.2 Set Points
3ff4e845-7531-52d5-a420-8d1e7a43b427 | note | AS2444-2001 - Section 6
cc7707e3-684f-5199-a5e0-be4c831c9eb0 | note | Are signs located above or adjacent to fire blankets?
25fca8cd-f159-5416-aa06-e7fbf31e54e2 | button | Are signs 2.0m above floor, or at a height that makes them most apparent to the average person? | Yes, No
f2ccb43d-db86-5ae9-a754-48bc6db11b17 | note | Add Photo
d5129567-5ab6-4a14-a173-6535be0661ea | checkpoint-no-value | GM Fire Sign Off
880749f0-6bcc-4522-9fb1-dca58a5df65b | signoff | GM Fire Sign Off
a23dbd07-da1b-48ec-9ee3-c25ee7a3a955 | checkpoint-no-value | Principal Contractor Sign Off
f7a990a8-910c-4d75-80b6-d402d2713c47 | signoff | Principal Contractor Sign Off
4196f1df-7b77-4730-b5e6-897fa26e12fd | checkpoint-no-value | Consultant Sign Off
63b8834f-95e8-4240-9cbf-ab5d80ef3035 | signoff | Consultant Sign Off
5c13bde6-ef36-448a-a186-62c8b93faead | checklist | ITPS-110 Valve Set Installation & Fit Off |  | ITPS-110 Valve Set Installation & Fit Off
5d942561-352a-4b52-a37d-c55d01d9e8e4 | section | Details
d02c01a1-0123-4f2e-8bd6-8a9c61f72efa | checkpoint | 1. UNDERGROUND SUPPLY
e924bc0b-5a56-5307-a97f-81561964459b | note | CIBSE W5.5.2 Flushing Procedure
59cfc609-cd54-545c-a66b-1b639e367e87 | note | AS2118.1-2017 - Section 7.9.7
a506b9ee-3311-5f35-865b-b6c9556f2187 | button | Has all supply pipework has been flushed by a hydraulic contractor? | Yes, No
1ebd3604-120a-574b-b668-08f765704302 | note | Add Photos
979ede1f-1768-4f4f-9252-8aaf7e796e9f | checkpoint | 2. CHECK GROOVES DEPTHS
f48c48ba-529c-59ac-b8e8-517390bd7a48 | note | CIBSE W5.2 State of the System
79b6ad3b-fa9a-53d5-a83c-8c5c5b2eebb9 | note | AS2118.1-2017 - SPRINKLERS: Section 7.1 | Yes, No
09b3756e-f660-5685-9032-4af75bcc71a2 | note | Has Victaulic Groove Tape been used?
6447ff86-8b9e-582e-b46c-9d2e9e69e262 | note | Are Groove depths are within tolerance?
f2f3188b-31ca-5f17-bdb0-cac08e06ff53 | note | Are Pipe heights correct?
799ca61c-6167-59b5-a31c-d56f83fbbeca | button | Have Pipework alterations been approved and recorded for as-installed records? | Yes, No
e4b5835e-1655-5b85-978b-682fd38505c5 | note | Add Photo
63a244d0-0285-4d19-a670-dde8e5f15ada | checkpoint | HOLD POINT
6ce7da56-9bf6-5ec2-86ab-dc4242854b9a | button | Confirm Safe to Proceed | Yes, No
40b91b69-e954-4913-a490-6dfee902b700 | signoff | GM Fire Sign Off
55c3ef03-1050-4604-8ecb-d5f3c956490e | checkpoint | 3. VICTUALIC COUPLINGS INSTALLED
8737b33f-ba6b-5caa-ac0d-626b1331c0e2 | note | CIBSE W5.2 State of the System
e42d67be-6249-5401-90dc-ac3dc43f7727 | note | AS2419-2005 Section 8.3.2
b32607da-781d-5696-bdaa-461e80b0854a | button | Are Victaulic brand couplings the only couplings that have been used? | Yes, No
a262fbb6-f721-5d3f-bff4-e263661c21bf | note | Add Photo
c7c73c4b-4e0e-4ed8-9d55-4496fc18e5d8 | checkpoint | 4. CONTROL VALVE ASSEMBLY
399e1f8c-f46f-593e-8ed8-9d0326379778 | note | CIBSE W5.2 State of the System
a3f2470e-adb4-5924-b35e-325a7b9cd64a | note | AS2118.1-2017 - Section 8.1
602041ed-e593-5f4b-ad77-2142afac99a3 | textbox | Drawing Reference and Revision Number:
18d23c2b-217e-52bc-88fd-331cd87ade7a | button | Is the assembly is installed as per drawing? | Yes, No
c7e04dc3-9007-5e80-a08a-9f6b1f8dc1a2 | note | Add Photo
859d0f95-b6d0-451c-a366-6f9925f6b47a | checkpoint | 5. PIPE SUPPORT
3a50b6dd-e080-50fc-869a-398f41538096 | note | CIBSE W5.2 State of the System
eed2d615-3e99-55b8-9f38-602a1f7ec46d | note | AS2118.1-2017 - Section 7.8
11968b05-406d-503c-b808-78b956606e56 | note | Are pipework supports as per drawing?
e62f90df-5299-507c-b544-084e2dd0d8cd | note | Are the supports capable of supporting assembly weight?
8cb7435f-4986-53ba-83ae-43a9736b3b4e | button | Are the supports capable of withstanding forces during operation? | Yes, No
ed305e05-2671-5af2-b014-c67ce8c9845d | note | Add Photo
b75acf93-6aef-4682-bb89-a26ef3acdd52 | checkpoint | 6. VALVES
ce009ff2-b641-5eca-9442-9b9e94caa702 | note | CIBSE W5.6.2 Mechanical Checks: Automatic Control Valves
752d2c96-eb85-5419-bcaa-0ffa0a8703f8 | note | AS2118.1-2017 – Section 8
68b6731e-a3e8-5738-a68d-6a58ccf1dbd9 | note | Are Valves installed as per drawing?
d3b657b1-7ece-518b-bff0-40b2be341a63 | note | Are valves are installed in the correct orientation?
f148f02e-64c4-53ad-92f8-3acd5ca7cf43 | button | Does the clearance allow for manual operation and future maintenance requirements? | Yes, No
bbf33a0f-f90f-5563-abbf-01adde59e56a | note | Add Photo
5d681ec4-654d-458e-a704-b7da8ed2ec98 | checkpoint | 7. INTERFACES
84b10d69-0f20-5f3e-84c9-837a9c74bfe8 | note | CIBSE W5.6.2 Mechanical Checks: Automatic Control Valves
048ca0ee-ed90-552d-813a-a924a1bddcc1 | note | AS2118.1-2017 – Appendix H
df157825-ad8e-50e5-b46f-2a6323ef6219 | note | Are valves/switches installed for connection by other trades?
585bc3d1-c721-5113-a38a-34ad2ab1036c | button | Have clearances been provided for connection? | Yes, No
add6a446-3d9c-5fbe-bb02-e75cf095fba8 | note | Add Photo
77e43a79-13e8-407f-8562-71937ea9368d | checkpoint | 8. PAINT / FINISH
66883011-6d8f-59f1-8cf9-d53c37bf1261 | note | CIBSE W5.2 State of the System
b8b9c329-09df-588d-9fca-3ae5a16b55f0 | note | AS2118.1-2017 Section 7.9.6
06cda158-359f-530c-8812-720f32fd6272 | note | Are exposed mild steel pipes painted gloss red (unless specified another colour or galvanised pipe)?
20a24e41-af0a-5332-948c-f7c2bd0e34ae | button | Have threads been de-hemped and tidied? | Yes, No
a7a35f4d-73cf-5234-87a4-af1b48bd72ba | note | Add Photo
08777ee2-c55e-5f41-a1a2-827e64707765 | note | Add Photo
fb523181-cfff-4635-be6a-d7c0debdc407 | checkpoint | 9. SECURING VALVES
673da2fe-fb86-5ae1-8611-c87cdba1d03e | note | CIBSE W5.2 State of the System
4218a4dd-2351-50d5-87c6-a6fdb8627351 | note | AS2118.1-2017 – Section 8
3d05c733-c5fb-50cf-9c99-e5dae9dc3239 | note | Are valves secured by 003 locks?
a6a6c3de-1f86-5484-89da-079748827623 | button | Have straps and chain been installed? | Yes, No
a3056474-676a-5c65-9c20-147c9d17acc4 | note | Add Photo
3c78a599-b5ee-4aee-a3c3-8da815d40357 | checkpoint | 9. SECURING VALVES
7a10d8bf-e641-52bd-b7b3-50a8f18a842d | note | CIBSE W5.2 State of the System
d6f1f089-5347-54e3-88bb-d258561f64eb | note | AS2118.1-2017 – Section 8
ca967ba3-0f01-5d7b-b987-003146585483 | note | Are valves secured by 003 locks?
db1ec564-8b68-5795-a71a-e8b568c6428d | button | Have straps and chain been installed? | Yes, No
cfcd5e09-e315-54b8-b525-b89ebfddb24a | note | Add Photo
2a919009-460f-479e-b501-264edf57ec42 | checkpoint | 10. LABELS & SIGNAGE
fc71934d-31c0-5021-93e1-14cd535802f9 | note | CIBSE W5.2 State of the System
74212d3d-b920-538e-8fdb-a111811b42ef | note | AS2118.1-2017 - Section 3 (3.3.4)
7dfcbea2-4976-54a0-ace1-adbc6538851c | note | Are Equipment name labels secured?
e67e435a-f8cd-5aec-8b59-ed1bcc9f9ac7 | note | Are Valve position labels secured (normally open / normally closed)?
f19cd54d-461a-5e70-84f2-0bb4731c74f5 | note | Have "Sprinkler Stop Valve Inside" signs been fixed at the valve set enclosure entry?
6ab27a5c-835d-5407-9abe-e6ed6fa2811e | button | Has the Sprinkler Block Plan been installed? | Yes, No
d82d9531-a115-5918-bc41-0c35c379014e | note | Add Photo
a75d74c4-2e4e-4719-b007-eff640ed0319 | checkpoint | 11. SPARES
5663c72e-5037-58c4-86f0-733ca04954b4 | note | CIBSE W5.2 State of the System
a6228270-4ec3-5323-abf5-98d3857af472 | note | AS2118.1-2017 – Section 6.7
70c05bd1-2826-5dbc-9b9e-8d9a2e187b2f | note | Has the correct size sprinkler spares box been installed?
edf4b25c-37d6-5a79-9240-cfd5bc069996 | note | Have the correct number of sprinklers been provided?
fa9b01d0-6add-582d-aff9-a3ab4a222b02 | button | Has a sprinkler spanner been provided? | Yes, No
ea558f19-800d-50c2-b649-49bb81c417e5 | note | Add Photo
c0f8847f-3def-4453-9d4a-f88f37b96e8b | checkpoint-no-value | GM Fire Sign Off
78920d99-b2a7-43e2-a51d-fa200b4cdd5b | signoff | GM Fire Sign Off
c6c30b6c-4e55-4d0e-88bb-5e0dffc23ba5 | checkpoint-no-value | Principal Contractor Sign Off
1668a7f0-6c47-40f4-afdc-6789c4b22a36 | signoff | Principal Contractor Sign Off
7009acef-beab-449c-9975-b6b29008057d | checkpoint-no-value | Consultant Sign Off
e64d8d80-7471-44ea-89f6-47cec8803973 | signoff | Consultant Sign Off
2059ceb9-1800-4680-85aa-a13f3d4f14bd | checklist | ITPS-111 Tank Installation |  | ITPS-111 Tank Installation
56e364f7-c26f-4a82-bfa6-f1f3100da8a2 | section | Details
ceb9175f-516f-4393-b029-a5e559a1438d | checkpoint | 1. LOCATION, CLEARANCE, ELEVATIONS
423db5b5-6d30-55fb-98e9-ace22867205d | note | CIBSE W5.5 Pre - Commissioning
1899412a-ea4a-5ad5-8294-e51373a66c87 | note | AS2304 - Water Storage Tanks
71f05a77-ab31-5657-a929-1d66da87cffd | textbox | Drawing Reference and Revision Number:
da59488c-ed9c-54f8-9698-ffd6ff96e12f | note | Are Structural Elements as per AS2304 – Section 3?
414af547-1d49-5b1a-a10a-6ccdbb5d95c7 | note | Is the correct Installation drawing onsite?
4cb5c049-729a-5b7e-8e28-7e35c1943006 | note | Is Ladder selection and orientation as per the submitted design drawings?
7c647726-f6f7-5685-8658-ea98c29694a8 | note | Is Nozzle selection as per submitted design drawings?
da6c9d7a-e87a-5106-a9a9-7de5b934f9dc | note | Has the poisition of the Tanks been confirmed with the Principal Contractor onsite?
446ed047-e002-54ec-b7df-e54ac2644dbe | button | Have you check the subcontractors Competencies and Authority to work? | Yes, No
3271cb81-cc53-5432-b22c-d0b13537f783 | note | Add Photo
aa75fd74-0718-4fe0-9914-9359d404adae | checkpoint | 2. COMMISSIONING
964ee2d4-3df3-54c3-ba90-44b1a4e6e668 | note | CIBSE W7.10 Commissioning Certification
f6fc6baf-e9b2-52f4-afed-8c254b8c3d98 | note | AS2304 - Water Storage Tanks
31282f27-f6bf-5cca-ba55-56c7ed7d5938 | note | RECORD, CHECK, INSPECT
9a8ec127-46f2-5a33-9010-b4b6ca8b3c2e | note | Structural inspection was complete prior to filling; and
1616bddd-16bf-5236-b739-7228d4f001eb | note | All ladders have been inspected for conformance and clearances and position of tank accessories (AS2304); and
765e0519-0d1c-55e3-9610-2bd6d01fcd3a | note | Hydrostatic inspection was performed after tank is filled to maximum capacity; and
9129791e-5ae6-5a6d-be78-c5c1475ace67 | note | Any defects have been recorded; and
0f828215-6a82-59e8-99b8-de9c6bfd7b33 | button | Have Certificates and warranty periods been submitted? | Yes, No
3e9fc717-d153-58d4-ad79-4e19de6d97d5 | note | Add Photo
9cfdbf95-a36c-4a4e-81c0-f530ec819cc7 | checkpoint-no-value | GM Fire Sign Off
daf30f23-bddd-4acb-b8d3-b4ee4309f067 | signoff | GM Fire Sign Off
5a07b6f4-84c9-4ff2-8f2b-322ef5e3cf51 | checkpoint-no-value | Principal Contractor Sign Off
9e685fcd-8ad7-4726-a04f-dac566fdddca | signoff | Principal Contractor Sign Off
2ff7e553-8d3d-4b2f-828c-e66dd65a3111 | checkpoint-no-value | Consultant Sign Off
48344f06-5061-446c-8f09-d53b708f83d9 | signoff | Consultant Sign Off
82a38ec5-4fe6-48ec-b7f2-a8272bf18e2e | checklist | ITPS-112 Deluge Rough In and Fit Off |  | ITPS-112 Deluge Rough In and Fit Off
1944fa46-5b22-4aab-9612-e8d7e3480e7f | section | Details
c95f66ce-bc28-4638-90c1-737be686f2e5 | checkpoint | 1. LOCATION - VALVESETS
464c61cc-85cd-5b87-bad8-a2dbb8cf86c9 | note | CIBSE W5.2 State of the System
d05ba1e4-ce62-5720-80c2-0932acf57c35 | note | AS2118.3
4584b86e-1956-533e-b448-4c67c223f904 | textbox | Drawing Reference and Revision Number:
47bc9411-b5c1-5110-bb6e-92bc87962d28 | note | CHECK:
a3df50bb-1f32-543d-b912-14d504313cba | note | Valves located outside building shall be considered protected if the external wall has a FLR of 60/60/60 or be situated at a minimum distance of 10 m from the wall.
5f54fb14-dbae-53db-8b08-ac0dce70ea99 | note | Valves located inside the building shall be situated at a minimum distance of 10mfrom the perimeter of the protected area.
f7a91b14-9698-5fce-a9c9-eb9911db93e4 | note | TRANSIT TIME:
3a1d8644-61b9-5efd-a012-e236d0762dab | note | Deluge valves shall be located as close as practicable to the system they are controlling. This will help ensure that the transit time to the most remote zone is no more than 30 s.
4e3334f1-7b96-5a16-9617-b68c1164eb22 | note | Add Photo
091a682f-042a-484a-9a36-d4c8caa9f050 | checkpoint | 2. LOCATION- DELUGE HEADS
e59bd4e2-4e1a-5699-b993-f510cc07ba70 | note | CIBSE W5.2 State of the System
ec0bb32c-6199-5528-b1a5-f1ea599463c5 | textbox | Drawing Reference and Revision Number:
10e3bdb6-ea07-5455-b8b2-d3c56612f361 | note | Are Deluge heads located as per dimensioned reflected ceiling plan / install plan?
8c12b782-2f25-5048-a9e8-e6c6f825f490 | note | Confirm sprinkler temperature and finish are appropriate for environment; and
2a257b9d-61e0-5fe3-83f2-64532ce1a144 | note | Maximum spacing from walls has not been exceeded; and
b628b2fb-87c8-5e25-941b-d55d1dfa4620 | note | Maximum spacing between sprinklers has not been exceeded; and
e0a827fb-d786-52c3-b50b-176d805672ed | button | All is as per manufacturers detail and FER? | Yes, No
b2298182-0436-5084-904f-a189869a3a00 | note | Add Photo
b21450c9-61f6-4e82-8c53-a252fdedd295 | checkpoint | 3. DELUGE HEADS & PIPEWORK
5a609ac3-af95-5c57-9cff-7ef65490bba9 | note | CIBSE W5.2 State of the System
db012914-1b9e-56f2-9a4d-c8ab56ff08ca | note | AS2118.3
58f8c154-8bd7-572f-8767-5a5d2d61b9bb | note | Open sprinklers are be nominally 15 mm or 20 mm diameter, and either upright spray (SSU) or pendent spray (SSP) pattern only.
0cbba433-f10f-5ab7-86ad-25a1e4b99768 | note | Deluge system pipe and fittings not normally filled with water or foam solution shall be hot-dipped galvanized.
b9229bdf-9bdb-555b-a711-4b5faae509a5 | textbox | Deluge Sprinkler Head Type:
dc1e48a7-869e-56f2-b5bb-ad48321a12f0 | note | Add Photo
c94809b7-9e6d-44e9-967b-16cacd4a0ca7 | checkpoint | 4. WHERE SPRINKLERS ARE USED AS DETECTORS - SYSTEM PARAMETRES CHECK
aa009de0-730a-513f-a8b3-c108531acf6e | note | CIBSE W5.2 State of the System
d35d30c1-2b95-5e95-b325-b6f0fdbab32d | note | AS2118.3 Section 2.9
263e17a1-4bb8-5c8a-902e-2d3f04cfb473 | note | Where sprinklers are used as detectors, ensure the piping layout shall be designed to ensure a response time of no more than 20sec after the operation of the most remote sprinkler or manual operation.
3e9aa530-2867-51c1-b10c-f08d41aac2ce | note | Manual control shall be located at each deluge valve and at a strategic point/s within each zone.
eba0aa31-d3f9-5e32-a94c-99272b8147a0 | note | Deluge valve trim shall be in accordance with figures 2 &3 in AS2118.3.
fdc18e1c-3095-59c4-b8e5-a8264e3fd8ff | button | Ensure a remote test drain line is installed (close piping deluge systems) | Yes, No
a0085fb2-74b9-5232-8dfd-6a9b94c772d4 | note | Add Photo
67e1e660-da86-4cd9-bc34-4897802ee868 | checkpoint | 5. SOLID SPRINKLER DROPPERS
36c709d8-3418-5721-a1c0-16f595ead17e | note | CIBSE W5.2 State of the System
d359fe33-0ff2-5757-a3ed-7d5686be65a8 | note | Is arm piece supported by hangers?
b5238985-12bf-5f30-be1e-6b97107fe095 | note | Is the dropper square?
7dc9517f-c51b-5b52-8d74-66eba4ec5899 | button | Is the finished sprinkler height compliant? | Yes, No
9ba72a26-94ce-5399-8a71-c100fe10748d | note | Add Photo
abaed4f1-6a8e-48da-9d14-0c274438d86d | checkpoint | 6. OBSTRUCTIONS
ca60e962-62f9-5146-837a-d5d5d88ffbaa | note | CIBSE W5.2 State of the System
cf22fcca-f338-56cc-9896-77ba6718f728 | note | Has minimum clearance been maintained for "On Ceiling" Obstructions?
796aa4a6-ffeb-59cd-8180-beb493378c05 | button | Has minimum clearance from the Sprinkler been maintained for "Below Ceiling" Obstructions? | Yes, No
db0026aa-bcf8-4df4-b1e6-f98a7b3d3d9d | checkpoint-no-value | GM Fire Sign Off
740450d2-9784-41c9-855a-f38abce35c64 | signoff | GM Fire Sign Off
a5f63c2a-276d-46f8-b88d-ea28b850df5a | checkpoint-no-value | Principal Contractor Sign Off
0071c88b-5444-47ad-8abf-261d554e78ab | signoff | Principal Contractor Sign Off
82adb27c-0df6-4260-850c-3004a531e895 | checkpoint-no-value | Consultant Sign Off
b0a285eb-20b3-4405-8176-42df3b8b8d51 | signoff | Consultant Sign Off
d5d570a7-eaed-4798-9aab-f714d8581bd9 | checklist | ITPS-113 In Slab Sprinkler Sleeves |  | ITPS-113 In Slab Sprinkler Sleeves
93365276-b24f-4cb3-9c1c-c43c0d033c07 | section | Details
39b3643e-297e-415f-b08b-9655923a2fba | checkpoint | 1. TYPE, SIZE, QUANTITY - CHECK
46459667-7743-5da5-b26a-5c76f3ed4577 | note | CIBSE W5.2 State of the System
c314139f-541f-5861-8a99-054e5a146649 | note | AS2118.1-2017
ea38accc-61c3-5217-8421-6af21107cb39 | button | Are sleeves the correct size, type and quantity to criteria and specified drawings? | Yes, No
a6ae314f-5087-559e-97f9-3a77837ee6cb | note | Section 9.5.2
5e206a0b-949d-5358-a880-85e5ad8766ba | note | Has pipe with a minumum DN 25 been used;
a90e3e61-df46-5e92-8b73-c392dbd743a4 | button | Or where a pipe supplies a single sprinkler protecting an external balcony, canopy or carport, or supplies a single exposure sprinkler, a minimum of DN 20? | Yes, No
2e241a2f-1982-5021-887b-ec9dc601a298 | note | Add Photo
bd972cbb-bd0b-462f-8663-cde137cc9f45 | checkpoint | 2. LOCATION - CHECK
ac673425-6bdb-520a-9eb9-c984ce971f83 | note | CIBSE W5.2 State of the System
8ca6b18d-364e-5ee2-b2d9-1c0b512cb2e3 | button | Have sleeves been installed as per specified layout and design criteria? | Yes, No
24e6a011-99c3-5fcd-a912-66f7611b14fc | note | Add Photo
e093e351-8cb0-4159-847e-0c70ac639ff5 | checkpoint | 3. INSTALLATION - CHECK
9b7da228-66b6-552a-90b3-67ee9355f4cc | note | CIBSE W5.2 State of the System
4c08cb9a-6d94-5c91-aac4-35c4ab9bea7b | note | Are sleeves joined correctly and tied in?
2e5063c2-7999-5156-9c1a-5254b1ba2b70 | note | Have sleeves been checked for damaged?
0e28b019-c116-56d8-9501-ebc3009e8445 | button | Have you ensured sleeves are not resting on form work? | Yes, No
1566ecdb-0fee-535f-a087-0aa26925fc18 | note | Add Photo
d9d2edd9-c5e1-4244-87e4-b3d3336aa8be | checkpoint-no-value | GM Fire Sign Off
2bd21ec9-b32e-46e9-a126-538a4057bb6b | signoff | GM Fire Sign Off
7dc81a63-4724-49cb-a594-1bf7ffd89e17 | checkpoint-no-value | Principal Contractor Sign Off
8f7aeed5-6450-4c6e-b40b-75d8cefeb9f8 | signoff | Principal Contractor Sign Off
355e20f3-1900-4475-940c-6899fad06629 | checkpoint-no-value | Consultant Sign Off
2f6db261-d496-4958-b5ca-f57017114387 | signoff | Consultant Sign Off
e1e73fd8-5b5f-4f38-b46b-efe2f178861d | checklist | ITPS-114 ASD Rough In |  | ITPS-114 ASD Rough In
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
78c6a2dc-4200-4ae2-ae92-a37f24986549 | checkpoint | 1. LOCATION
7444cac4-98d7-5593-92b1-02d39e5c38cd | note | C5.2.2 Set Points
280cbc79-0738-5503-aa58-738fe7a316d4 | note | AS1670.1
398c09c5-8280-5e4e-9940-ebb27a6a59df | note | Have you check that the ASD device does not cover an area great than 2000m2?
80f70b29-1cf4-50ea-89b8-276efb0d7bcc | note | Is the ASD unit in an accessible location with no obstructions?
30e1042c-2aaa-5ea3-90f2-0abc4a01825c | button | Is the ASD unit free from damage? | Yes, No
a34d4b60-fa55-5ecc-b90d-66a0d70b9044 | note | Add Photo
716ebe38-1133-4e6a-8bd1-c7c3341dd5b5 | checkpoint | 2. SAMPLING POINTS
e02583dd-be2e-58d8-a5ea-aa92de4d124b | note | C5.6.0 Sensors/Detectors
7e0755a8-ad4d-5e84-b378-b49425561891 | note | AS1670.1
a0c4cfa5-1121-5fe2-a116-01d4e051e3b2 | note | Are ASD points unobstructed, unpainted and free of burrs?
5049fb57-c72c-5574-aaa0-15d80d6cdc0e | note | Have ASD points been labelled and identified as required?
2a3178d6-04c5-5440-885a-1e3a0a63fe9e | note | Are ASD points installed in accordance with spacings of point type detectors?
ad8091b6-66a8-5c35-8d58-5a29969f513b | button | Have you confirmed ASD points are no more than 600mm below ceiling? | Yes, No
8823ceca-77b8-5fdb-b037-01079cde759b | note | Add Photo
7f3b4a3e-102d-45d6-89e6-4e582f86eb42 | checkpoint | 3. EXHAUST
ef00a705-8975-5671-9815-d7bb6401415d | note | C5.6.0 Sensors/Detectors
555bdc18-7fb2-5ec7-a59d-51170f64bc24 | note | AS1670.1
480fe7e7-6516-5001-a953-0eaaf00248d1 | note | If the ASD is mounted outside the protected area and the potential for pressure differentials can occur between the sampled and exhausted air:
081f603a-87e2-5c3e-859d-f93e28bb42d7 | button | Are the exhaust outlets returning back to the protected area, or as per system design? | Yes, No, N/A
72e8ca01-bf03-55f9-a1d7-e4b6d7b55089 | note | Add Photo
9c51de65-39b8-4155-9052-ff792bf3b33b | checkpoint | 4. OTHER INSTALLATION REQUIREMENTS
e25eeeac-81f7-5830-99b0-cfd14d43ea25 | note | C5.2.2 Set Points
a4d8b8ab-6a34-54bd-8098-64def0cee3ad | note | AS3000, AS1670.1, AS3013, AS/CA S009
3b3d57b2-ceb8-5896-b37d-0d097d5dea4e | note | Are all sampling points AND capillaries red in colour OR have visible red stripes at least 2mm wide at intervals no more than 2m?
62c68d36-b6f5-53e0-bf37-c47e2ff26de4 | button | Is the pipe orientated to ensure identification of markings is visible? | Yes, No
2d4a3c9f-340d-5ebd-91c1-fb8b866bbe93 | note | Add Photo
07821b19-82c8-45c4-8491-543b5ef27d9a | checkpoint | 5. CABLING
e1d78a7f-c9e9-5a39-a21e-c1ab010638a9 | note | C5.4.0 Wiring
b66f95e9-8df5-5fe2-98a4-7d03d144f766 | note | AS1670.1, AS3000
7d1bcd81-d0a2-5f1e-8b23-e217ebbcf10a | note | Is the cable installed the correct size & type?
65caffb3-f56c-53aa-bd0b-9ce7e066eadc | note | Has cable been secured at regular intervals?
42e3006a-42da-579f-a3f0-63980210d790 | note | Has 24v cabling been installed where required?
07b61790-6105-5201-a779-86c7a0cfde1c | button | Is the power supply in accordance with AS1670.1 Cl 3.15? | Yes, No
e82caa11-686c-5796-a73f-3669948ef45f | note | Add Photo
2413d1cc-b8ee-47d7-b428-5f3b1a0309b4 | checkpoint | 6. PIPE LAYOUT
2a51e3d0-9192-5d8c-9cd5-0100f90dd29a | note | C5.2.2 Set Points
6a83aec7-83da-518f-9d74-7a9734b50f6a | note | AS1670.1
f0cef599-7d28-5ec8-81a3-714040800828 | textbox | Drawing Reference and Revision Number:
915ba364-33b8-5535-b3ce-7c9f847853c7 | note | Is the ASD pipework as per Aspires or Calculations?
52d9d227-1fe4-5e11-a704-e646c3a9c372 | button | Have you confirmed the pipework layout with measurements? | Yes, No
dd7881a8-c274-58de-8698-6aa50e31c7cc | textbox | PROVIDE measurements:
79683abd-2aff-53b8-a7a9-a4bed70f692f | note | Add Photo
8c5aeabc-3a0f-43ff-8a50-7d7ba020a8b6 | checkpoint-no-value | GM Fire Sign Off
112e2ce2-b86e-45ad-a4f7-89f495c7f0de | signoff | GM Fire Sign Off
c140c377-1014-415f-a1a9-0f708d9d93cf | checkpoint-no-value | Principal Contractor Sign Off
d97812b4-a4a9-4aae-a680-6ab24518ebe6 | signoff | Principal Contractor Sign Off
0bd20af6-74a5-4230-94e3-17b821319124 | checkpoint-no-value | Consultant Sign Off
1f56b3a5-ba18-43e3-b54c-d686e9ee98dc | signoff | Consultant Sign Off
9e22e938-8d08-4986-b742-1a94d4e6b80d | checklist | ITPS-200 Fire Detection and Alarm Commissioning |  | ITPS-200 Fire Detection and Alarm Commissioning
92b1fe8f-7c89-4b0c-8d9c-b176a6a42a0f | section | Details
670ebe51-7a20-45e0-adbc-a63dc4778618 | checkpoint | 1. CONDUCT 100% TESTING OF ZONING
8686b06b-2911-5c59-803e-3048d4692a60 | note | CIBSE C5.2 Dry Fire Commissioning – Automatic Controls
1dcaf204-678e-5c07-ba46-de77cd6d2c94 | note | CIBSE C5.2.9 Alarm Functions
3c65d2b9-edee-51d8-bbfb-e846e53be771 | note | CIBSE C5.6.0 Sensors/Detectors
ad99ec4d-2485-577d-9533-bddb8ecc50ae | note | AS1670.1-2018
f8e4e0ad-f882-5aec-9204-ba2ede096a8a | note | Are Detectors activated when tested?
4f490fd6-96c7-549c-ba36-60c2e22c2256 | note | Do indicators function correctly on Detectors and FDCI?
abe1e3b1-6a8f-551d-ada2-f1c4200ffa2c | button | Has "GMF-COMRPT-001 Fire Detection Zone Commissioning" been completed? | Yes, No
caedfcf8-7c63-51c1-a211-b61eae60b7c9 | note | Attach relevant photos and a copy of GMF-COMRPT-001 below:
788d76e0-b191-4e97-9884-76143f52f96c | checkpoint | 2. CONDUCT 100% TESTING OF SMOKE AND THERMALS
a3662efe-fa5f-56c8-9c53-b717491b0e82 | note | CIBSE C5.2 Dry Fire Commissioning – Automatic Controls
66043776-3f60-5d35-985f-11871f7cfd0d | note | CIBSE C5.2.9 Alarm Functions
d5909172-71ae-5102-933a-480bdfb111a1 | note | CIBSE C5.6.0 Sensors/Detectors
c2c72adc-9163-5aa4-b107-629e78d4b1d8 | note | AS1670.1-2018: Ensure Detectors are activated when tested and correctly indicates on the detectors and at the FDCI
b7a224be-0dd5-5fab-930c-91a72e10d86e | note | Are Detectors activated when tested?
49e64727-4c32-5a95-ac92-62b19c79337b | note | Have all dust covers have been removed from detectors?
f0db42b4-d52b-5675-b99d-9a115f4fca6f | note | Do indicators function correctly on Detectors and FDCI?
839c60ef-54db-53cb-bd80-5a2d18198520 | button | Has "GMF-COMRPT-002 Fire Detection and Alarms (Smokes, Thermals, Duct Probes)" been completed? | Yes, No
61299804-070e-5990-98a7-dd7a3bed7e07 | note | Attach relevant photos and a copy of GMF-COMRPT-002 below:
7a563a71-274a-4f63-b97e-8e7bade36ee8 | checkpoint | 3. CONDUCT 100% TESTING OF MCPS
973a7b8d-e5cc-5e87-bfe1-82b902bf7d51 | note | C5.2 Dry Fire Commissioning – Automatic Controls
bf0eef11-328d-5a1c-b517-aa49796e124c | note | C5.2.9 Alarm Functions
2030950e-a652-571f-887b-781aa06228b4 | note | C5.10.0 Manual Call Points
c415566c-fae4-5549-8e09-e824c9b4e9ef | note | AS1670.1-2018
59aa211b-e10a-5137-bb7e-33bb53741f56 | note | Have you checked:
49ead160-021e-5702-8032-c45ee3a76292 | note | The correct operation of each manual call point; and
31831b0c-fcee-54ac-bbcd-01738fc28e40 | note | That the activation of manual call points on the same circuit as other actuating devices does not cause existing detector alarm indications to be extinguished; and
74496c36-d70e-5d6b-953e-5e889ff05a1d | note | That manual call points are not subjected to alarm dependency; and
72d614ff-8d79-5c37-b9b5-632683ec1fe8 | button | Has "GMF-COMRPT-003 Manual Call Points" been completed? | Yes, No
51912044-cde0-538f-8e83-6bdc10840dc2 | note | Attach relevant photos and a copy of GMF-COMRPT-003 below:
ee8c9407-2d8c-4210-b719-e7ba4ef75e87 | checkpoint | 4. CONDUCT 100% TESTING OF DOOR DEVICES
d3d78a61-7d34-5023-8fc8-b075856ec0c3 | note | C5.2 Dry Fire Commissioning – Automatic Controls
cc47435b-f82a-59c7-a2ff-9575255833e2 | note | C5.2.9 Alarm Functions
a6396b25-c39a-5ccd-9aa6-ca8e89bc4271 | note | C5.8.0 Modules Input/Output
ea3ace77-029d-586c-89f0-894e3b0e7336 | note | AS1670.1-2018
8c69bc59-a14b-5df4-8f31-6995347e3aeb | note | Has the operation of each device/door release been checked after install?
41ce1f7c-6550-5586-864d-ee6d82835496 | button | Has "GMF-COMRPT-004 M.D.H / Auto Door Commissioning" been completed? | Yes, No
2065fa91-338f-5de2-b2a7-d4477623333b | note | Attach relevant photos and a copy of GMF-COMRPT-004 below:
d9e0d8e3-4880-4ec1-a8b0-dbbb30095b60 | checkpoint | 5. CONDUCT 100% TESTING SPEAKERS AND ZONES
238a3e69-4235-5c9c-875e-c5710a242332 | note | C5.2 Dry Fire Commissioning – Automatic Controls
d166244d-3df1-58b1-a218-c2e13a749fcb | note | C5.2.9 Alarm Functions
561e8d47-bb96-509f-ad1a-e7536c370ae0 | note | AS1670.4-2018
b5f8945c-2775-51e9-b130-22d75d282092 | note | Have the audible signals, visual and tactile signals been checked? (automatic operation)
319ffd0c-76c8-55c3-a14d-3e361212c598 | button | Has "GMF-COMRPT-006 Emergency Warning Commissioning" been completed? | Yes, No
50a553c1-e7bc-5d7d-a768-4407efb71eb6 | note | Attach relevant photos and a copy of GMF-COMRPT-006 below:
df08f181-7afd-4c2b-8684-4d7f62e7d5e7 | checkpoint | 6. CONDUCT 100% TESTING WARDEN INTERCOM PHONES
e41d3cde-e66c-5ec1-afd4-f6a27783ad24 | note | C5.2 Dry Fire Commissioning – Automatic Controls
a10ce05d-6af1-595e-803e-7c10b89a5133 | note | C6.2.8 Warden Intercom Phones
3ab8227c-a791-5e35-9d8b-ed4857a8f0f4 | note | AS1670.4-2018
d7292231-bf39-59b2-955f-97875ae96b27 | note | The WIP audible call signal shall have a SPL of not less than 80 dB(A) when measured at a distance of 1 m from the WIP.
723c0292-f143-5da9-a857-30b23258e796 | note | The SPL of the WIP handset audible call signal shall also be met when the WIP handset is mounted within a security enclosure.
5df65415-1045-532a-afdf-9f3181519ef7 | button | Has "GMF-COMRPT-007 Warden Intercom Point" been completed? | Yes, No
9d2aca89-555f-5480-abb5-027287e5ed8c | note | Attach relevant photos and a copy of GMF-COMRPT-007 below:
b565d282-f91f-4f8c-9cb6-9e193dd3e441 | checkpoint | 7. CONDUCT 100% TESTING CASCADE AND EWIS ZONING
f787cc5b-64ea-5c7c-af4b-b2e3cddb4f30 | note | C5.2 Dry Fire Commissioning – Automatic Controls
a8506e82-cc69-537f-b9dd-bb20828878a2 | note | C6.2.5 Cascade Sequence
f3fa0265-e566-528e-8959-3b02a611deee | note | AS1670.4-2018
71ae6d0b-7daf-58b9-9614-119412d6e131 | note | Have the audible signals, visual and tactile signals been checked? (automatic operation)
2f203db6-c652-5412-b067-372eedf85a2b | button | Has "GMF-COMRPT-005 Emergency Warning Cascade and Matrix" been completed? | Yes, No
477f7f4e-cdca-5f01-8c8b-23ed222d9bef | note | Attach relevant photos and a copy of GMF-COMRPT-005 below:
aa562d94-5751-45cf-a6d9-b90d8725fe74 | checkpoint | 8. CONDUCT 100% SPEECH INTELLIGABILITY TESTING
db12342e-cf26-58af-a890-7c8ce45280d6 | note | C5.2 Dry Fire Commissioning – Automatic Controls
ac1413e1-40b9-593e-a2cf-d38bca4c8d18 | note | C6.2.5 Cascade Sequence
aaacdc48-6e5b-5579-8566-c36fee45f076 | note | AS1670.4-2018
c65bdd64-393c-520a-8096-17122983ad9d | note | Have the audible signals, visual and tactile signals been checked? (automatic operation)
55685784-a321-56ee-b639-bb84545d2869 | button | Has "GMF-COMRPT-008 Speech Intellegability Readings" been completed? | Yes, No
a7f05a12-9116-5406-8d4a-6ca2aa7179e5 | note | Attach relevant photos and a copy of GMF-COMRPT-008 below:
92592713-ad9e-45f1-b764-84c943d8dc22 | checkpoint-no-value | GM Fire Sign Off
326fe5af-cdf2-40c1-988a-abc6b02297c6 | signoff | GM Fire Sign Off
2adc5fdb-05b3-45c6-a02e-674cc99099a0 | checkpoint-no-value | Principal Contractor Sign Off
f7d22a18-caf0-4cea-afaa-348245ac15a9 | signoff | Principal Contractor Sign Off
8f027204-bdbd-4f51-a814-c7474a7006a4 | checkpoint-no-value | Consultant Sign Off
2e5c3489-fd31-4784-b8d0-997f2bb5b369 | signoff | Consultant Sign Off
0bc82b69-5f25-484c-be23-a067a4d31967 | checklist | ITPS-201 Interface Commissioning | itp | ITPS-201 Interface Commissioning
071ba445-3e3f-4b99-9016-b5779b0b4eb3 | section | Details
351d42fb-a2e7-464d-a664-7fb826b16576 | checkpoint | 1. CONDUCT FIRE MATRIX TESTING
b551a101-79d9-5ece-ba50-8548ac93d2d0 | note | CIBSE C6.2.4 Fire Matrix
57782cd7-c95d-51a6-9722-074a59819843 | note | AS1670.1-2018
6b730da2-fe83-5911-959c-59ff7e2bda9a | note | The ‘end-to-end’ test should include the activation of associated detection devices to confirm that all required functions operate correctly in accordance with the system interface matrix.
ad5c9024-13d7-5461-a536-910c77e2c6ef | button | Has "GMF-COMRPT-009 Systems Interface Matrix" been completed? | Yes, No
d46783d2-39d4-5503-b04a-0b75fb1fab48 | note | Attach a copy of GMF-COMRPT-009 below:
c3aa5017-c502-4390-8bc4-9c651ab313f2 | checkpoint | 2. CONDUCT FIRE FAN CONTROL PANEL AND BRIGADE INTERFACE TESTING
29605bdf-857d-59cb-822e-7a72a2b03207 | note | CIBSE C6.6.0 Brigade Interface – FFCP
26a05699-1561-5831-965b-f436e7dea21d | note | AS1670.1-2018 Appendix A
05620425-a064-58af-8b5f-2a231cdd92d0 | note | Check Fan Control Operation as per Matrix.
e0319afc-3b6f-53b1-8389-3cd201f56f6c | button | Has "GMF-COMRPT-010 Fan Control Matrix Testing" been completed? | Yes, No
6d6eb604-ad88-5c5b-8cef-579961f5a359 | button | Has "GMF-COMRPT-011 Fan Control Overrride Controls" been completed? | Yes, No
61ed7f36-979f-5a93-90b7-af44379539f3 | note | Attach a copy of GMF-COMRPT-010 and GMF-COMRPT-011 below:
96c5ca4f-7d45-4447-bdfb-eaf4597390f2 | checkpoint | 3. SPRINKLER INTERFACES FITTED OFF
e6fa1b03-39ce-54f4-8c59-5b834fa5fe9b | note | CIBSE C5.8.0 Modules Input/Output
779e33d3-692b-5459-92c7-6dc04863febf | note | CIBSE C5.2.9 Alarm Functions
9451eff4-9c81-551c-a682-641656c48c5a | note | AS1670.1-2015
62156d37-ee7f-5106-ab39-778ac58013a1 | note | Prior to any interface testing, have you checked all systems listed in the system interface schedule are complete and operable?
9c0f5439-8a11-537d-887c-6eb9b1ec1e06 | note | Have you checked all systems interfaces to the FDAS?
fdbb3997-6ea1-5e9a-87a7-8833dfe0de4f | note | Has "GMF-COMRPT-020 Sprinkler Zone Commissioning" been completed?
d152edf9-8b93-501f-bd9c-cc576bf3b162 | button | Has "GMF-COMRPT-021 Pump and Tank Indication" been completed? | Yes, No
782c8e79-62ae-528d-938c-78d462d7d6be | note | Attach a copy of GMF-COMRPT-020 and GMF-COMRPT-021 below:
3204321d-6063-4bd6-8dd6-7df9718e9b0c | checkpoint-no-value | GM Fire Sign Off
1fc7b52d-c7e0-426f-a951-f311531bfcb3 | signoff | GM Fire Sign Off
1534743e-0996-4032-82da-608f5fe5f620 | checkpoint-no-value | Principal Contractor Sign Off
3965b173-0ca6-4e1e-be4d-8abf1a10df5d | signoff | Principal Contractor Sign Off
e9a8b6f9-c94f-443a-9e9b-ae47a23b2354 | checkpoint-no-value | Consultant Sign Off
3264a182-9c5f-454e-9121-3d1295f2c7c3 | signoff | Consultant Sign Off
0af7f7bd-f281-4f45-a083-a3d7e9e01a60 | checklist | ITPS-202 ASDS Commissioning |  | ITPS-202 ASDS Commissioning
da725858-b227-44be-b143-815b281598c9 | section | Details
19927976-88a0-49e4-9d5c-9b3cee3100a2 | checkpoint | 1. VISUAL INSPECTION
65de9628-9efc-5f9a-bd3d-e9dd60734459 | note | CIBSE C5.6.0 Sensors/Detectors
130c82f6-f2ff-5d64-ba92-1cc156695ad2 | note | AS1670.1-2018 Appendix A
392fd07a-1f0c-52d9-aed4-400b96c1796c | button | Have you visually inspected every sampling point to ensure it is not obstructed? | Yes, No
5c229693-d840-5b21-b7d6-e3db42413d0b | note | Add Photo
c0546a84-6f19-45f8-a355-e25558a0293e | checkpoint | 2. ALARM TESTING AND TRANSPORT TIMES
d1461450-3c94-5007-a088-4ec5b22b50ed | note | CIBSE C5.6.0 Sensors/Detectors
31e3b1f9-abaa-53d6-8d98-a480b841915c | note | AS1670.1-2018 Appendix A
fd9a8702-c7e7-5c1b-a83e-3ad1712bd77c | note | CHECK AND RECORD
e22f04cf-c5bf-5ff6-a744-dd548c818e62 | textbox | The response of all capillary sampling points using a test medium placed at each sampling point:
03771667-a3d3-57b3-9c25-b98d5e5e4014 | textbox | Measure and record transport time (TT) from the EACH sampling point:
ddd4108d-ab90-564e-911d-3e93a18d9ca4 | button | Has "GMF-COMRPT-012-ASD Commissioning" been completed? | Yes, No
be9768e1-b8e0-57f5-98a9-f4461af34e74 | note | Attach a copy of GMF-COMRPT-012 below:
a9093d71-0eab-4b21-999b-f719ced4616d | checkpoint | 3. OPERATION - ALARM, FAULT AND ISOLATE
67e8b1fd-3ddc-5089-baa1-3117feee106d | note | CIBSE C5.2.9 Alarm Functions
1bea7aa5-2f28-5a12-b938-26fb8aae54bc | note | AS1670.1-2018 Appendix A
6dd1ee00-741c-5ef2-a8a4-d3aa9c7764ba | note | Have you checked:
6cfeb5e3-1695-531e-9f86-7c3a9939ba90 | note | The operation of remote indication of alarm and fault signalst; and
912f40a2-e674-51b3-bbd7-a4694cebb5bd | note | The operation of airflow failure indicators; and
362d6020-5f40-5499-99a9-4adc40ce10de | note | The operation of the system failure indicators; and
3f82d29f-635f-5c77-90c8-e3c0588bb7e3 | note | The isolate and reset functions; and
5d0526b7-8516-5e03-83d2-081e31993605 | button | The fault and alarm test facilities (where provided)? | Yes, No
b608d23a-89c3-4ea7-baf2-0cdf94f9f1e6 | checkpoint | 4. ASD MATRIX (If Applicable) - Including Thershold Testing
da922a9e-baa6-5662-90cf-6dc2b36e02d9 | note | CIBSE C5.2.9 Alarm Functions
a8fe7b58-f4f7-560b-94ed-9a28896b0c2a | note | AS1670.1-2018 Appendix A
3f2d644d-e8b7-5e62-a6cd-d05d068eb43b | button | Has "GMF-COMRPT-013 Double Knock Testing" been completed? | Yes, No
c988509f-659b-5f93-9233-3c9727f3e604 | note | Attach a copy of GMF-COMRPT-013 below:
e1f49d10-80a2-4ed3-9264-8f9b13d1eb06 | checkpoint-no-value | GM Fire Sign Off
486f688d-66fb-4ccb-ad22-c53a2417aac8 | signoff | GM Fire Sign Off
432e12d8-1eb1-4b55-9024-87ed598787e0 | checkpoint-no-value | Principal Contractor Sign Off
d4a829a4-837e-48ed-aaa9-cdf49558a5d4 | signoff | Principal Contractor Sign Off
989d8672-9c0c-4e33-8555-2472a831600f | checkpoint-no-value | Consultant Sign Off
95c70f3d-e0fb-4367-9189-46e69986f7d2 | signoff | Consultant Sign Off
b518705d-c53f-4236-a3bd-2f3c958c4db2 | checklist | ITPS-203 Pipework Pressure Testing |  | ITPS-203 Pipework Pressure Testing
8985bc4d-4cd1-4827-8a6a-d504aecef02c | section | Details
6c3c9ac2-a9f9-4f14-a356-cef6bbed0855 | checkpoint | 1. SCHEDULED TEST IS APPROVED - CONFIRM
0552a92f-5700-5d73-8a84-0d6e86af6979 | note | CIBSE W5.5 Pre - Commissioning
a74dac25-77d8-5d89-8f44-95c9ca665978 | note | Have you received Approval for test time and location?
f7850cd8-c01d-5c1e-82a7-d3a1ad22f896 | button | Has the site been notified? | Yes, No
e6f729e7-bbc6-5a75-96ed-9aacb49d8887 | note | Add Photo
cafec96d-9852-480c-b268-b7119097b30c | checkpoint | 2. EXCLUSION ZONE - CHECK
d2086720-a7f5-5736-80c4-3f7173adb84c | note | CIBSE W5.6 System Checks
ea30edff-311f-5d6c-8908-cd5ff3497ea1 | note | Has an Exclusion zone been set-up?
34ea636c-c09d-54d1-81c0-2ace8becc430 | note | Have you erected appropriate barriers and signage?
9ff74dcf-b5da-515e-806c-965912d0dcde | button | Have all workers/occupants been notified and have they exited the area? | Yes, No
d859e37d-6956-508e-9394-f0b4bac86b08 | note | Add Photo
81ea02e2-91b3-4d5e-9971-b5ece95ef8b0 | checkpoint | 3. VISUAL INSPECTION - CHECK
b94b2385-0a8c-50e3-be03-ef4fdd92c8c3 | note | CIBSE W5.3 Check before Filling
571e97e2-a7ec-5b04-862c-426ca3c64d27 | textbox | Drawing Reference and Revision number:
396c8b20-3dfc-5973-b3c1-9df704079618 | note | Is Installation complete?
1f8c99b7-6bff-52c7-aafc-d574e3fe5258 | note | Have End Caps been fitted with lockable ball valves? (BLANK END CAPS MUST NOT BE USED)
9110a9a0-ad5b-5d11-9145-83261969d336 | button | Are all outlets sealed? | Yes, No
a7cab62e-fd84-5352-84e1-7ca5d75990ed | note | Add Photo
ac846062-069e-4d38-8292-873509b921a6 | checkpoint | 4. FIT TEST PUMP AND CALIBRATED GAUGE - INSTALL
ec6f5b5b-efef-5d5e-9361-6747b87fe28b | note | CIBSE W5.3 Check before Filling
4b938c60-0fbf-53ff-b234-40463cde639f | note | AS2118.1-2017
b6ceb0bd-58fc-5206-b86c-b8b489dd9812 | note | Is the Pump installed in a safe location?
2572f4f5-c82c-56af-9997-5a31d0baf906 | note | Is the Callibrated gauge in visible location, and accessible to photograph?
4a9eea49-74e9-596b-ad18-200725d542c8 | button | Have the Pump and Callibrated gauge been tested? | Yes, No
9725e8ee-22e6-51db-93ed-04f0ff1d637f | note | Add Photo
7ebade1a-dc2e-4d6d-ad3c-9495fffdf82d | checkpoint | 5. CONDUCT BREATH / LUNG TEST
beb3305d-7c06-5ac5-8f16-87f72fd5d55a | note | CIBSE W5.3 Check before Filling
c6b70bf1-f000-5606-a6bb-2e1fb3c3cec0 | note | AS2118.1-2017
a2176b11-c671-5e53-a7e2-7669820dc23c | note | Perform Lung/Breath test where possible;
9cd092d1-a110-546e-ab0b-5ba7720c367e | button | Is the system sealed? | Yes, No
784f3bcc-77c0-5e23-a7bc-183b97ef72f9 | note | Add Photo
852e3284-7b49-466a-9aa8-da671e133d83 | checkpoint | 6. FILL SYSTEM - STATIC PRESSURE ONLY (OR AIR PRESSURE)
64d76aa5-9727-5788-8207-8660ec7af6e9 | note | CIBSE W5.4 System Filling and Venting
934d3ab8-6c19-5a42-b497-5b0a7c2dbf17 | note | Prime system to towns main pressure OR 300kPa (depending on test);
70b05a30-ca35-500a-9482-1be87aea553e | button | Are there any leaks in the test area? | Yes, No
d5045738-07fc-503a-b707-013e948bcb5e | note | Add Photo
f8ca983b-4f3b-4483-82bf-4c4adcd6fbdb | checkpoint | 7. START PRESSURE TEST - CHECK
25a9d7ac-8f61-5ddb-9835-2478cbced0db | note | CIBSE W5.4.1 Pressure Testing
f8cb4b3c-9af1-5634-926c-f467765ab450 | note | Increased pressure to 600kpa start pressure;
31b694fc-347d-568e-8c91-8b611ae4bd87 | button | Are there any leaks in the test area? | Yes, No
ea5ce428-a149-5d90-873f-ec0e1a4cf95c | note | Add Photo
15d19e64-5d99-4f23-97e8-9e30a8601792 | checkpoint | 8. INCREASE PRESSURE
c69e88c8-6f0b-53d2-b38d-a6cf90f1dac5 | note | CIBSE W5.4.1 Pressure Testing
08779b4a-c391-5ac4-8f30-bfb476f093bd | note | Progressively increase pressure in 100kPa incraments; and
ccab2c31-4285-59be-8277-45294e597c67 | note | Inpect test area for leaks at each increase; and
920263ce-43a8-52bd-a43b-a63d4d1255fe | note | Repeat until pressure reaches 1600kPa;
92d07555-b6a7-5bb0-9e3a-13822e7c4db7 | button | Were there any leaks in the test area? | Yes, No
62b811c2-6f10-5ce8-996e-141402290728 | note | Add Photo
bd4f02ab-5a8d-4bd1-a8a9-0f0bbe3be93d | checkpoint | 9. HOLD PRESSURE
ffd4c143-8718-56ac-ab37-9b6292dec615 | note | CIBSE W5.4.1 Pressure Testing
eb1a115f-43a8-5fa7-a263-4234250776db | textbox | Record Start Time and Photograph Guage:
07d9837a-eafb-58cc-af9a-9f1ca7b2de20 | note | Hold pressure for 120 minutes.
583d077b-27c0-54f9-9a9c-d6192cc1d4bf | button | Was there any pressure loss? | Yes, No
ebf6ef12-04b3-5b86-8f5f-ff5d14504f40 | textbox | Record Finish Time and Photograph Guage:
ac39800e-6432-5e5e-a37b-96dcd69a69de | note | Add Photos
a1a562bc-0a18-435f-896a-bb68c6cba1e4 | checkpoint | 10. DE-PRESSURIZE SYSTEM
7e68afd1-ff1b-55b1-8370-7aca03ce54d9 | note | W5.4.1 Pressure Testing
83164e45-7f7a-5551-a28d-a130e9c65627 | note | Release test pressure from system.
2d21ce28-0820-5809-bf13-337ccfcc29b9 | note | System remains primed with towns main pressure.
24fa4947-1771-5e1a-ac2a-f76c8977e01e | note | Add Photo
7a1fbc5d-f642-42d8-a2bc-2504f4bf9eb3 | checkpoint-no-value | GM Fire Sign Off
6760046b-d624-4bab-aff4-7ea13ae7677f | signoff | GM Fire Sign Off
29b48be2-12d2-4428-a484-9a24e2af0e5b | checkpoint-no-value | Principal Contractor Sign Off
346d1859-b0e3-4125-93ea-c0d27d3305e8 | signoff | Principal Contractor Sign Off
3b4dc6f3-9371-4000-8214-921b85931fbb | checkpoint-no-value | Consultant Sign Off
8bb088bc-760c-42d4-be8b-80c28b841ef3 | signoff | Consultant Sign Off
cd8fbcf3-20c2-4ec8-aea3-66936bf6d79d | checklist | ITPS-204 Electric Fire Pumpset Installation and Commissioning |  | ITPS-204 Electric Fire Pumpset Installation and Commissioning
159fa0ba-ae67-45c3-85ff-8005879b04c3 | section | Details
f57a5ce0-7ef4-47ec-a1e3-bbf7a8e24bd9 | checkpoint | 1. CHECK AND CONFIRM - LOCATION
c42a424c-60a6-5a5a-84d1-40c8a3801f5e | note | CIBSE W5.2 State of the System
f132d39e-161a-59f8-bc04-6c8780693d7e | note | AS2941.1-2013 – Section 11
93d35a66-be35-5a8e-8fa7-c34a5ea8e289 | button | Has the Installation Pump been installed in a position that is protected from falling debris, and vehicular and mechanical damage? | Yes, No
966f9ed0-bf94-5d4c-8864-efe215063bab | note | Add Photo
bdfcb128-9f0d-414a-af70-10e0d223a074 | checkpoint | 2. CHECK AND CONFIRM - CLEARANCE
32f8b54f-e0ab-559a-a62e-a2ebee72c499 | note | CIBSE W5.2 State of the System
06826f2e-a72a-5f66-8e16-c14b813b5d9d | note | AS2941.1-2013 – Section 11
64873849-7289-52c0-9e20-88e4de125545 | note | Is there at least 1.0m of clearance around the perimeter of the complete pump setup; and/ or
f0d722e4-387d-5e60-a2b6-cf91c5155d25 | button | for multiple pumpset installations, there is a clearance of atleast 600mm between each of the installed pumps? | Yes, No
53e5653d-6be8-5c4e-949b-c16133a00119 | note | Add Photo
f76b9f2c-c87f-493d-ad59-6a6df6e9d90f | checkpoint | 3. CHECK AND CONFIRM - ELEVATIONS
cc2895c9-c12f-5f24-9ffc-f1bda24e835e | note | CIBSE W5.2 State of the System
f6b308ec-af57-5f17-b105-caa55db967b6 | note | AS2941.1-2013 – Section 11
ec4c2d86-60cc-5222-98dd-a05d7db5dbdc | note | Have pumpsets been installed with the centre-line of all suction pipes at the same elevation; and/ or
63997cfc-e8c0-5d6e-bf4b-7ea41d5d310f | note | if the pumps have been installed at different elevations, the elevated pump is installed on a properly constructed mezzanine floor; and
c25356f9-0920-54d7-9d82-39b880e50369 | button | with head clearance of minimum 2.1 m to the underside on both levels? | Yes, No
daf58310-c2a7-5987-9e91-e7dcd6cf28e1 | note | Add Photo
217a6815-393b-4e3f-bdbd-8b80c4f4f743 | checkpoint | 4. CHECK AND CONFIRM - PLINTH
0b9dccde-7cea-56b1-abbf-d69dafdd6bbc | note | CIBSE W5.2 State of the System
7b52d910-1551-5082-a140-f72bd7a83754 | note | CIBSE W5.6 System Checks
9e4c2b7e-dd18-5e07-ac41-1ac272887550 | note | AS2941.1-2013 – Section 11
a5b973ba-9fa3-534f-be9a-1c364b821776 | note | Have pumpset baseplates been mounted on concrete plinths with a height not less than 150 mm above the floor?
6911492d-5138-5b3b-95f9-1e3ac43f3d75 | button | For fixing purposes, does the concrete plinth extend 150 mm past the edge of the baseplate on all four sides? | Yes, No
0dbe39f6-4567-5846-b923-1922b6d9266c | note | Add Photo
7dd395fe-1899-445b-9a5f-a20d2e4ac47a | checkpoint | 5. PRECOMMISSIONING CHECKLIST - CHECK
acca55ea-8fc3-591a-b8da-81b802fdb2ac | note | CIBSE W5.5 Pre - Commissioning
0266b948-3e8a-5594-a1aa-dbb4bfcdd22b | note | CIBSE W5.4 System Filling and Venting
a370e5e7-d7ff-5d70-ab6b-36c595d75d88 | note | AS2941.1-2013 – Section 12
39e4a5be-030b-593e-98c0-dcd89d59cd7e | note | Have you checked the coupling alignment to ensure that the unit is aligned within the manufacturer’s specified tolerance?
a7cba846-8082-5f37-82a2-cc67ce20dd06 | note | Have you confirmed the direction of rotation?
57f3204f-5590-5f8e-b7c7-8b6368ac6a97 | button | Has the battery electrolyte level, and the battery leads and connections been checked? | Yes, No
97ef5044-5215-5f7c-b97c-136d68c244df | note | Add Photo
288d8302-a082-40c3-9e5e-fc8406d14039 | checkpoint | 6. PRECOMMISSIONING CHECKLIST - ENSURE
e8b57586-9319-5c1b-b818-b3498e9c44e6 | note | CIBSE W5.5 Pre - Commissioning
c8874d3a-6d93-5c04-984f-be14bef95066 | note | CIBSE W5.4 System Filling and Venting
ad012a34-faf8-5070-b11e-ce13b4f2b3a0 | note | Is the delivery from the pump under test the only supply to the measuring device?
fd5bd383-0eeb-5c62-9b0d-c9acfeb53b81 | note | Does all flow from the pump passes through the device?
5908a09e-8fa3-540f-ab6b-ef5de7128cd1 | note | Is the pump primed and lines are clear; and
4a958a46-c463-55ce-a841-e3faf883d25f | note | valves are correctly set (open, closed or adjusted to required pressure); and
ece9e633-1494-542a-8327-3e0445451e19 | button | is water available? | Yes, No
23a9c32c-ae0a-59c6-a78e-fe492e8ead65 | note | Add Photo
72618fbd-64de-4e04-9ec8-b25602fc7680 | checkpoint | 7. PRECOMMISSIONING CHECKLIST - ISOLATE
7130a1ca-4600-5c74-a41f-489e4265c371 | note | CIBSE W5.3 Check before Filling
b0ab59a3-cbf8-5ee5-a2f8-74d0bacf593a | note | CIBSE W5.4 System Filling and Venting
4d59f759-7c8c-5594-9d1d-6749e578792e | note | AS2941.1-2013 – Section 12
f5d70b0a-60b7-59a3-b968-a8a514e1f4fe | button | Have you isolated all other water supplies to the fire protection systems, such as the automatic pressure maintenance pump and any other compression-ignition engine driven pumps in the system? | Yes, No
4bed1507-acd5-589f-8280-c96a2acd2791 | note | Add Photo
03a6ad8a-54e8-4aad-8767-356dbd01d6ae | checkpoint | 8. PRECOMMISSIONING CHECKLIST - REPORT
aab6b237-2476-53ba-b4fb-24e61a56ac90 | note | CIBSE W5.5 Pre - Commissioning
410f8cd3-d584-5791-9943-d236a6270ea3 | note | AS2941.1-2013 – Section 12
d3331474-5de3-5216-bf95-3e86554f01fb | textbox | Pump plate details:
6af18428-b1de-50e0-b693-5e14b715145a | note | Add Photo
3744be90-5f56-4fff-948c-fcd195d08592 | checkpoint | 9. COMMISSIONING CHECKLIST - RECORD
ed5d9a2a-5682-50f8-8137-d43118c17601 | note | CIBSE W7.10 Commissioning Certification
174f74e1-0a25-5e39-849f-1daa00e7e5aa | note | CIBSE W7.2 Flow Rate Measurement Tolerances
98fc42c1-94db-5cdc-ba09-25960e9f3eac | note | AS2941.1-2013 – Section 12
3a904a20-6f04-543c-bfc6-e1a381d75074 | textbox | What is the pressure in the system at which the pump starts automatically?
ffae48d0-5577-5a23-a82d-7b3f0b7cccb1 | textbox | Pump shutoff pressure:
243f6fca-9f2f-5a03-9c51-8f9ccc631f63 | textbox | Motor shut off pressure:
2d103750-b9b0-513f-b6f5-580c07564bbb | textbox | Delivery pressure at maximum flow:
e42f9090-3ff1-51a4-8894-4e44d26f1d84 | note | Add Photo
7461239d-2f0e-4a76-acc8-768dd0e319c4 | checkpoint | 10. COMMISSIONING CHECKLIST - RECORD
e335cab8-352f-5a2b-a06a-d82a20063cff | note | CIBSE W7.10 Commissioning Certification
3bd8e11e-4360-5096-b104-bf52a9016f00 | note | CIBSE W7.5 Preliminary Flow Rate Check
5de02cb6-fc40-5b44-b18c-2480cf8e0717 | note | AS2941.1-2013 – Section 12
fb68faf6-eb7d-57d6-818c-4e2d42185f5a | textbox | Record the pressure on discharge gauge and motor current at three other flow rates between shutoff and maximum flow, one of which should be at the duty flow rate:
fa632960-a88b-539c-97c2-cf0d94a6e81f | note | Add Photo
570f29c6-d623-434f-87db-10f25f7dd880 | checkpoint | 11. COMMISSIONING CHECKLIST - RUN AND RECORD
84479f96-bceb-5fa9-a9e2-3dbca44e830e | note | CIBSE W7.10 Commissioning Certification
75b8fc0b-327e-5c97-a164-897095315aa8 | note | CIBSE W5.7 Static Completion Records
4cfd1470-cb3e-5faf-bd19-3df42f4b7c5f | note | AS2941.1-2013 – Section 12
e622a898-6a2f-575b-ad4b-e85d25587e6f | note | DURING OPERATION:
21ae68c0-00c4-51b0-aee4-a1c9cbe9daf5 | note | Have you checked the temperature of the bearings and stuffing box leakage and noted any abnormality?
b48c85ab-8d03-5387-ac7e-6042eb8ab933 | note | Have you checked that all alarms and indicators, both visual and aural, have been activated; and
3264d7bf-2d0a-5aed-a83d-7f7904eb94b2 | button | Alarms and indicators, both visual and aural, revert to normal stand-by status when pump is stopped? | Yes, No
2bd641ca-5633-5a1a-a6bf-6bda41ee8d28 | note | Add Photo
cfb7dfb8-2521-447d-82e5-780623fe0db3 | checkpoint | 12. COMMISSIONING CHECKLIST - RUN AND REPORT
70fc5af7-9201-5fae-9618-1ba405127011 | note | CIBSE W7.10 Commissioning Certification
0c4e64ae-16a0-58be-8e40-9d2e61ca844f | note | AS2941.1-2013 – Section 12
a7ba8cc7-6f34-5fa4-8a7f-4bfd02bb4992 | note | RUN AND REPORT:
1372118a-49b4-5ff6-a76f-7ddf4fe93bc3 | note | Is the electric pumpset, together with its associated control gear and ancillary equipment, functioning correctly?
f51f1ced-d806-513b-aa8d-f076473c9d56 | button | Does the pumpset satisfy the intended performance conditions? | Yes, No
e7ab5652-5dc3-5068-824f-592f6bf82a19 | button | Are there any operational abnormalities? If Yes, detail below. | Yes, No
52d2f653-cbc3-519e-af39-fff864d781f3 | note | Add Photo
72942767-0888-4c67-887c-440d0ad0e13f | checkpoint-no-value | GM Fire Sign Off
0033d60c-40b5-4203-8041-a5d610601b17 | signoff | GM Fire Sign Off
ea69d34f-1261-47de-8eec-d3bcc5a55de1 | checkpoint-no-value | Principal Contractor Sign Off
8f60dfd9-1c2e-4261-9821-66349293f55a | signoff | Principal Contractor Sign Off
4b4d35d5-291f-4740-999a-0cc39967396f | checkpoint-no-value | Consultant Sign Off
85c7663b-7b93-4c7d-a1af-442af69f5aa8 | signoff | Consultant Sign Off
b225c4ca-4192-44b2-9a7d-ce4b375c0f4e | checklist | ITPS-205 Diesel Fire Pumpset Installation and Commissioning |  | ITPS-205 Diesel Fire Pumpset Installation and Commissioning
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
4ce8a016-716e-4119-a807-6438dd1d0d46 | checkpoint | 1. LOCATION
794d0e1b-427c-577c-872f-8289bab1e680 | note | CIBSE W5.2 State of the System
686ffbcc-ec7d-521c-9d27-25947de4b41d | note | AS2941.1-2013 – Section 11
2adb0d11-9d2a-5bb3-a1b6-58e23cf20fa6 | button | Is the Installation Pump installed in a position that is protected from falling debris, and vehicular and mechanical damage? | Yes, No
4df3f32b-0f87-5657-8c3f-a6e21ef8fd91 | note | Add Photo
54061128-a235-4f60-8a3c-d283d1335169 | checkpoint | 2. CLEARANCE
76d8b8c5-cbc0-5097-9f5f-9d5c3af94244 | note | CIBSE W5.2 State of the System
9aa700d0-ad24-51d3-8b46-183fff9d583a | note | AS2941.1-2013 – Section 11
f749bc67-c5a0-51df-bb01-c98506f32005 | note | Is there at least 1.0m of clearance around the perimeter of the complete pump setup; and/ or
aed13af4-22b7-5d02-b6e3-8233d7317ed2 | button | for multiple pumpset installations, there is a clearance of atleast 600mm between each of the installed pumps? | Yes, No
268f7072-6619-5644-9d73-d9ebb6a98ed8 | note | Add Photo
675e3953-b21a-4ad0-bf09-42567bd9b816 | checkpoint | 3. ELEVATIONS
f46cfa5f-0707-52d4-bfa1-53bfe364c43e | note | CIBSE W5.2 State of the System
9654eadf-0ceb-55c7-9d38-d23a5c197700 | note | AS2941.1-2013 – Section 11
0d73cca0-1903-554c-88b3-7386dc4fbd8a | note | Have pumpsets been installed with the centre-line of all suction pipes at the same elevation; and/ or
5b13ac35-221b-5169-a4a8-256dab2c2c08 | note | if the pumps have been installed at different elevations, the elevated pump is installed on a properly constructed mezzanine floor; and
acc4194b-766c-5831-9450-1adb4d845be1 | button | with head clearance of minimum 2.1 m to the underside on both levels? | Yes, No
14103439-dc2e-599c-87a0-30ce2ea3a6b1 | note | Add Photo
81e0f263-dad4-427a-af7f-d5efe6a0a6e6 | checkpoint | 4. PLINTH
48c97d13-0628-55c4-a52f-d329abe8128d | note | CIBSE W5.2 State of the System
9399cda3-de56-5783-91b3-83f0c37cf42b | note | AS2941.1-2013 – Section 11
cf3bf002-a5d5-5807-adb5-726e71f0a6aa | note | Have pumpset baseplates been mounted on concrete plinths with a height not less than 150 mm above the floor?
bd37f5fe-91c5-56e4-876e-e156a9557a0c | button | For fixing purposes, does the concrete plinth extend 150 mm past the edge of the baseplate on all four sides? | Yes, No
9ef51a25-72d5-5453-bfc3-8cb05384f310 | note | Add Photo
6caf1ba3-e213-4999-b4f8-613bcecfe6da | checkpoint | 5. PRECOMMISSIONING CHECKLIST - CHECK
a6288286-7f1b-5dd3-8394-fed057b7504c | note | CIBSE W5.5 Pre - Commissioning
7c21a387-f111-5938-ab94-1bbc614726e4 | note | CIBSE W5.6 System Checks
aa5e8242-9950-5086-b5c1-f9650df7fbd0 | note | AS2941.1-2013 – Section 12
f32c9d1d-f54b-5369-9845-f3365cfcbb2d | note | Have you checked;
a5704812-7296-5229-884f-d236462b83d8 | note | The cooling supply system; and
dea07c29-762e-5bb0-9847-c59584d87512 | note | Engine fuel supply; and
c0e16c39-1614-5b7b-aa6b-6d57480455a2 | note | The coupling alignment to ensure that the unit is aligned within the manufacturer’s specified tolerance; and
05b5ca73-41d5-56e1-a696-c1411eeb07f2 | note | The direction of rotation; and
886bfe0d-ab0c-5922-9615-190e1457d4ea | note | That the engine lubricating oil is at the correct level; and
8326b3b4-c592-5bc5-a0a3-d415f92a347c | note | The battery electrolyte level and the battery leads and connections; and
a8803385-4669-5ac2-9023-ac0c4c11030f | button | That the exhaust system is intact? | Yes, No
c4bd2397-874c-5123-9a93-cbbb52b84522 | note | Add Photo
c1b3d17c-5960-43ed-8533-9295e58bc863 | checkpoint | 6. PRECOMMISSIONING CHECKLIST - ENSURE
f2ac4c7d-e199-50a4-b4b4-8c4844d7e9b0 | note | CIBSE W5.5 Pre - Commissioning
4a83a057-c48c-5634-98c1-f4c45aa542a6 | note | CIBSE W5.4 System Filling and Venting
f87ba262-d673-5206-b659-06ff26e3fcfd | note | AS2941.1-2013 – Section 12
bce6df7b-8cb6-5f07-9ce2-97a6b9854ecb | note | Is the pump primed and lines are clear; and
487c4f22-37a3-5c82-bd46-14134ef14cf4 | note | valves are correctly set (open, closed or adjusted to required pressure); and
334d11fb-7b43-54d2-a998-55c4e5b7b1dc | button | is water available? | Yes, No
0afe26e6-6897-5565-b2bc-8c8d81e6d139 | note | Add Photo
fd9cf697-3927-4b7f-a1e6-9bb40344f444 | checkpoint | 7. PRECOMMISSIONING CHECKLIST - ISOLATE
b8b6c16d-c996-552d-8183-3f3e6f15a476 | note | CIBSE W5.3 Check before Filling
dde4fdbb-e2a1-5999-b41b-0b340fa4982d | note | CIBSE W5.6.2 Mechanical Checks: Automatic Control Valves
12da7dbe-a45c-5411-8b34-d9a5c1e5d39a | note | AS2941.1-2013 – Section 12
1c5ee796-e8e3-5c56-8941-4cd94160e178 | button | Have you isolated all other water supplies to the fire protection systems, such as the automatic pressure maintenance pump and any other compression-ignition engine driven pumps in the system? | Yes, No
0db53e62-ec9f-5916-85e0-f81f8d1c225c | note | Add Photo
06f8dd1c-e3c8-42f8-9a19-d633128cfd83 | checkpoint | 8. PRECOMMISSIONING CHECKLIST - REPORT
699335ec-c08c-5722-9640-015a90d537f7 | note | CIBSE W5.5 Pre - Commissioning
363c3ca4-2040-56db-a7da-dc6711e7aa84 | note | AS2941.1-2013 – Section 12
e7c265b9-237d-51cb-a3f1-628bdcc784ca | textbox | Pump plate details:
06b2ad24-c743-52d0-b6a7-3bb01b06b318 | note | Add Photo
9de6ad24-9873-4fc2-9d09-f6f8cad53eb6 | checkpoint | 9. COMMISSIONING CHECKLIST - RECORD
9fdc2da0-be2f-5776-80b0-a4ed8ca147f0 | note | CIBSE W7.10 Commissioning Certification
96adc920-fb98-5022-8aa2-935da569ad6a | note | CIBSE W7.2 W5.7 Static Completion Records
aa37baa3-6a77-5355-a2e0-e6febb1296d8 | note | AS2941.1-2013 – Section 12
3f97bb98-632e-54a6-bf5d-18ee0e1fe17c | textbox | What is the pressure in the system at which the pump starts automatically?
b9779469-c274-5f9b-9e38-f392f69f8bc1 | textbox | Engine oil pressure:
300590e9-f721-556a-83c8-0907c6ce3d1f | textbox | Pump shutoff pressure:
a583503a-f9bd-5f82-8c94-41dddfbdd7d4 | note | Is the Coolant flow correct; and
d8e2b1a1-4362-56fd-9da8-5640f14b14fc | button | Are the fan belts rotating and intact? | Yes, No
573cdf2e-49ca-5a1a-bbed-cc13747d61fa | note | Add Photo
b4f51475-6a2d-5885-becb-0aed1a830701 | checkpoint | 10. COMMISSIONING CHECKLIST - ISOLATE
34d928d4-b9bb-52f4-a207-87e55c84b6a8 | note | CIBSE W7.10 Commissioning Certification
05cf3260-4c6f-59f9-925c-051faf6d69b6 | note | AS2941.1-2013 – Section 12
ad2cd759-071a-5a3b-a267-98919468bc20 | note | ISOLATE the flow meter, partially open the test valve, and flush to remove any debris or foreign matter;
c86753cf-9de2-5f3c-976d-f6a4767887fb | textbox | open any meter-isolating valves, open the test valve, and record pump delivery gauge pressure when approximately full load flow is indicated on the flow meter:
2b90ec82-c5d2-5ac4-a1df-5db191cc2f60 | note | Add Photo
b9f052e6-e367-44ac-87dd-5dbb542e2b97 | checkpoint | 11. COMMISSIONING CHECKLIST - RUN AND RECORD
7c198f01-15d0-5179-aacf-7f6cc7dc3882 | note | CIBSE W7.10 Commissioning Certification
4e41ddad-fa1b-5d69-936f-5aa8ef9b07fa | note | CIBSE W5.7 Static Completion Records
216d48d3-f40f-50f2-b065-22746228af05 | note | AS2941.1-2013 – Section 12
3808afd6-096a-56d7-a966-afb08390b4f6 | note | RUN the pump for 30 min at maximum flow and record.
85c324eb-7978-5870-bb73-02dbf6d56af9 | textbox | Suction and delivery pressures:
3bc1a54b-e7fe-5c73-bbd2-6d5717580a12 | textbox | Engine running temperature:
bef05381-4376-5910-b711-7d32fe4b7cf4 | textbox | Engine oil pressure (within the engine manufacturer’s limits):
70583689-1e01-579f-8b2f-02786794a553 | textbox | Air temperature at pumpset:
93b0c498-f14f-5e40-8647-7f2dca4eacb5 | note | Hold the engine shutdown mechanism closed and simulating an automatic start signal until the engine has attempted to start for five automatic starting cycles.
3da5fb4b-c30e-5f25-96af-74186d4dc46e | button | On the sixth starting cycle, return the engine shutdown mechanism to its normal starting position. Does the engine start immediately? (Clause 9.3.6.2) | Yes, No
cf87689c-22b1-5db8-8800-84352c7e5d09 | note | Add Photo
89136ac2-e7da-4e71-a217-c350de26b0a3 | checkpoint | 12. COMMISSIONING CHECKLIST - RUN AND RECORD
ed60559c-6802-576a-9039-af992d446f15 | note | CIBSE W7.5 Preliminary Flow Rate Check
456c383e-a94c-5f72-8e5b-ccd49c1e7dad | note | CIBSE W7.2 Flow Rate Measurement Tolerances
af71fb18-5590-5fa9-980f-2cf72875722a | note | AS2941.1-2013 – Section 12
2e7a63fc-1937-516d-ac01-0fa327f5be11 | note | RUN the pump for 30 min at maximum flow; then
8ef4f6cf-6be2-59cd-8430-6734765f89b1 | textbox | Discharge pressure at three other flow rates between shut-off and maximum flow, one of which shall be at the duty flow rate:
9af852e3-223e-50b1-98ff-26acdc0d8e54 | note | Add Photo
dd3d2e6f-1737-484e-8668-9e581e9320c0 | checkpoint | 13. COMMISSIONING CHECKLIST - RUN AND RECORD
88b0c517-c4e7-5e0a-8f13-5dee0728761a | note | CIBSE W7.10 Commissioning Certification
f2889d4b-c540-5330-942c-8674032f367f | note | CIBSE W5.7 Static Completion Records
fdaf169d-ab25-5a8e-bc1b-e61eb216d6c9 | note | AS2941.1-2013 – Section 12
4b54d5f7-4419-5cca-b9db-53ade154d1d1 | note | DURING OPERATION:
2790d9fc-b6f4-5886-b46c-1378ee69ed15 | note | Have you checked the temperature of the bearings and stuffing box leakage and noted any abnormality?
479f48f8-b4c4-51ae-a5ac-635fbff14a3a | note | Have you checked that all alarms and indicators, both visual and aural, have been activated; and
31ac04f5-e82f-5839-b71d-3fc0bb732e21 | button | Alarms and indicators, both visual and aural, revert to normal stand-by status when pump is stopped? | Yes, No
89c5ba42-39f1-53a3-9f77-0fc68a5c5034 | note | Add Photo
562239d0-93ca-499d-a4dc-43537d65d5ae | checkpoint-no-value | GM Fire Sign Off
b70049f6-f23e-4b93-be4a-a692a143cb15 | signoff | GM Fire Sign Off
6ba80533-95e6-4bf9-b5c0-9c8640af64d0 | checkpoint-no-value | Principal Contractor Sign Off
e06386d2-67db-4b92-ae29-cf4a8bd4833f | signoff | Principal Contractor Sign Off
dbf9dc45-d8a2-44ab-b08d-e4a20e96abd5 | checkpoint-no-value | Consultant Sign Off
cc2d01a5-a24b-403d-91d2-cd072b39b6a1 | signoff | Consultant Sign Off
b64211c8-ed16-43a7-a185-0ea3cfaaa131 | checklist | ITPS-206 Sprinkler Commissioning |  | ITPS-206 Sprinkler Commissioning
29dbf407-c83d-4d9d-b918-f6d020a46fa5 | section | Details
72f1236a-97ad-4446-8898-e227648cb7bd | checkpoint | 1. CONFIRM WATER SUPPLY & PUMPS PREVIOUSLY COMMISSIONED
7b3bb54e-96f6-5646-b007-839ac2bb9e1b | note | CIBSE W5.2 State of the System
f02c1bc2-49e1-56bd-a96d-e4effe29f285 | note | AS2118.1-2017 - Section 14.9
78abe8ee-e183-5ded-b50e-0ffc1e9103bd | note | Water Supply & Booster Pumps have been commissioned
84da98c1-948b-5c9c-805d-ee260bfcc588 | button | Are all Valves in the correct position? | Yes, No
4931b28f-d25b-40c1-adce-93d56f49c336 | checkpoint | HOLD POINT
98f6d477-ef01-5f01-ae75-bbfbd86e2588 | note | There is a risk of damage to pumps if system is not ready for sprinkler commissioning . Refer ITPS-204 and ITPS-205.
0caac1b7-28d7-493a-ae8f-ec12632b2d9a | signoff | GM Fire Sign Off
c055b8a5-49fc-4975-aab1-3cb593f99849 | checkpoint | 2. CONDUCT FLOW TESTING TO PROVE SYSTEM PERFORMANCE
791575f7-a233-5562-a1fb-728b481a1005 | note | CIBSE W7.5 Preliminary Flow Rate Check
94cd816b-4fe6-5fe0-92e2-b204de252027 | note | AS2118.1-2017 - section 4.2.2.
4c57e011-4af3-509b-9a03-2d66004f4d6e | note | Test
bdaf475e-1be8-514b-8f62-91b401a926f0 | note | 1) Confirm flow & pressure requirement
da431bf3-34df-5797-973f-dc2b40d84c49 | note | 2) Secure flow meter to annubar test line
e8391e1a-5243-518a-9f87-512da589f45b | note | 3) Manually start booster pump 1
9f87bc54-f447-5f6c-8766-15c80c7748c8 | note | 4) Incrementally open annubar test valve
9c4461de-7659-5c2a-acb4-79ef6e714c69 | textbox | 5) Record test flow & pressure at each stage:
7e81063e-9c14-577b-b7b5-bb5a11ccd529 | textbox | 6) Record pump data at each stage:
2332d512-5fa6-5512-bb08-028d165d2ab3 | note | 7) Confirm system achieves pass result
66c69617-552d-5808-ba92-3f92ff24fca8 | note | 8) Close annubar test valve
091f57b6-3c28-5f34-acd1-4a63694f06ba | note | 9) Stop pump
39a2eed1-db5a-5093-a1d7-ba2196d23f65 | note
318447c8-9946-5393-8b41-d097df31340c | note | Has the Sprinkler Block Plan been completed?
313f9c44-64e0-5b14-9529-6965415a96fb | button | Have you recorded this on the Pressure Gauge Schedule? | Yes, No
248020c2-a977-5d8a-81aa-94708dbc89b1 | note | Add Photos
78a1be0a-9501-4acc-8352-a71c13d06f7c | checkpoint | 3. CHECK OPERATION OF DBA PRESSURE SWITCHES
0826824a-1475-56e9-bb86-e51b9d06c77e | note | CIBSE W5.6 System Checks
14f41050-35c9-5ed0-83a8-656118fd4e0a | note | AS2118.1-2017 - Appendix H4
a7a0b581-7215-5606-82ea-4218fde036c8 | button | Does the pressure switch change state when system is activated (Rise in pressure switch)? | Yes, No
174607f1-03e8-5e3d-9530-d554628f826c | note | Add Photo
ef9f4883-29af-4ee4-8b0e-43388f4b31c9 | checkpoint | 4. CHECK OPERATION OF PUMP START PRESSURE SWITCHES
ce3957d3-77a4-53b9-a6db-c11e94497b48 | note | CIBSE W5.6 System Checks
658218a3-0dc1-5d64-adf2-746d9159dc77 | note | AS2118.1-2017 - Appendix H5.4
9390aded-3e72-5d53-b9bf-82e599dd28af | note | Are the pump start pressure switch settings in accordance with pressure gauge schedule?
9934a45d-e956-5e27-8433-3e85c0cdc40b | button | Have you checked the operation of All pressure switches individually? | Yes, No
31984170-69f5-5344-8e04-87990023aac5 | note | Add Photo of Pressure Gauge Schedule
08648517-96d3-41d9-b347-c1649492dc69 | checkpoint | 5. CHECK OPERATION OF DRY FIRE INTERFACES
605e5d64-d9fa-5f35-b24d-b8f9de643d00 | note | CIBSE W5.6 System Checks
349a3131-36b2-5617-89d1-a680fce8a1f0 | note | AS2118.1-2017 - Appendix H6
61ac5854-3d3e-5243-b1af-b7a11c578890 | note | Activation of ancillary Pressure Switch (Rise in pressure switch) registers at FIP
be467401-167c-5609-8de0-b0a882605e02 | note | Activation of flow switches register at FIP | Yes, No
7cfea7b8-5ec7-563c-a4e2-9d27e216e35f | note | Change in valve state/position register at FIP
6e6df6bc-04e0-504d-8383-cb3617ab4133 | note | Attach the valve list
0d20e9d6-191b-4dc3-8a3d-dba777e7db02 | checkpoint | 6. COMPLETE FORM 71 & ALL TEST RECORDS
dd891fe5-a54f-5acc-a3d1-b65473ffb0cf | note | W7.10 Commissioning Certification
cc6b87af-b88e-5e35-a6d0-2257954f294c | note | NCC 2019, AS2118
5a66d5e5-d417-5c8d-ac4e-4563dac816a0 | note | Flow test pass result on Form 71*
6ca10d28-0961-5aab-bf8f-ba3abe2b2514 | note | Record the pump start pressure switch set points:
e5296aa2-b6ee-565f-9d94-722de69a9d4d | button | Record the dry fire interface test results: | Yes, No
ba502499-ebc6-53ad-a8ad-869b7c576f0f | note | *Form 71 - Fire Hydrant and Sprinkler System Commissioning This form is to be used for the purposes of commissioning water based fire safety installations, as required by the Queensland Development Code – Mandatory Part (MP) 6.1, which is a building assessment provision under the Building Act 1975, section 30.
56efb860-7000-5baa-a3f9-9eb01857518c | note | Add Photo
9096634f-312f-4907-aa01-b0df26625138 | checkpoint-no-value | GM Fire Sign Off
5b91dc0c-1092-4792-baa2-7cc792a6ecb4 | signoff | GM Fire Sign Off
408bdde5-585a-466c-95f0-1fdf1e066ff0 | checkpoint-no-value | Principal Contractor Sign Off
00dbada9-c2ef-4ff1-9d95-b66819956c52 | signoff | Principal Contractor Sign Off
c498b80d-231c-4b7d-b68f-a83b476b3d48 | checkpoint-no-value | Consultant Sign Off
95673340-5df8-4443-adb8-264cd4174d40 | signoff | Consultant Sign Off
92868c49-68e8-4851-a633-85ca57d9f88b | checklist | ITPS-207 Hydrant Commissioning |  | ITPS-207 Hydrant Commissioning
ed73caa8-6a89-4089-b942-e357839e73a6 | section | Details
3ce02fce-fae5-445b-a23e-df1f11c3ed26 | checkpoint | 1. CONFIRM WATER SUPPLY AND PUMPS PREVIOUSLY COMMISSIONED
c3af4091-cc0d-5319-8148-060dd645d40c | note | CIBSE W5.2 State of the System
37526f76-a48f-5a1a-aef8-06bb2ecf1b1a | note | AS2419.1-2005 - Section 4 - To comply with Part 4.2
6f9e046b-028c-55b9-adbd-2231ac992b4c | note | Have the Water Supply and Booster Pumps been commissioned?
2e911a9d-31ca-5360-9fc7-027197cd290d | button | Are ALL Valves in the correct position? | Yes, No
cc24e2d0-f068-4119-b5b4-5351a5b2fbeb | checkpoint | HOLD POINT
a1b525be-75ed-51c5-9f22-13331730087f | note | There is a risk of damage to pumps if system is not ready for sprinkler commissioning . Refer ITPS-204 and ITPS-205.
ae05e58b-1caf-41f9-bd76-41802fcb2c22 | signoff | GM Fire Sign Off
452a6b51-9dc5-4f7c-b243-b8b0305c9608 | checkpoint | 2. CONDUCT FLOW TESTING TO PROVE SYSTEM PERFORMANCE
e7230c46-4dee-5b7a-a95e-30d2ef320b22 | note | CIBSE W5.2 W7.5 Preliminary Flow Rate Check
00671c11-cc35-583b-8a2d-b28653dc5a1f | note | AS2419.1-2005 - Section 2
413d2871-a295-5d1e-bc12-3d12eb007f3e | note | 1) Confirm flow and pressure requirement
2009dd0e-5610-53d3-89d0-06dbfe00c8b9 | note | 2) Secure micrometre and calibrated gauge to hydrant outlet
5592f14b-1c65-54cd-9024-f8d59574d3b7 | note | 3) Manually start booster pump 1
5a942f0f-2285-5969-ad62-cd44100d4c56 | note | 4) Open hydrant valve to required flow rate
859d2de0-2470-51cf-aee2-4510689630c5 | textbox | 5) Record residual pressure at required flow rate:
b1b505c8-b725-58fc-8c26-2cc2bf575869 | textbox | 6) Record pump data:
742b7c99-76b5-51d9-bfe9-ec55cb0a44be | note | 7) Confirm system achieves pass result
3349d287-50ed-5f74-86d3-9150450b9352 | note | 8) Close hydrant
1d218417-1dfb-5eaa-b584-76c87dd08581 | note | 9) Stop pump
640cfe8e-0736-54bc-b687-3e349ec49d22 | note | Attach Hydrant Block Plan and Pressure Guage Schedule
3c55d2a7-65f3-4de1-a328-c96df6477842 | checkpoint | 3. CHECK OPERATION OF PUMP START PRESSURE SWITCHES
1075b8b9-45f1-5f1f-b165-e4b18754164c | note | CIBSE W5.6 System Checks
9f1707d2-b51f-57b7-9102-6cb35f0c559c | note | AS2118.1-2017 – Appendix H5.4
3ce01053-6618-55fc-81e1-37d818e3b746 | note | Is the pump start pressure switch settings in accordance with pressure gauge schedule?
eff4208d-c237-5738-ba9a-5d1ea966bfe2 | button | Have you checked the operation of all switches individually? | Yes, No
25a44730-5cf8-5c4a-aa34-59584356e6d9 | note | Attach Pressure Guage Schedule
7f99377b-57ea-4183-82aa-f1c81ae12a54 | checkpoint | 4. CHECK OPERATION OF DRY FIRE INTERFACES
9f3a8315-82dd-5676-84f9-477667e1cafd | note | CIBSE W5.6 System Checks
85b55e60-ed1e-5b35-931c-5f5efd516941 | note | AS2118.1-2017 Appendix H6
6773f7c3-bb8f-5f9e-bc81-c2efe643eaf6 | button | Change in valve state/position register at FIP | Yes, No
20591f9a-8fb8-5b76-b0a2-e01ed3df249d | note | Attach Valve List
51398cfc-5ed5-4457-b6c1-1ecdb339138d | checkpoint | 5. COMPLETE FORM 71 & ALL TEST RECORDS
d2e428e3-8747-59e6-a5b0-5c58bf91b408 | note | W7.10 Commissioning Certification
cdde687b-b4b0-501f-92e1-9ff2e5651f8d | note | NCC 2019, AS2118
15707bcf-419a-5bb4-bda3-28dd6180679b | note | Flow test pass result on Form 71*
f0a733a5-2d43-593a-8f83-ef51c812aceb | note | Record the pump start pressure switch set points:
56334f86-7e2e-5eb9-bf2a-3db8a451149c | button | Record the dry fire interface test results: | Yes, No
706587a1-4b4a-578a-955c-5e54f93a0e91 | note | *Form 71 - Fire Hydrant and Sprinkler System Commissioning This form is to be used for the purposes of commissioning water based fire safety installations, as required by the Queensland Development Code – Mandatory Part (MP) 6.1, which is a building assessment provision under the Building Act 1975, section 30.
671a01d7-bcbb-5c7f-8788-f83b9e7ea215 | note | Add Photo
f5c57e75-28ec-40a1-b47a-db5cf3dd5498 | checkpoint-no-value | GM Fire Sign Off
db01e9df-4b9e-4b9a-9d2f-a928160604b6 | signoff | GM Fire Sign Off
944026a7-5ac4-4ddb-8c2e-62d67c8fa177 | checkpoint-no-value | Principal Contractor Sign Off
47746bef-d8fb-401f-9238-3f1bd28653ee | signoff | Principal Contractor Sign Off
996559f9-56e9-4d3c-96c9-46a5667a7fe4 | checkpoint-no-value | Consultant Sign Off
c7a8d6cb-9860-428d-95b0-9e665a2410a1 | signoff | Consultant Sign Off
8c078969-1aab-4260-8cc2-a2251813c709 | checklist | ITPS-400 Temporary Fire Strategy |  | ITPS-400 Temporary Fire Strategy
1d2a4619-6763-4275-a5af-9166e110d038 | section | Details
7a73b0d2-7382-446e-8268-e6209eb8c2ea | checkpoint | 1. INSTALL AND CHECK PORTABLE FIRE EXITINGUISHERS INSTALLED AT FIRE EXITS
fe100014-0875-4305-84aa-d423176a7304 | checkpoint | 2. INSTALL AND CHECK HYDRANT BOOSTER INSTALLED, BLOCK PLANS, LABELS
348f2f0d-de67-40b7-9252-f62cf8a7492d | checkpoint | 3. CHECK EXTERNAL ATTACK HYDRANT IS WITHIN 20M OF BOOSTER
c27aeca3-8e84-4140-a885-5ddc993a8d86 | checkpoint | 4. INSTALL AND CHECK SYSTEM IS PRIMED WITH WATER (TOWNS MAINS)
2bfd571e-fbc0-46cc-adb1-503a7c09d98b | checkpoint | 5. INSTALL AND CHECK HYDRANTS INSTALLED PRIOR TO JUMP
b042c967-262a-44c3-aa2a-7215d2223283 | checkpoint | 6. CONDUCT WATER PRESSURE TEST OF HYDRANTS
4f527d88-9c31-4f59-81b1-de5c3735c44b | checkpoint | 7. HOLD POINT DETAILS
456c91b6-7ea5-56c0-866f-d4664b366cc3 | button | Hold Point Required: | Yes, No
4ec94095-33c6-4ef2-8c3b-456e4c1bbc71 | checkpoint-no-value | GM Fire Sign Off
d2188bf6-ca7b-4a4d-81d9-720fc5c8dbef | signoff | GM Fire Sign Off
8693e9be-608b-4f28-8c17-e3ece023243b | checkpoint-no-value | Principal Contractor Sign Off
85da8dad-4221-4f46-8452-ea28e9dec3bf | signoff | Principal Contractor Sign Off
a670ee85-482c-42c5-99ca-26a6802f1f14 | checkpoint-no-value | Consultant Sign Off
d92f5a61-5ad4-4614-9d09-4fe9d2adacf6 | signoff | Consultant Sign Off
00f9c6ca-2ed6-4b78-955c-596c0d7bf539 | checklist | ITPS-401 Site Temp Asset Lists Extinguishers |  | ITPS-401 Site Temp Asset Lists Extinguishers
87be8f9c-f357-4f39-a964-ee612a2d275a | section | Details
a7da47b9-ed3b-4e65-97f3-1c52f72bd721 | checkpoint | 1. ASSETS 1 TO 10
8bb896ed-2c88-5781-93e2-2910729cfbd0 | note | Add Photos and Numbers Below:
f95b2224-edc7-45b7-833b-3ebef2055462 | checkpoint | 2. ASSETS 11 TO 20
7c8085bd-7581-5dd3-862f-fd9faa68e7ef | note | Add Photos and Numbers Below:
73fb7601-f122-4259-b74d-4c97b9de8219 | checkpoint | 3. ASSETS 21 TO 30
05822f84-ece0-5579-9017-9328316d958c | note | Add Photos and Numbers Below:
ba37e1f8-9f20-4101-b5e8-4a1a084d4e41 | checkpoint | 4. ASSETS 31 TO 40
31920b50-e8f3-537c-95cb-55409f3ba85e | note | Add Photos and Numbers Below:
530e28c3-48b1-4d0a-bd9a-4127a6052b77 | checkpoint | 5. ASSETS 41 TO 50
e215f267-2b3a-5c04-9267-5d46286c7a30 | note | Add Photos and Numbers Below:
5e5712ff-5c27-400b-9a84-6403d4460c87 | checkpoint | 6. ASSETS 51 TO 60
ea009f7e-9314-5710-9f8c-9b8d538d6078 | note | Add Photos and Numbers Below:
7ba44ae2-927c-4160-9678-7554ee8da9e1 | checkpoint-no-value | GM Fire Sign Off
1960547d-5d12-46b1-bd86-b21eb4a31a88 | signoff | GM Fire Sign Off
c04ffa4f-b58f-4b32-928c-933fd435d348 | checkpoint-no-value | Principal Contractor Sign Off
ca7069b9-6176-4d9e-b0f1-223e982e9940 | signoff | Principal Contractor Sign Off
c724f82c-5ddd-4bb7-84fc-2a7e3f1e97b2 | checkpoint-no-value | Consultant Sign Off
e577a4e8-0c8b-4728-8bbb-8b6208d64bea | signoff | Consultant Sign Off
1e70382a-cd84-5ae1-8862-c1c058edde43 | checklist | Lendlease Contractor Schedule H Checklist |  | Lendlease Contractor Schedule H Checklist
7a748d55-533f-527b-b0f9-60e8fa293f5f | section | Incident Reporting
49cfc842-08a8-4648-9fda-d0120c4209b3 | checkpoint | Incident Reporting
b5b35a37-7382-54ba-8bfb-811dbf4572bf | button | Any incidents were immediately verbally communicated to Lendlease | Yes,No
6801e20c-e2f1-5a7f-a0d5-fe47c4fd717b | button | A copy of Incident Notification Form was submitted within 4 hours | Yes,No
66e9a4c6-0421-5ef0-8732-cd78bca8e3a8 | note | Detail any incidents from the past month below and attach relevant forms below.
826609b4-fc54-5a39-ad75-e1293f234680 | section | Workers compensation first, progress and final medical certificates and Return to Work Plans
0c9492a0-811a-544b-b5bc-2fc846063034 | checkpoint | Injuries and Illnesses
e20f96b2-5ee3-56b2-b5c5-912388171f1b | note | The following have been provided;
5492c177-794d-5136-81c9-8f8430e1d1c8 | button | First Medical | Yes,No
823e0dc6-15b2-594f-962a-261c0a26bf92 | button | Progress Medical | Yes,No
09fd6dbb-22b0-55d9-bec1-c657d23b526c | button | Final Medical Certificate | Yes,No
d36edd68-abcb-576d-b8fc-6978886ed6b8 | button | Return to Work Plans | Yes,No
a20041b8-0ee5-5f04-a4e5-2f9b0b26598b | button | I have submitted any necessary Injuries and Illness forms within 2 hours. | Yes,No
b9e71c13-fb0c-5796-9a4d-1f3ce13a3ae0 | section | Reporting
e2cefbe1-7b4c-58cb-9296-52013acd2aff | checkpoint | A copy of any regulatory notices has been submitted to Lendlease via email immediately following receipt from regulator.
4094ba7a-5738-5658-93bd-78c5dff3acda | checkpoint | Daily Pre-Starts have been delivered to the office by 9am each morning.
4fb06383-4684-5418-9d3a-cc9f4daa39dd | checkpoint | I have submitted a copy of Toolbox Talks to Lendlease weekly, including records of attendance.
67b6449c-0fcb-586a-8ebf-2addf988ee69 | checkpoint | I have conducted a miniumum of 1 EHS inspection per day and a copy of EHS inspections for the month have been submitted.
2c6854ff-7dce-52fd-90e9-e611023a913b | checkpoint | Labour Statistics and Man Hours
c45fef96-b2bf-597b-b3ce-585cf62a4bdb | note | Contractor Labour Statistics:
3961a981-e885-5a9c-877f-050b8d38419c | button | Has been completed weekly? | Yes,No
2fcfc2ff-fc1b-5978-9631-1633f919466f | button | Has been submitted before the 26th day of each month? | Yes,No
506b1288-bedf-5659-a27b-52efdb96cd11 | button | Is attached below? | Yes,No
c5929b96-f03b-5652-94b3-156328f9754d | checkpoint | SWMS
1bfaab1b-8e49-53ee-9e9e-873030346dbc | button | Copies of updated SWMS have been submitted to Lendlease | Yes,No
e4104c40-5765-5a71-b723-f81d0bcfb590 | button | Contractor SWMS review register has been submitted to Lendlease | Yes,No
1adcbe56-3cdc-5f92-af30-4e947fc6e60f | button | Updated copies of signed SWMS have been submitted after onboarding each worker | Yes,No
d064d5c0-d0e0-5fe2-a4de-7727e0a3ff4a | checkpoint | Workers are trained and competent
973bcb55-6152-5f6d-a2b0-4d5902cff6f6 | button | Copy of current training register has been submitted | Yes,No
58d3b39a-17b8-56a7-9770-52ce522e2ef8 | button | Copies of licences, qualifications, training records for any courses attended during the month | Yes,No
3495576f-5639-59ab-a767-a607784a3cf2 | button | VOC (Lendlease Template) for concrete saw/angle grinders and Plant to be submitted for all workers before operation | Yes,No
aef74d7b-d587-5e34-9266-884de37191d4 | checkpoint | I have submitted copies of daily pre-start inspection records for the month
d77f5e32-8a3c-5a96-97b8-96e1ee4e803b | checkpoint | I have attached a copy of the up-to-date Plant & Equipment Register
863d56e4-a279-57b2-a68e-d4b15f9c5577 | checkpoint | Copy of current and up to date Electrical Register has been submitted ( 3 monthly unless new tools added)
1c11da09-d5b8-50be-807f-7a10f77c3645 | checkpoint | I have attached a copy of the Fall Prevention Register
f73063a9-6e9f-572b-981e-bc4461355341 | checkpoint | Lifting gear to be inspected, tested and tagged
e9a421ee-a73c-5e73-8691-a5ecb3c66c99 | button | I have submitted to Lendlease and attached below a copy of lifting equipment quaretly testing register | Yes,No
92bd2845-9677-5a10-9f62-2f292143cd1c | button | I have submitted annual inspection certificates to Lendlease | Yes,No
d8e7b937-09da-531f-a96c-18f76041589f | button | Monthly inspection register has been sent to Lendlease as per Lendlease Lifting and Slinging Guideline | Yes,No
ae92f7c6-9451-56f7-ae90-9960f5122f4b | checkpoint | I have attached copy of Hazardous Substances Register highlighting any chemicals brought on site this reporting period.
a02a0ab0-ff4d-53ee-8a92-1c3a98928fa7 | note | NOTE: Subcontractors are required to use Chemwatch to log all chemicals utilised
ba1f906f-1a0c-5a9f-a883-1abf31d17b82 | checkpoint | A copy of the Ladder register has been submitted this month
3d903859-b52d-52dd-aabf-1957c83c9f42 | checkpoint | I have attached a copy of Safety Data sheets for chemicals brought onto site within this reporting period (this month)
23484093-b5c0-5552-a60d-8d92e054fe12 | checkpoint | Temporary Works Design Register
75720ec4-cb43-5a56-a617-c22bb12e8de3 | note | NOTE Temporary Works Design Register must be submitted prior to mobilisation capturing of all Temporary works to be implemented by the trade
fcd4c867-242a-5081-80f1-6d415a64ea0b | button | I have attached the updated Temporary Works Design Register | Yes,No
5d21287a-0bce-5c38-a159-cd6673bf2998 | button | I have attached Evidence of Engineering Certification | Yes,No
d80834eb-8560-5715-b772-28441493f097 | button | I have attached Evidence of 3rd Party review of engineering | Yes,No
92ddcd9e-8e9b-5040-844d-c86a13562740 | signoff | Signatures
40c2f47c-d509-51bf-996f-09d340053a5d | checklist | POLICY-005 Safe Work Procedure |  | POLICY-005 Safe Work Procedure
90e555f1-b7db-5342-8f6e-ab9bb0160482 | checkpoint | Task Details
20503208-5969-5f1e-8ff9-70b6e2b47077 | note | Use this form to record your safe work procedure after analysing a particular task in your workplace.
b001c900-3957-50e9-b919-4df2a4169949 | textbox | Work Area:
87e46dc9-0ac6-51ce-8698-afc002e13ed2 | textbox | Task:
b0acb42f-8cae-5c1c-8664-abc6205a5de6 | textbox | Safety Risk: e.g. electricity, moving parts, noise
73bf96f4-9e1e-51a1-a557-4789936e6b2d | checkpoint | Personal Protective Equipment (PPE)
406fd4cd-4e32-5d69-a999-d4ce4993431e | note | The following PPE must be worn, and precautions taken, when doing this task:
8bcda9c5-55b1-5c0a-a247-b26b8235a9d7 | tickbox | Work Gloves
db367474-52c5-554a-9e48-e056818c3380 | tickbox | Safety Glasses
82e23f77-77d5-5234-81f9-a2801b0e1e8a | tickbox | Steel Cap Boots
6c384b5b-a38a-5f1b-a778-b43c46c05cd1 | tickbox | Ear Protection
0329ea2b-4e15-586f-87c2-da1048416cff | tickbox | High Visibility Vest
bc657fef-de49-506e-a3c4-742594337e70 | tickbox | Head Protection
d1cb54d8-7624-5a76-ad17-cb15c3d5fea9 | tickbox | Respiratory Mask
0698a563-4f2d-5274-b695-afceb564aeeb | tickbox | Face Mask
a1cabd01-53d8-566c-9a83-7f01c539f6e2 | tickbox | Protective Clothing
9124e5fe-8f03-5725-a5bb-2e9a66ec240f | tickbox | Wash your Hands
cc546369-bca4-51b6-ab24-8e4406ba760e | checkpoint | Supervisor Signoff
4570fb2e-7310-5ac1-a58f-8ade9076d7c2 | signoff | BY SIGNING I CONFIRM I HAVE APPROVED THIS SAFE WORK PROCEDURE
eb08fbdd-c180-58ae-b2d9-db72ca29c15b | checklist | REPORT-002 Hazard |  | REPORT-002 Hazard
8111ace1-1386-5c1f-8290-3df28e3c8d3f | section | Details
7016619e-d9e9-575d-a598-04fc8176f882 | checkpoint | Hazard Report
f420bf15-d63e-5570-a15e-3c71cb656360 | note | GM Fire employees shall complete a Hazard Report in the event they identify a hazard that may result in injury or incidents to person(s), property/plant, the public or the environment.
0bcd93f0-1075-5f3a-af9e-2cf89bc5e0cc | note | The principal contractor will be informed immediately and provided with a copy of this report.
423d5ed9-def2-5985-8cad-6c2afa7e0d08 | checkpoint | Hazard
a922a8f0-9b5e-5623-92bd-923e2f78adb6 | textbox | What is the hazard?
e23dd611-f6df-5b35-a2ee-6c2f1af58ca8 | checkpoint | Contributing factor
75fc5566-9ca7-57cb-90ed-2b98b506e44d | note | What are the contributing factors?
a38fdc36-19aa-5ee5-8f2a-6881c3a63b7e | tickbox | Environment such as noise, slip or trip
0498232e-4825-5b7b-b7c9-fdff6973fa0a | tickbox | Equipment/ materials i.e. wrong or inadequate
6e54f58c-4667-5587-81e3-cae566531ad4 | tickbox | Work Systems i.e. inadequate training
b14b4545-edbe-5604-a35c-e1fde7df54bb | tickbox | People i.e. production pressures, lack of communication, lack of procedures
79c645eb-13a3-594f-83b4-813a64224459 | tickbox | Other
7d3ef2d0-fcdd-5431-a5ec-d32a40d56cb7 | textbox | If 'Other' please specify:
5b8936dd-da50-5d1e-a2b4-e9a5b6b57cc3 | checkpoint | Corrective Action
51be76b0-2935-5404-bdf6-91f2dac836f1 | textbox | What are we going to do to fix the problem?
089bb444-dcf4-5d1b-a1e6-5db54fda1b91 | textbox | Who
f8c21bfc-54e4-55d9-a3f9-ad3b1785ba59 | textbox | When
09c0367c-9df2-5a1e-b57f-ce79d5be231a | checkpoint | Completed By
e8cad4f8-a779-54c4-8306-b65b38b7a52b | signoff | Signature
8775b17a-b99f-530a-8efa-ff6ef4427d02 | checklist | REPORT-003 Chemicals Review |  | REPORT-003 Chemicals Review
8111ace1-1386-5c1f-8290-3df28e3c8d3f | section | Details
1aed2016-2dab-4421-988c-18b0007058bf | checkpoint | Details
9d086d01-9819-5876-9635-47589ee4ed49 | date | Date:
2fcb38d5-3cc2-54cb-9612-a0599205bc5c | textbox | Time:
eefd7d21-c3a8-5249-9155-dcea38b4b61b | checkpoint | Existing Register
7743be1c-9492-5b55-b2eb-21c7c9c750ac | date | Last Revised on (date):
4abf95c3-68c9-568c-ae8e-61f6743b9112 | note | Upload a photo of the "Register-006 Hazardous Chemicals" as it is on site today.
586de132-0677-5158-8fb0-c38150ef6201 | checkpoint | Chemicals on Site
0319350e-85df-568a-9c33-e4d66393d53f | textbox | Location where Chemicals are being stored:
40e88e59-b8c5-5115-af83-9c985d94c47a | note | Upload a photo of each Chemical on site
8cbd2a0e-3c28-53bd-b9da-5a65540b2443 | checkpoint | SDS
0400bff8-e490-51a7-ad5b-dda864c24f58 | button | Have any of the SDS sheets expired? | Yes, No
0ecff0bc-b9ba-52a0-909f-64ca0bcb96cb | note | If 'yes', cease use of Chemical and contact GM Fire Management immediately.
7e10f6d7-4dc0-58b1-b284-03f370395982 | note | Upload a photo of ALL Safety Data Sheets (SDS) on site.
58bfb4fd-b3d4-5f94-a67a-e067a225bcd0 | checkpoint | Declaration
52ce4c9d-9064-5154-8047-14361ccddf8f | button | All Chemicals on site have been approved for use by the Principal Contractor | Yes, No
d540fed6-0daf-5c5b-b13d-deedb195eed0 | button | All Chemicals are stored securely | Yes, No
cbcc3039-8059-55cc-a9ae-e30c681e3d09 | button | Any Chemicals that are no longer required on site have been removed and or disposed of as per WHSE guidelines | Yes, No
0da0ee29-0ac0-5051-ad4a-3e439a9e4b19 | signoff | BY SIGNING I CONFIRM I AM THE REPSONSIBLE PERSON FOR HAZARDOUS CHEMICALS ON THIS SITE, AND THAT ALL INFORMATION I HAVE PROVIDED IN THIS REPORT IS CURRENT AND TRUE.
42c7df9a-ccb8-5d7f-9abf-a956b1f84163 | checklist | REPORT-006 Incident Investigation |  | REPORT-006 Incident Investigation
8111ace1-1386-5c1f-8290-3df28e3c8d3f | section | Details
6412ac75-35b3-555b-a89e-87d89553cfa8 | checkpoint-no-value | Incident Investigation Report
26c7a877-82ff-5d4d-9964-4e831bec896a | note | GM Fire shall complete an Incident Investigation Report in the event of any injury involving medical attention or off site treatment or in the event of any incidents involving a near miss, property/plant damage or injury to the public or the environment.
c7009061-5139-5526-a062-83adc69dbabf | note | The principal contractor will be informed immediately in the event of the above. Following discussions with the principal contractor, a decision will be made as to who will conduct the incident investigation. The principal contractor will be provided with a copy of the completed Incident Investigation Report.
0bb42031-c4a8-5bcf-80ff-6fc5304ee4f4 | checkpoint | Class of Incident
319b1c6b-9f44-55ea-b16c-b1a07631b0a3 | tickbox | Injury
0adde8bb-4f35-5400-993c-c7d0180c2af2 | tickbox | Property/Plant Damage
621668cf-7542-5404-a731-45e940e7d4ee | tickbox | Near Miss
95d75d3d-669b-5354-b3b0-96b4a129a1c0 | tickbox | Environmental
67776edd-303c-58ed-b6a4-4c93c3ad56de | tickbox | Other
c5515547-5acf-5223-adaf-ff810432bbba | textbox | If Other - Please explain
e433ee97-85b5-52fa-97a9-25ca60ea13bc | button | Reported to Princpal Contractor | Yes,No
857bb4fc-18cf-5306-a76e-802c247b752f | textbox | Details:
e1d07f73-ecd2-514f-8842-5a2e0effd57f | button | Further Action Required | Report to Authorities,Other
820f14d5-50a0-5c15-96c5-71e6e32d06c6 | textbox | If Other - Please explain
bc36afa9-00da-5f53-99b5-0b99d61a7935 | checkpoint | Details of Incident
92284681-efd2-53d4-8e0b-d46de0d7e437 | date | Date of Incident
673f8d24-ff72-5e07-b453-93880d52a9f4 | textbox | Time of Incident
325ed646-43a2-5fc3-9425-0bef6e03fe7f | button | am/pm | am,pm
4b70799d-acc0-5966-a907-0ef28ba3f126 | textbox | Witness Name
541505a5-4428-5a09-a1c7-efa380a6cf43 | textbox | Witness Contact
fdfff4a4-8f76-588d-97bd-e1944521b0f4 | textbox | Nature of Incident
725a55af-18c7-57c8-afe2-bfa092de1b6a | textbox | Location of Incident
3f3be10a-9abd-53e3-82f0-2667d7e71aa8 | textbox | Description of Incident
b482344c-2e6d-577b-9ddb-70e3d053f88b | textbox | Details of damage to equipment/property?
5acc9a29-5ef8-55dc-93ab-9320efe0254e | checkpoint | Injured Person/s (if applicable)
24e6a102-3cb8-5740-9562-2f6fcc5871ca | textbox | Name
c68b8d90-60e8-5111-8e35-d7857559c628 | textbox | Address
e678a59a-6b1f-5756-b6cf-2d17da084cb1 | date | Date of Birth
66d64f8b-744b-59a5-8649-41a77a1b3902 | textbox | Occupation
f3631539-86a5-543a-ad2e-dad8be5e4b52 | textbox | Employer
df6586a3-039d-5599-8263-333b90fa2c9b | textbox | Referred/transferred to
2653d5b4-f6f4-5d10-b061-5710923ec319 | section | What factors contributed to the incident?
673b3686-24cc-52e8-a200-da491c74d4d4 | checkpoint | Environment:
5bebb027-96f0-5460-890a-132a143a47e3 | tickbox | Noise
5e04e3c6-c511-54d9-855b-61b79ba33d83 | tickbox | Layout / design
be7367f6-b65c-5e31-9806-b57e064484b1 | tickbox | Lighting
b344a257-3875-58bf-9242-ae1b70d9c52a | tickbox | Dust / fume
c1b98094-8764-57ae-8d8f-23524f9f5e83 | tickbox | Vibration
c6079cb7-cfed-539d-a3de-4ffe5242c1a5 | tickbox | Slip / trip hazard
85c76db0-7b13-5e0b-b320-9a0f6543aa2d | tickbox | Damaged / unstable floor
1e95cef6-f5ed-5510-89c5-ba7214c48c16 | tickbox | Other
7af769cf-fdc6-5763-a34f-36b7668432b1 | textbox | Other (if applicable):
da263eea-7753-5dda-9253-36aae5136ab1 | checkpoint | Equipment/materials:
fe1e78dd-509e-5b53-8078-3c13e8d0020a | tickbox | Wrong equipment for the job
48449b5b-94f5-56fd-aa68-28179f2a1234 | tickbox | Equipment failure
34dbaa91-66eb-5b35-86e6-12b7080c0add | tickbox | Inadequate maintenance
340c7cf0-23ea-5aaf-be3e-08341656325a | tickbox | Material / equipment too heavy / awkward
d44177e4-2535-597e-9309-931a3a8d12ee | tickbox | Inadequate guarding
3d7d49b4-0c2b-5d53-bfdc-aa67787549d7 | tickbox | Inadequate training provided
000690e7-a449-5a80-a869-a79c71c27c48 | tickbox | Other
e2a3d872-b06f-56d7-868a-7dfc157a60c7 | textbox | Other (if applicable):
29bb93fe-1a56-5a6a-a4d8-caafbdc08848 | checkpoint | Work systems:
5dd9bf85-df05-50a5-9d39-ba8c92524aee | tickbox | Hazard not identified
2fbf68fc-22c1-530f-9cb2-b87b25344ca7 | tickbox | No / inadequate risk assessment conducted
0387a054-0cba-5d62-97d1-4479ebe8b41d | tickbox | No / inadequate safe work procedure
d37a698b-994a-54ae-81f2-b04aa7a1df63 | tickbox | No / inadequate controls implemented
c6ba7810-1a06-5766-8b22-30f4fdc6cfd1 | tickbox | Hazard not reported
8f15171b-ea63-518f-a1d3-40a0cdb8bb86 | tickbox | Inadequate training / supervision
22ddaef3-e684-5031-82f2-eabc39055e20 | tickbox | Other
df7a8e40-28bc-528b-b28a-0b6efe49c3d3 | textbox | Other (if applicable):
13eb0e36-06f7-5153-ba71-5b36d7104644 | checkpoint | People:
68c29607-73a8-59a9-918a-e8a1a7758f3b | tickbox | Procedure not followed / no procedure exists
f49a9eb6-f469-5486-a041-424512d20bb0 | tickbox | Drugs / alcohol
315224a4-528b-59d0-b752-048abb08d4dc | tickbox | Fatigue
2ed0f27c-86d8-5e84-a4f2-361debecd863 | tickbox | Time / production pressures
1cf8af67-af67-5409-bca2-d1a6cdab08ea | tickbox | Change of routine
91dc8070-c2b8-5f0c-bd24-be694c6f87a7 | tickbox | Distraction / personal issues / stress
06712e9c-8051-58f7-8676-16be7955cabe | tickbox | Lack of communication
feefc030-bfe5-5354-a12e-104f9508da2b | tickbox | Other
c3685b47-7234-5973-bc9c-d337e162b8f6 | textbox | Other (if applicable):
1c21ef12-b1aa-5192-a53b-a50ba28212cd | section | Corrective actions:
e23dd611-f6df-5b35-a2ee-6c2f1af58ca8 | checkpoint | Contributing factor
34fb92e3-cc81-5b39-9cc4-3570d31ea806 | textbox | (from above list)
73874509-bac9-555d-8853-d738436ac006 | textbox | What are we going to do to fix the problem?
da26fb44-6d60-52fb-870e-90b8c5ffd716 | textbox | Who
f5d8b083-01e8-5841-aea1-53e16258b921 | textbox | When
585d5a57-d317-5a2c-8c86-399f10c406d3 | date | Completion date
09c0367c-9df2-5a1e-b57f-ce79d5be231a | checkpoint | Completed By
11f31f0b-4a44-5a8b-8133-2e07b430d536 | textbox | Name
9346513a-1500-5fae-b25b-d6e769dd31d7 | textbox | Position
40b6d092-dcdd-58fd-840d-c4a54e7f5c2d | date | Date
e8cad4f8-a779-54c4-8306-b65b38b7a52b | signoff | Signature
5366e371-dd65-506c-977e-7c0c1dd499d9 | checklist | REPORT-010 Request Corrective Action |  | REPORT-010 Request Corrective Action
8111ace1-1386-5c1f-8290-3df28e3c8d3f | checkpoint | Details
8ca36ac4-e6a9-5c19-9f68-62df6b342ef9 | date | Date:
c1a8a3f3-ccd2-53fe-b6ed-75d785b9ec39 | textbox | Time:
236bf886-feed-5b89-b88e-189ab3a6aa09 | textbox | Location:
a7658600-97ab-5025-a5c8-d9346f363897 | textbox | Supervisor Name:
d5aaa5eb-093f-5332-af20-a8b65033877e | checkpoint | Corrective Action Report
470080c9-030a-5408-af52-4ce248203d53 | textbox | Principal Investigator
ae03f694-88c2-588b-9699-60507b906c4f | note | Non-Conformance is:
c68dc5af-6087-5c14-9f38-81709a3cf3e7 | tickbox | Minor
eb8cf326-d137-53a7-aa6f-322b88f46596 | tickbox | Major
fd65dc4a-4b47-59a1-b27e-73e7258caff7 | tickbox | Critical
83501f61-a7dd-58f2-ba98-8215422c94d5 | textbox | Details of Non-Conformity Identified
37926311-3d71-57b1-a160-ee79a6a6c30e | button | What is the likelihood of Fatality? | Very likely, Likely, Unlikely, Highly Unlikely
e8d491d2-a505-535a-b825-bb94bf8d98d5 | button | What is the likelihood of Major Injuries? | Very likely, Likely, Unlikely, Highly Unlikely
7b2a6704-3444-5657-b31e-17541b6fb8e6 | button | What is the likelihood of Minor Injuries? | Very likely, Likely, Unlikely, Highly Unlikely
b02cf86f-6c86-5841-a153-0817738ac475 | button | What is the likelihood of Negligble Injuries? | Very likely, Likely, Unlikely, Highly Unlikely
e5e5fcb4-d671-531d-b13b-56f1f2037a96 | note | Add photo evidence if applicable.
5d294295-86ae-51e1-92b2-e35eee764d2a | checkpoint | Corrective Action Plan
ee12348c-7dfb-5dc3-b9b4-79fb91b527cb | textbox | Describe corrective action
d4828a33-3bfd-5ce9-b3e1-c7cf58c9d639 | textbox | Is this plan permanent or temporary? | Pernament, Temporary
6b7a6d3e-c89d-5150-b59d-01ac4ed55fa6 | date | What is the proposed completion date?
42c21dbd-9bff-5051-bd1f-f936237b2320 | checkpoint | Signoff
2923664c-ab55-5c48-87d4-1901f7c5ef27 | signoff | BY SIGNING I CONFIRM I HAVE COMPLETED THIS REPORT TO THE BEST OF MY KNOWLEDGE
0432706e-8008-5259-a763-1bc4a6e80f82 | checklist | SYS - Ground (South) ¦ Pour P1 ¦ MPX-GMF-ITR-FIR-G001.01 | itp | Ground (South) ¦ Pour P1 ¦ MPX-GMF-ITR-FIR-G001.01
8111ace1-1386-5c1f-8290-3df28e3c8d3f | section | Details
1f54bcfc-1215-5b13-86f0-788b385cdaaf | checkpoint | 1 - CHECK CONDUITS ARE CORRECT TYPE, SIZE AND QUANTITY TO CRITERIA - In-house QA
1d4d54b6-61c5-55a5-bc17-fcafd822cc07 | textbox | Drawing Reference Number:
3f00b1a5-c401-5cc9-96f6-b3d6fc3103d3 | date | DATE:
cdda51a2-ec33-5f1a-ad9b-93ba09f1fffa | checkpoint | 2 - CHECK CONDUIT ROUTE IS AS SPECIFIED IN LAYOUT/ DESIGN CRITERIA - Shop drawings (certified by an RPEQ engineer) are to be provided for each and every item required within 1170.4 Structural design actions – Earthquake actions in Australia.
4d767396-ad74-5214-a089-f107d1687b04 | textbox | Drawing Reference Number:
fbd16d5e-1a59-56db-80fd-babe64df79fd | textbox | Inspection performed and witnessed by: Please print name and company of all involved parties
63662228-becf-5361-b037-9af77fea6063 | date | DATE:
2101dbbe-c6d6-508b-808b-07ed470b819d | checkpoint | 3 - INSTALLATION, CONDUIT IS JOINED CORRECTLY - Installation is in compliance with AS 1170.4 Structural design actions – Earthquake actions in Australia.
324ca920-7767-5f4e-8739-aa28e114ce76 | textbox | Drawing Reference Number:
6415e655-f646-5319-85c1-0396ac43487c | date | DATE:
7461120a-7b68-549d-ab46-27acbf9138e4 | checkpoint | 4 - CONDUIT IS TIED IN
87fc4d82-0207-51a4-83a4-70b4fc735966 | date | DATE:
df0acc65-a74a-567e-b9da-a9b41cefa14b | checkpoint | 5 - CONCRETE COVER IS IN PLACE - General Technical Requirements – Services Ripley Sub-Acute Facility (RSAF) 2.2.3 - 9. All Fire services penetrations post concrete pours are to be immediately sealed with sheet metal cover plates (mastic or similar) to prevent water ingress. Plates to be fixed by use of nylon anchors or similar. Plates to remain in place and maintained until directed by Hutchinson Builders to remove.
f8e1478e-8dea-5143-ad8b-73e40c6aa03c | textbox | Drawing Reference Number:
e782a2e2-c839-54c5-a510-dc5daac59887 | textbox | Construction Issued Drawings Number:
f345e4fd-195b-56e0-ba35-8f341112d09a | date | DATE:
a33da194-3c31-5029-abad-3648543ffca3 | checkpoint | Hold Point Details
e933d674-6e4f-5ac0-8454-114932b6d60f | button | Hold Point Required: | Yes,No,Other:
7b6245f8-135c-55bc-81d9-e85647ae9cc7 | textbox | Other (if applicable):
44e88cf3-cf50-5199-a59a-6ff2df77334b | textbox | GM Sign Off - Name:
c310eec6-1061-5275-885f-06e3bf9bf329 | textbox | PC Sign Off - Name:
5bb0d0c1-fcd4-5df4-839d-9c9472e4a927 | textbox | CS Sign Off - Name:
769f3b14-6ddc-5a47-9865-d630a2b388c1 | signoff | Signatures