## Master List Templates
Id | Type | Name | Values | Prompting Name
87dbf723-3c96-462d-bf66-e455fedf5f06 | checklist | ITPS-209 Deluge Commissioning |  | ITPS-209 Deluge Commissioning
8eea13d2-6902-4b58-986a-3c9ed55875f7 | section | Details
7817e386-1f03-4300-b563-044adf24669d | checkpoint | 1. AREAS PROTECTED
0f26962a-7b53-515d-b6b3-22f5c1ae0bbc | note | CIBSE W5.2 State of the System
f6c8df84-0587-588f-a3c6-5fb3d4f3a162 | note | AS2118.3
579b67c5-1d15-5b2f-bfaa-4893198ed8bd | button | Have you ensured areas protected do not exceed 300m/sq per valveset? | Yes, No
69a0a452-eee7-5400-b4c3-1d18d8f626f5 | note | Add Photo
e13b2f41-965d-47fe-b293-b669ac827608 | checkpoint | 2. PRESSURE TEST
b77b8a3d-9734-5cad-b586-4c6c8f11065c | note | CIBSE W5.4.1 Pressure Testing
b5dd3634-0e61-5e2b-a53d-78f9fd902b38 | note | AS2118.1
088ba1e8-65f5-5bab-b519-e8d61450a0f6 | button | Have you completed a pressure test as per ITPS-203 for each deluge system? Note: Where open sprinklers are used ensure all heads are plugged prior to pressure testing. | Yes, No
b4e01887-62fb-5ccb-9378-5e7c57b095e0 | note | Add Photo
1ae11dd8-82e8-4a6a-9c03-a5c7b3ce35dc | checkpoint | 3. EQUIPMENT TESTS - SYSTEM FLUSH
728f2aca-b05d-5e3e-89ac-d818871303ea | note | CIBSE W5.5.2 Flushing Procedure
0851b159-f1c6-5973-977a-cb3586eb9363 | note | AS2118.1
543b63ae-49e1-55ad-b2ff-593c4e0fb7af | note | Complete the following PER valveset and open sprinkler head:
ec26301e-47b5-50d4-972e-b4d24505bd78 | note | 1) Flushing of each open sprinkler head to ensure debris is removed.
9c12745e-e70d-59ce-abb7-ac762de00e99 | note | 2) Setup filtration mesh and water bin at each open head off each system (is there are a large number of heads then separate system by plugging each head).
1903c679-9e94-5e4a-8788-0686e90ca55f | note | 3) Let water flow through pipework onto filtration mesh
29b7d2ca-0540-5357-b85d-d2214726c8f2 | note | 4) Once water is clear from debris shut off water and return system to normal.
79de03cd-4a66-53e9-a70f-2b83859bb91b | note | Take photo per deluge head and record deluge head/s location:
c62db6fb-5360-49e9-b201-c73c7170ea52 | checkpoint | 4. TRANSIT TIME TESTING
c61592c5-2057-5eaf-873e-fdc3c8791cd9 | note | CIBSE W5.6.2 Mechanical Checks: Automatic Control Valves
655f698f-f7f9-5633-8f34-22bd130f6610 | note | AS2118.3 Cl 2.9.1
dca9d2ad-e275-576e-b1fe-5f22044bf59a | note | Complete transit time testing
24da5ecf-6c2c-59bf-886c-e935fd082ba3 | note | Test of the deluge valve to ensure the transit time does not exceed 30s from the valveset to the remote deluge head.
ca7a5928-1b84-55d6-9e89-7a1559ca7660 | note | Add photo of results of transit time.
3a04b841-ac9a-4574-b21d-5e715db680a8 | checkpoint | 5. RETURN TO NORMAL OPERATION
0a93862e-2b51-5279-931c-3b3f60087f9c | note | CIBSE W5.6.2 Mechanical Checks: Automatic Control Valves
83d068c2-f166-5a5a-950f-7dba0ba9b53f | note | Are all open sprinkler heads re-installed where previously plugged?
eb006e7b-ed6a-56f8-8e5a-e7b3b4e19414 | note | Have system valvesets been returned to normal condition (or approved condition where construction still occurring)?
b0c22b87-45d6-5de6-a6c7-d46ea7ff4bc3 | button | Have water filled bins been emptied as per principle contractors requirements? | Yes, No
e3e5c507-051b-5c83-9f98-b95a7e82ef8d | note | Add Photo
f4e4ad9b-dd6e-4b4c-9955-2e35567b6483 | checkpoint-no-value | GM Fire Sign Off
8b042243-f6a4-4082-8826-804c333eb1ce | signoff | GM Fire Sign Off
44ef14c4-0907-4701-b770-28081a0f23f3 | checkpoint-no-value | Principal Contractor Sign Off
85d7a163-ece4-4347-b7b8-2cd6e059e22b | signoff | Principal Contractor Sign Off
287159ad-2b09-44b6-9445-76962cf3474e | checkpoint-no-value | Consultant Sign Off
0531c335-d3e4-4752-a6dc-20e7e02a75ed | signoff | Consultant Sign Off

## Project Checklist Templates
Id | Type | Name | Values | Prompting Name
c5dc7d7c-df99-5ec2-a589-b436df406a75 | checklist | 010SAF_08 SWMS |  | 010SAF_08 SWMS
a1c9d02b-1fdf-5e00-bcb7-56aeec761826 | checkpoint | 1. INDUCTION - Attach your signature to confirm you have completed the Principle Contractor's Induction.
d39621b2-57eb-545c-b19b-913b988ebada | signoff | By signing I confirm I have completed the Principal Contractors induction.
93e7a6a9-2417-5a63-a628-5bbbe7c40d86 | checkpoint | 2. ALL STAFF
cbaa5304-d926-5145-abea-643403fc7075 | note | 003G Using Platform Ladders
4c0dcfe7-d8a0-5008-bd8b-d7bc54f1ac2a | note | 004G Inhalation of Respirable Crystalline Silica
1117a6d0-9a4c-5b98-b403-d22a7b5ad3a6 | note | 005G Working at Heights
68979298-f5d8-548e-baec-8741d208ed87 | note | 006G Working at Heights Rescue Plan
1e1b9f0c-d012-59f5-9748-6f1fbc413551 | signoff | By signing I confirm I have read and understood ALL the SWMS documents listed above. I have reviewed these documents onsite with my supervisor and I have signed the hard copy.
d3e29984-ceb2-515c-9230-7a6de1161462 | checkpoint | 3. WET FIRE TECHNICIANS
b4e0d11c-383a-5193-a4d8-06886c652d7b | note | 019T Pressure Testing of Pipework
543f3f86-57b8-5b16-b786-9b1a07dba3bc | note | 020T Sprinkler System and Associated Pump Test
e8307916-4807-52bf-87e5-102669e43c3f | note | 021T Hydrostatic and Flow Testing of Pipework
b9ed5514-0cad-5767-9bc2-787d09c4b91b | note | 022T Fire Rating
3eda0a35-e17c-5ffa-8f13-550cbe45fa28 | note | 023T Fire Alarm and Emergency Warning Systems Testing
6a966737-d7b0-592b-adaf-4fd6c5c1ce28 | note | 024T Commissioning and Testing of Hydrant System and Booster Area
ec96f917-5f59-57b4-b51e-789fed1bc3e7 | signoff | BY SIGNING I CONFIRM I HAVE READ AND UNDERSTOOD ALL THE SWMS DOCUMENTS LISTED ABOVE. I HAVE REVIEWED THESE DOCUMENTS ONSITE WITH MY SUPERVISOR AND I HAVE SIGNED THE HARD COPY.
cb6326be-0982-5008-a0f6-df63d2b7f5a8 | checkpoint | 4. SWMS - DRY FIRE TECHNICIANS
5d11d398-a985-5a6c-aeb6-18ee293dc7c2 | note | 008I Removal of Existing Fire Alarm Systems and Devices
92d6eeb4-8277-5022-83a0-fc89644f8bed | note | 009I Removal of Pipework Fittings
52103321-2daf-5ff5-83c8-2ade86fd2490 | note | 010I Fire Alarm and Warning System Rough-in
8205c84e-07ea-575b-bae8-d3015acb0b02 | note | 011I Fire Alarm and Warning System Fit-off and Installation
884a1c0d-249f-5a69-b8f2-2e03f9760652 | note | 012I Installation of Fire Alarm and Warning System Cabling
61c0ba51-1491-512b-936c-ac2c0f143740 | note | 013I Installation of Pipework and Fittings
c29e79e2-249c-55ba-b869-187073053c35 | note | 014I Installation of Fire Control Panel & Emergency Warning Systems
12c89be3-5c80-51bc-be0f-9f94b3c520b4 | signoff | BY SIGNING I CONFIRM I HAVE READ AND UNDERSTOOD ALL THE SWMS DOCUMENTS LISTED ABOVE. I HAVE REVIEWED THESE DOCUMENTS ONSITE WITH MY SUPERVISOR AND I HAVE SIGNED THE HARD COPY.
8b3b509a-75aa-5bb4-bf99-8e6b8d8e597b | checklist | 010SAF_08 SWMS - AIDP Ripley |  | 010SAF_08 SWMS - AIDP Ripley
8111ace1-1386-5c1f-8290-3df28e3c8d3f | section | Details
a1c9d02b-1fdf-5e00-bcb7-56aeec761826 | checkpoint | 1. INDUCTION - Attach your signature to confirm you have completed the Principle Contractor's Induction.
d39621b2-57eb-545c-b19b-913b988ebada | signoff | By signing I confirm I have completed the Principal Contractors induction.
93e7a6a9-2417-5a63-a628-5bbbe7c40d86 | checkpoint | 2. ALL STAFF
e10de068-098a-54e4-9ca5-367664a0021d | note | GM FIRE 001 Working with Elevated Work Platforms
15671497-ad54-5d32-afa4-04d3f3c4b7b8 | note | GM FIRE 007 Manual Handling
520f9407-d01a-5995-b868-f3de1b60147e | note | GM FIRE 008 Working at Heights
fd6856ce-5fcf-5581-a5f9-83f42ae44906 | note | GM FIRE 051 Using Platform Ladders
98e081c0-c0f2-5647-a6e5-e314220d57ab | note | GM FIRE 060 Inhalation of Respirable Crystalline Silica
1e1b9f0c-d012-59f5-9748-6f1fbc413551 | signoff | By signing I confirm I have read and understood ALL the SWMS documents listed above. I have reviewed these documents onsite with my supervisor and I have signed the hard copy.
d3e29984-ceb2-515c-9230-7a6de1161462 | checkpoint | 3. WET FIRE TECHNICIANS
12aa4e47-69ce-583a-99b5-9ec6063e0430 | note | GM FIRE 009 Pressure Testing of Pipework
68ec500e-a59b-5b0b-b97e-769b3dde3619 | note | GM FIRE 031 Sprinkler System and Associated Pump Test
f9b74e32-e4b3-583e-91f9-e7b3e7f28716 | note | GM FIRE 032 Hydrostatic and Flow Testing of Pipework
ec96f917-5f59-57b4-b51e-789fed1bc3e7 | signoff | BY SIGNING I CONFIRM I HAVE READ AND UNDERSTOOD ALL THE SWMS DOCUMENTS LISTED ABOVE. I HAVE REVIEWED THESE DOCUMENTS ONSITE WITH MY SUPERVISOR AND I HAVE SIGNED THE HARD COPY.
cb6326be-0982-5008-a0f6-df63d2b7f5a8 | checkpoint | 4. SWMS - DRY FIRE TECHNICIANS
96e187af-4508-5796-814d-edf71d430753 | note | GM FIRE 002 Wiring Rough In Minor
edf53965-a075-57b6-9e59-ee1f53c5eea8 | note | GM FIRE 003 Fit Off Fire Alarm System
6d09c463-be7a-5e4e-bf48-f312657a39db | note | GM FIRE 006 Installation of Pipe and Fittings
12c89be3-5c80-51bc-be0f-9f94b3c520b4 | signoff | BY SIGNING I CONFIRM I HAVE READ AND UNDERSTOOD ALL THE SWMS DOCUMENTS LISTED ABOVE. I HAVE REVIEWED THESE DOCUMENTS ONSITE WITH MY SUPERVISOR AND I HAVE SIGNED THE HARD COPY.
02820854-2b26-5b84-8a78-37944efc42b3 | checklist | 010SAF_08 SWMS - Wacol |  | 010SAF_08 SWMS - Wacol
8111ace1-1386-5c1f-8290-3df28e3c8d3f | section | Details
a1c9d02b-1fdf-5e00-bcb7-56aeec761826 | checkpoint | 1. INDUCTION - Attach your signature to confirm you have completed the Principle Contractor's Induction.
d39621b2-57eb-545c-b19b-913b988ebada | signoff | By signing I confirm I have completed the Principal Contractors induction.
93e7a6a9-2417-5a63-a628-5bbbe7c40d86 | checkpoint | 2. ALL STAFF
e5f4983c-79f9-5d2c-aa86-19628d97bca4 | note | GM FIRE 001 Working with Elevated Work Platforms
cb97e826-81ed-5498-a1ce-8026ccaa34ad | note | GM FIRE 007 Manual Handling
3b53ae2d-a214-5919-8837-5ff53a686f11 | note | GM FIRE 008 Working at Heights
ad6ae2e0-0d48-5ac4-ab38-827dbaaad25f | note | GM FIRE 049 Working at Heights Rescue Plan
addf5555-e97e-5e0f-a3ae-e0bdc7cb00d5 | note | GM FIRE 051 Using Platform Ladders
29dc9e88-4534-5045-931b-379ccf48318e | note | GM FIRE 060 Inhalation of Respirable Crystalline Silica
1e1b9f0c-d012-59f5-9748-6f1fbc413551 | signoff | By signing I confirm I have read and understood ALL the SWMS documents listed above. I have reviewed these documents onsite with my supervisor and I have signed the hard copy.
d3e29984-ceb2-515c-9230-7a6de1161462 | checkpoint | 3. WET FIRE TECHNICIANS
f1b0bb87-0310-5266-aeba-e3557c2bc226 | note | GM FIRE 009 Pressure Testing of Pipework
aeb50cbd-b592-59f9-889d-b43dcaf721bd | note | GM FIRE 031 Sprinkler System and Associated Pump Test
afab2c86-7bc8-5186-b3b3-7364105642c4 | note | GM FIRE 032 Hydrostatic and Flow Testing of Pipework
ec96f917-5f59-57b4-b51e-789fed1bc3e7 | signoff | BY SIGNING I CONFIRM I HAVE READ AND UNDERSTOOD ALL THE SWMS DOCUMENTS LISTED ABOVE. I HAVE REVIEWED THESE DOCUMENTS ONSITE WITH MY SUPERVISOR AND I HAVE SIGNED THE HARD COPY.
cb6326be-0982-5008-a0f6-df63d2b7f5a8 | checkpoint | 4. SWMS - DRY FIRE TECHNICIANS
c22eb604-a543-55e8-a9bc-009aa41cad12 | note | GM FIRE 002 Wiring Rough In Minor
f0a3092c-62a3-588f-ae43-2a09e0cbbfe5 | note | GM FIRE 003 Fit Off Fire Alarm System
666707d9-d1a3-5bb1-800c-46a33c145d82 | note | GM FIRE 006 Installation of Pipe and Fittings
12c89be3-5c80-51bc-be0f-9f94b3c520b4 | signoff | BY SIGNING I CONFIRM I HAVE READ AND UNDERSTOOD ALL THE SWMS DOCUMENTS LISTED ABOVE. I HAVE REVIEWED THESE DOCUMENTS ONSITE WITH MY SUPERVISOR AND I HAVE SIGNED THE HARD COPY.
6b9ec89b-4933-5a77-8770-19454f0369a6 | checklist | ASSESS-001 Risk |  | ASSESS-001 Risk
8111ace1-1386-5c1f-8290-3df28e3c8d3f | section | Details
1c657631-910b-56b0-9af0-2d9a539b2537 | checkpoint | Assessment Details
ebec7ca2-baf4-5394-9f4c-5a39277ce26a | note | Use this form to document the risk management process for a single generic hazard.
a8df1d92-87eb-5bd6-9a1e-7189a87091d9 | textbox | Work Area:
910554ad-3617-5193-a400-23a3e982bc7e | date | Date of Assessment:
e6470cc1-0ce4-5737-88b6-6192f2c577f4 | textbox | Name of Assessor(s):
1f7c9678-9071-592d-9f2b-fdeed42463ee | textbox | Position(s):
9eb99e7d-e9db-52ba-afad-b83b25d88869 | textbox | Incident Ref. No:
270f8fc3-f5f3-5606-80eb-fc2c80ae4f95 | checkpoint | Hazard Identification
0fbdfaf6-39d4-513a-9dc2-aa2de530e235 | textbox | Describe the Hazard:
bfd5195d-87aa-5c40-ac91-f0b3a6ea86bc | checkpoint | Risk Assessment
eecf1be0-f5a0-5146-affb-ea0c9267ac93 | textbox | What harm could the hazard cause?
9b76330d-d6c2-5ee3-b756-569aef547c30 | textbox | What is the likelihood of this happening?
a9823f8b-9cae-532a-b714-f4d55e4c991f | textbox | Persons at risk:
1649d0aa-d687-5fcd-b94f-193a4064b3b8 | textbox | Existing control measure:
3e513e09-62f9-55d4-9810-b685a7f0d339 | textbox | Consequence:
d3023452-bb0d-5a43-9b49-7d8612c97d05 | textbox | Likelihood:
4476555e-3f2b-57cc-8096-51918ad6f035 | textbox | Outcome:
32563b01-0feb-5e94-999f-2bc4f92e2c20 | checkpoint | Control Measures
fc9a29a1-567e-598e-a42d-c4ef9c566289 | textbox | Elimination:
f356548f-e3b8-579a-8a5c-4d424438c214 | textbox | Substitution:
f2594983-f0f0-50cc-bf38-89b62b3431a6 | textbox | Isolation:
91ea73aa-c135-563d-b976-013ed7e22bcc | textbox | Engineering:
1a3f7ddf-1c91-54e4-aeb9-28e4040d710c | textbox | Administrative or PPE:
1e98c287-4227-56d4-a52f-666e0890f589 | textbox | Preferred control option:
71245745-e635-5d28-b0f1-51a28405fcc8 | checkpoint | Implementation
c101a88f-577d-5aaf-8130-bdde5a3b606e | textbox | Associated activities:
cd9446a0-12ea-5e23-8920-99c401834be2 | textbox | Resources Required:
d6919195-e9d4-526a-a2d4-5ff56748eb99 | textbox | Person(s) Responsible:
27fe5d05-a1fa-5dbd-bf8b-f4085db256d4 | date | Scheduled Review Date:
7717528b-ba68-53aa-a357-393c48e0a282 | signoff | Signature
2d472844-3796-5e71-8f7d-fed3d910e0e5 | checklist | ASSESS-002 Manual Tasks Risk |  | ASSESS-002 Manual Tasks Risk
8111ace1-1386-5c1f-8290-3df28e3c8d3f | section | Details
1c657631-910b-56b0-9af0-2d9a539b2537 | checkpoint | Assessment Details
4a78344c-4f70-5961-83c2-8506abd6d634 | note | This assessment identifies how to manage the risks associated with hazardous manual tasks and control the risks of workers being affected by musculoskeletal disorders as per the code of practice under section 274 of the Work Health and Safety Act 2011 (the WHS Act). Use this form to help identify and manage risks of hazardous manual tasks.
7978ca62-0031-5077-9008-73a2753cf6c6 | date | Date of Assessment:
90cd1555-52db-5fab-b171-d057d4b1f026 | textbox | Name of Assessor(s):
350f60dd-ddda-5c61-9c07-60fe88d9bde1 | textbox | Position(s):
d1dbebf9-4772-5650-992f-7272a3357d60 | textbox | Incident Ref. No:
58267725-2c6f-55fe-83b6-0579eb36ea4e | checkpoint | STEP 1 What is the Manual Task?
648902e1-5a78-5a23-9422-3fb2816cb14f | textbox | Relevant worker(s) to consult:
af7d49de-f9a4-59e8-83d1-b5c6282a1d9e | textbox | Name of task or activity:
790830b0-254c-59d0-9498-f8e6a3e5994d | textbox | Location where task occurs:
a6ce5163-1dca-516d-ab69-a80613049086 | textbox | Who performs the task:
f751c17b-70c1-5786-955a-a7c51351eb09 | textbox | General Description:
bf2b5766-0a58-58a5-9304-cb818f3230f5 | checkpoint | STEP 2 Is the Manual Task hazardous?
9a8be61d-05ce-591a-816b-7d038edecca9 | note | Hazardous manual tasks can result in musculoskeletal disorders (MSDs) such as sprains or strains. Work through the following to determine which postures, movements and forces of the task pose a risk.
ce1584f1-d067-51a9-bedc-d58db8d8ded6 | note | 1. Does the task involve any of the following risk factors?
108b55dd-97b1-59c0-b722-b57c91ce2cf5 | button | Repetitive movement | Yes, No
0cbb82c7-330f-58c1-9053-d3ecbd4373e6 | button | Sustained or awkward postures | Yes, No
d7ba2a23-7fdf-5d39-a7a1-977bd95cf963 | button | Repetitive or sustained forces | Yes, No
5593875b-6283-5c62-b099-d399e44656e7 | note | 2. Does the task occur over a long time?
3fa140de-6444-5d65-b32a-6f199bec72e8 | button | More than a total of two hours over a whole shift? | Yes, No
4fc74ce3-1d32-5924-9a22-e53e7dd2cd4c | button | Continuously for more than 30 mins? | Yes, No
b69fbcbb-e8e9-5af1-a6ab-0a37f94ad803 | button | 3. Does the task occur over a long time? | Yes, No
93aedfcd-b333-5968-83a0-532b87c22a60 | button | 4. Does the task involve vibration? | Yes, No
edefc681-b52e-57f6-9c25-60d89da77b1a | note | 5. Is there a Risk? The task involves a risk of MSDs (e.g. sprain and strain) if you answered ‘yes’ to either:
b7efa233-2bc8-527b-95be-4241006a1bf5 | tickbox | Question 1 and 2 (above)
784bbcd5-f912-5f8f-9952-61a99bd028a5 | tickbox | Question 3 (above)
c3fb5206-551c-5ab2-817a-e958ceff7fcb | tickbox | Question 4 (above)
1aa966df-5fd2-543e-9c4a-f64feb4588df | note | If you ticked anything in question in Question 5, continue to Step 3.
e50b9f28-4a60-59c6-8383-e57f027d07dd | note | Additionally, if you answered ‘Yes’ to Question 4 the task may be a risk and will require further investigation.
43bb97fe-9131-5be9-be82-2660ffb39a19 | checkpoint | STEP 3 - What is the source of the risk?
4913c1e0-c99e-51da-96f0-96fec679e6db | note | These are the things that are causing the risk and may be changed to eliminate or minimise the risk.
6a01eb35-c062-5a17-a8c6-9a2598e002d3 | tickbox | Work area design and layout: workspace available; design of workstation, furniture and equipment.
37e5be23-078c-5ef6-84c6-fe57bf8ad3f4 | tickbox | The nature, size, weight or number of things handled in performing the manual task.
eee7c8e7-32b7-508f-8452-810244f8f277 | tickbox | Systems of work (e.g. pace and flow of work; resources available; maintenance).
4c772b2e-3148-52f7-9cda-d1d24d0a3d09 | tickbox | The environment in which the manual task is performed (e.g. flooring; obstructions; lighting; hot/cold/humid environments).
75306ffa-8cad-5fb5-8c60-4770efcfbc4e | checkpoint | STEP 4 - How do I control the risk?
f99d59d6-0ba8-5feb-b57a-808f95fc11f2 | button | Can the task be eliminated? | Yes, No
c989c8c8-4564-5752-81b0-defc2c70c722 | button | Can you change what is causing the risk (the source)? (e.g. change the work area; alter the size of loads; use mechanical aids; manage environmental conditions; use adjustable equipment; implement preventative maintenance program). | Yes, No
6403b515-51db-5ff5-9649-68831acf4afa | textbox | If 'Yes', provide detail:
ab848ad5-79fb-54df-831c-48ea8d3fe235 | button | Is training needed to support the control measures? (Training needs to be task specific, noting that training in lifting techniques is not effective as a sole or primary means to control the risk of MSDs.) | Yes, No
406fc662-a981-509d-b317-cfb2597a4be2 | textbox | If 'Yes', provide detail:
249717bf-db57-5fb4-b61b-9f7678983512 | checkpoint | Implementing Controls
4ad85a6d-b5c6-5bed-912c-c2bf1101387e | textbox | Name of Responsible Person:
12f4cc58-0ab6-53b5-9c0c-df26cad3f7e4 | button | Responsible for: | Approving, Implementing
b30fc5a7-bec3-5723-9d8f-ed22a11d2253 | textbox | Name of Responsible Person:
93b5ee23-770d-559f-8e3a-7f0afd124b04 | button | Responsible for: | Approving, Implementing
2c3690f9-5863-553d-ba99-ac01d8d201d0 | textbox | Name of Responsible Person:
9e46d041-0b37-55fd-b5ba-d6ac0f10759a | button | Responsible for: | Approving, Implementing
3d610353-c57f-5248-994a-a1e9787f8e48 | textbox | Name of Responsible Person:
ab66fce0-3df0-57ab-b0b7-b6a808082eb1 | button | Responsible for: | Approving, Implementing
89334ebf-57ec-5f05-8b4e-750b91a0dc81 | signoff | BY SIGNING I CONFIRM I AM AWARE OF MY RESPONSIBILITIES AS OUTLINED IN THIS RISK ASSESSMENT
1ac85fbd-c1e0-52f8-a16f-a7d8e29a8854 | checkpoint | STEP 5 - Review the Controls
e90ab923-8e9c-5650-91aa-5485e3083876 | date | Evaluated on(date):
74ac5179-55ed-5ade-9ff0-34e746fa69e8 | textbox | Name of Assessor(s):
d5ae74b8-acd6-5019-89e4-3d7cb4defc5f | button | Consultation undertaken with relevant workers and others? | Yes, No
06c20aa9-8b08-549c-9973-75b4fc9390b8 | button | Have any other risks been created by the controls? | Yes, No
44485087-230b-517b-b738-42d99b2ba613 | button | Have the controls implemented reduced the risks? | Yes, No
ca56f38e-8c88-5762-9475-d85a94cab9b1 | button | Can further controls be implemented to minimise the risk? | Yes, No
3e1898ec-5e8d-5a77-837c-beceed17a9c1 | checklist | ASSESS-003 Hazardous Chemical/ Dangerous Goods Risk Assessment |  | ASSESS-003 Hazardous Chemical/ Dangerous Goods Risk Assessment
8111ace1-1386-5c1f-8290-3df28e3c8d3f | checkpoint | Details
6d7fd0df-5c96-552e-9196-f1142dc4e665 | textbox | Hazardous Chemical (product name):
b223e14d-2f70-5f92-963c-239c91b7aee1 | textbox | Hazardous Chemical Reg Item No:
e4059f96-9930-5427-9917-b31102d691a7 | textbox | Use:
eec44df0-883b-5db0-a668-e111f5465eb4 | checkpoint | Nature of Hazard:
38e9e40c-5127-56a7-97b0-ec76e440f4c7 | tickbox | Toxic (Poisonous)
7d9d2b08-2a65-5ab0-b691-15ec34da795f | button | Route of Exposure: | Eyes, Skin, Inhalation, Ingestion
1da8d56d-0d04-5808-8c7f-9f828158e83d | tickbox | Carcinogenic (Cancerous)
ee31f877-baeb-57ba-a54a-817982d12460 | button | Route of Exposure: | Eyes, Skin, Inhalation, Ingestion
293e1568-d6af-5911-80a7-cb993c091407 | tickbox | Teratogen (Harmful substance that could affect abnormal prenatal development)
1b17e649-5cbb-5c76-9739-737dc4a4d5a5 | button | Route of Exposure: | Eyes, Skin, Inhalation, Ingestion
e4e0c8af-ee41-5a47-829f-6c18e37e708b | tickbox | Sensitiser (Reaction to an antigen, such as pollen)
f1e72b8e-bc86-5257-acf3-64e53f1f3e67 | button | Route of Exposure: | Eyes, Skin, Inhalation, Ingestion
28d3c98f-681b-57e2-a8a1-f6ed8f804034 | tickbox | Mutagenic (Capable of mutating DNA, such as radiation)
25bdbb44-b273-53eb-abbd-a220e322a298 | button | Route of Exposure: | Eyes, Skin, Inhalation, Ingestion
dff86b77-e2b9-5277-9244-b8c545c0d0d9 | tickbox | Irritant (Inflammation of the skin, eye or respiratory system)
7762431d-a81a-50a1-87cf-59011d98efa5 | button | Route of Exposure: | Eyes, Skin, Inhalation, Ingestion
f6ae227f-bf99-5ea4-b52b-a93cb374aaa9 | tickbox | Flammability (The ease of which a substance will ignite, causing fire or combustion)
e27b2edf-847c-5e41-9c5a-a890a436f100 | button | Route of Exposure: | Eyes, Skin, Inhalation, Ingestion
c5299fc2-0138-5c3e-9df0-fdb6f6a23c55 | checkpoint | Risk of Injury
a8a9e7b0-28f6-5900-985f-ecf1c3fcecb4 | button | Risk of Acute (Short term) Injury: | High, Medium, Low
18f9045c-fc51-57dd-9c4b-697e48720240 | button | Risk of Chronic (long term) Injury: | High, Medium, Low
6adca422-e108-5631-9168-8f36735799d3 | checkpoint | Controls and Requirements
3bf7f78d-12c9-5e9d-83f7-d793a1c49c99 | textbox | Control Measures to reduce exposure i.e. change to a safer product, ventilate area, (P.P.E.):
9c3d4679-70e4-5713-9d12-43baa46ca7d0 | textbox | First Aid Requirements and Storage Requirements:
42c21dbd-9bff-5051-bd1f-f936237b2320 | checkpoint | Signoff
f6e6ad58-755a-5ec6-ac1a-b3db6c24bfc3 | signoff | The persons listed below have been consulted in this risk assessment, understand the hazards associated and agree to use the control measures identified above to carry out the works safely and in a manner which protects themselves, others and the environment.
7a2e19d4-a232-5ccb-9e9b-f9c2132fc0a5 | checkpoint | Assessor Signoff
d0aabc79-7a66-528f-976e-31f5a7db0456 | signoff | BY SINGING I CONFIRM I WAS RESPONSIBLE FOR CONDUCTING THIS ASSESSMENT
077c0ba8-41d6-5fdc-a2a0-3038b5cf5aa9 | checklist | ASSESS-004 Plant Risk |  | ASSESS-004 Plant Risk
8111ace1-1386-5c1f-8290-3df28e3c8d3f | section | Details
5011c755-395d-598c-bc65-ea69efabb143 | checkpoint | 1. Competent Peron(s)
8dfff598-ec53-5cdf-b0fc-4deb06a555ba | note | This familiarisation checklist should be completed by a Site Supervisor or Site Foreman to verify that the workers involved in the operation of Plant Equipment/ Mobile Elevated Work Platforms (MEWP) can demonstrate their ability to understand and operate the MEWP functions in accordance with the manufacturers operating manual. This familiarisation checklist must be verified by a competent person who holds the equivalent licence/ ticket required for the type of Plant Equipment/ MEWP to be operated (e.g. Boom lift/ Scissor lift)
66f15263-78a6-59ff-8d83-b55627e468e5 | textbox | Your Name:
01a2d559-8a1a-5b7b-bfac-bca3e8c33cd7 | note | Your Licences / Tickets:
81305c94-7af6-57e3-94fa-40cb9093b900 | tickbox | WP High Risk
742b18e5-9f8a-5147-bd12-9c398e69841d | tickbox | Boom Lift
5fbbf76e-277a-5ac7-bf9e-f26300f7790d | tickbox | Scissor Lift
9264bb98-4a15-514d-809c-eac1613c5b2b | tickbox | Vertical Lift
d3fbe112-1e18-5595-805a-64f7cc89feeb | tickbox | Other
6378241b-b477-5269-9a42-9999ba0ef14d | textbox | If 'Other" please specify:
c06fe721-a6e8-585c-ad93-6752e11d8265 | checkpoint | 2. Plant/ MEWP Details
03ffd26e-223e-55e1-ab28-feaf0fcb5ae0 | textbox | Make and Model:
4ff0ac34-7208-5b62-9956-626330225ca5 | textbox | Type (e.g. BL>11m, BL<11m, SL, VL):
6b0e5610-cf37-5886-aa78-b8bc2aea3ba0 | checkpoint | 3. Employee Competency
c6633421-b88a-5cfe-9729-4b5e0f4b24f6 | textbox | Name:
37a67cc8-c658-500f-b650-71bb19761e48 | note | Role:
e1b7e27d-f6e4-5d43-b6dc-b266ed6d95d6 | tickbox | Operator
b52e283b-ca4f-5e74-9391-01eebda93677 | tickbox | Spotter
3ca061af-0407-5aeb-b893-5507e00751a3 | note | Licences/Tickets Held:
34af4379-e12d-572f-be00-3e7752e004da | tickbox | WP High Risk
97501945-f4af-51a5-b817-3a901818c0c6 | tickbox | Boom Lift
d87f160b-bb1c-574c-a6b6-a71d83b70c30 | tickbox | Scissor Lift
89ae4d95-5c87-5980-9835-d209d590acc0 | tickbox | Vertical Lift
06ebc66d-119e-58a4-8c6d-3668b83861ad | checkpoint | 4. Employee Competency
466622f1-f215-5a17-b534-efbfa4fc91a3 | textbox | Name:
6a53eb82-d6ea-5cec-91ba-5ffdb23f1a9a | note | Role:
c9ec9cb3-009a-5fdf-942a-9e73aa00281b | tickbox | Operator
926f0583-2089-5322-89be-b8bebae43f6a | tickbox | Spotter
0ad70551-7f8e-5563-a241-0ed565b25a43 | note | Licences/Tickets Held:
df5776a7-1af1-5f27-9fda-7505440ce756 | tickbox | WP High Risk
ea1f110a-d803-5bda-ad3f-c82ecd292132 | tickbox | Boom Lift
65d2bd08-411a-5a2e-90f4-b60518456519 | tickbox | Scissor Lift
93bc7570-597e-5b36-bf2f-bb8ae873e79f | tickbox | Vertical Lift
3ef8e758-7384-5d13-8fa3-292a5f04a9d8 | checkpoint | 5. Employee Competency
03df98fb-2cc2-5d85-a119-bf9cdf34dce7 | textbox | Name:
687353f6-e90c-51fc-9592-76be79acecc8 | note | Role:
baade171-b6ae-54bc-b029-3f67bb663d38 | tickbox | Operator
f73b873c-70ff-51c8-9fe9-c68fb44963ee | tickbox | Spotter
dd629524-b0b1-5b4a-928e-cc1b275ed8de | note | Licences/Tickets Held:
beb5043c-763a-5c9a-b5ea-8da2872ad88c | tickbox | WP High Risk
fee25bd5-e91b-5a22-a773-a46d345362db | tickbox | Boom Lift
1aaea53c-620a-5ca1-913e-06c6e5016020 | tickbox | Scissor Lift
0ba9e51c-73e4-5448-8242-8e2fee566ba7 | tickbox | Vertical Lift
0db35e59-5266-54bd-bc6b-7ababdb43cef | checkpoint | 6. Declaration (to be completed by competent peron(s) noted in Section 1.
a6d50b3c-b0aa-5535-9812-8eef86ea4eb7 | button | All 'Operators' hold the appropriate licence/ ticket for Plant/ MEWP | Yes, No
e5250465-b3c1-5c3a-9da9-6bac11597a5a | button | All 'Operators' understand the operational controls and emergency functions | Yes, No
3a04f0f0-9e25-59f4-a467-ce1a62520a32 | button | All 'Operators' are aware of the logbook and pre-start requirements | Yes, No
2c604bf6-8953-5576-a6fe-3fe835e71587 | button | All Ground Support understand the emergency functions | Yes, No
7404767f-2547-53e5-8196-d71a7d589017 | button | All GM Fire employees on site have participated in an emergency drill | Yes, No
3daa4413-0627-5ac6-adee-a6fa2309e525 | button | All GM Fire employees have signed onto applicable SWMS | Yes, No
9899d9ec-b306-5aed-bbc5-b1347ea6537c | signoff | BY SIGNING I CONFIRM I HAVE ALL PERSON(S) LISTED ARE COMPETENT TO OPERATE THE LISTED PLANT/ MEWP ON THIS SITE.
72a6061b-dcff-5ec5-ad90-e324d3adc1d2 | checklist | ASSESS-005 Confined Spaces Risk |  | ASSESS-005 Confined Spaces Risk
8111ace1-1386-5c1f-8290-3df28e3c8d3f | checkpoint | Details
3cdecd9d-6497-571c-93eb-16406f32c174 | note | Use this form to document the risk management process for a Confined Space.
d903addd-2bb6-5fdc-b6b0-c6775f727bfa | date | Date of Assessment:
afee0a3e-faa4-5507-88be-995324d4cf32 | textbox | Name of Assessor(s):
aba0b723-52f8-5e26-b1ee-61d6f087fbdf | textbox | Position(s):
270f8fc3-f5f3-5606-80eb-fc2c80ae4f95 | checkpoint | Hazard Identification
b67b9f50-80a8-589e-a6cc-7ab74b9ba2a7 | textbox | What Hazard/ Risk is associated with the task?
6ae78a1a-4280-5a8b-9abb-02a9bf1b8a30 | textbox | Planned control measure to remove/ minimize hazards/ risks
5f69f6d8-d080-5c8c-b889-89407687bb6d | textbox | What Hazard/ Risk is associated with the task?
3c099c1e-63c6-548b-bdde-4fb89ecd71e5 | textbox | Planned control measure to remove/ minimize hazards/ risks
30151f4a-f525-57ba-8625-5f8f871f9dd3 | textbox | What Hazard/ Risk is associated with the task?
3287c836-d44e-5235-b54f-a7ab847d4793 | textbox | Planned control measure to remove/ minimize hazards/ risks
af1c68ca-85c2-5c50-bfdf-a1b9c933b825 | textbox | What Hazard/ Risk is associated with the task?
950e3e1f-5dfc-5dc3-ace7-4514cfcc8099 | textbox | Planned control measure to remove/ minimize hazards/ risks
1554a091-1f11-5982-b8c1-a45382e94d83 | textbox | What Hazard/ Risk is associated with the task?
5209d488-e2d5-5dd1-96c7-26f30f8df97d | textbox | Planned control measure to remove/ minimize hazards/ risks
520f3973-2a3e-554c-9da3-fcd0d6905a7f | checkpoint | Review
6f5c0c2a-9dac-5024-bc8f-8053e09fd222 | button | Does the Risk Assessment Identify that confined space work is involved? | Yes, No
367899b3-e413-5d70-8728-515aa8f527aa | note | If YES the Confined Space Work Permit MUST be completed
5639e689-367c-57a4-ac32-0a12c00db8cf | note | NOTE: EMERGENCY & RESCUE PROCEDURE: Where an accident occurs which requires that an emergency rescue be attempted, the standby/ rescue person is to immediately contact EMERGENCY SERVICES on 000 for assistance.
7a2e19d4-a232-5ccb-9e9b-f9c2132fc0a5 | checkpoint | Assessor Signoff
56f8102f-b903-54da-bf96-8ff06b6e209d | date | Scheduled review date:
946f9c2d-1950-57b6-981a-43e43c738227 | signoff | BY SINGING I CONFIRM I WAS RESPONSIBLE FOR CONDUCTING THIS ASSESSMENT.
f2099058-5b60-5dc8-8c33-99ece43f7707 | checklist | ASSESS-006 Job Safety |  | ASSESS-006 Job Safety
5e25be48-4354-51fa-a917-1881487cb8a0 | checkpoint | Client Details
c20ed422-6fc8-5dfb-96c2-b8a692ce9f6c | textbox | Client: i.e. Principal Contractor
715a39f1-438a-5b94-8bfb-ecf301e00d4d | textbox | Client Contact Name: Responsible Person(s)
9f4b9726-f803-59c7-a5ba-423711e16cf3 | textbox | Client Contact Phone:
98c66d61-9777-50f7-95fa-480b10deaf39 | textbox | Client Contact Email:
bad8a559-d874-55eb-a218-4243f23c1f05 | checkpoint | Job Safety Analysis Details
29c38107-6af9-5162-b072-b24e48f24501 | textbox | Work Activity:
1f96f05e-ba35-5464-9c16-8c5b2e2dfcfd | textbox | Location:
c8b622ae-9b65-5cc8-8fc4-764e2f526486 | textbox | Who is involved in the activity?
4f89259e-5559-5181-b26a-6f220faf9a35 | textbox | Plant and Equipment used:
0d3897eb-f9e9-5a98-af3b-4ec02aa773cb | textbox | Maintenance checks required:
89ab4ecb-dfa4-5901-b152-43defe585b5d | textbox | Tools used:
1e45506c-b5a1-589c-ba54-469c15c40504 | textbox | Materials used:
dc6356e3-4029-59bb-bd5d-5f1136aa6ce3 | textbox | PPE used:
2908127c-03c5-56f2-93ef-463091659feb | textbox | Certificates, permits and/approvals required:
9407282f-27a6-5a6f-a47a-139ee45a02d3 | textbox | Relevant legislation, codes, standard MSDs etc. applicable to this activity
f948400d-3b6d-5037-a27e-a1da8d06232a | signoff | This JSA has been authorized by:
df68f526-1e94-59d2-832e-1b4bc4eb113c | checkpoint | Job Safety Assessment
2441ce2d-6047-5e4b-85b5-61808ea5bab5 | note | Refer to the attached Risk Ratings table to complete the following..
da2d7ca1-87c3-5623-9896-72c94c6f0632 | textbox | Job Step Details:
70167b74-6574-56fc-ab62-9d6215af2974 | textbox | Potential Hazards:
1079d75b-446c-5d41-a37e-653115256551 | textbox | Name of Person(s) Responsible for work:
4c373fb5-55b5-5e6f-82c6-34de8011165c | button | Risk Rating: | Low, Moderate, High, Critical, Catastrophic
fc6005a3-ef4c-5428-a7ed-855ef71443b6 | button | How to Control Risks: | Eliminate, Substitute, Engineering, Administrative, PPE
b32654ab-87aa-52d2-9a05-371dfb4ba673 | textbox | Job Step Details:
18d8f83c-2102-5843-b368-9361c6d410e9 | textbox | Potential Hazards:
271a144b-5f8d-5211-8d52-d07708663b26 | textbox | Name of Person(s) Responsible for work:
6b646000-e7ce-5ee8-a6fb-2b691b4602da | button | Risk Rating: | Low, Moderate, High, Critical, Catastrophic
cf4b7d2a-cce0-53c0-88ab-fc3d24faf1cd | button | How to Control Risks: | Eliminate, Substitute, Engineering, Administrative, PPE
a1cb8a85-125d-51a8-8a14-7c1d13959125 | textbox | Job Step Details:
d5e5acf5-b6ba-5f82-822b-51b1dd128e3e | textbox | Potential Hazards:
38125a9a-7ef4-5a49-8bb4-c32dfd31c781 | textbox | Name of Person(s) Responsible for work:
c423d710-b1b2-5a3c-9f58-5a5a0314a6e2 | button | Risk Rating: | Low, Moderate, High, Critical, Catastrophic
1824b5cd-99be-514c-9b8f-af2507485114 | button | How to Control Risks: | Eliminate, Substitute, Engineering, Administrative, PPE
42c21dbd-9bff-5051-bd1f-f936237b2320 | checkpoint | Signoff
9c249912-b3c0-5116-b8ec-aba0ea058e1e | signoff | This job safety analysis has been developed through consultation with our employees and has been read, understood and signed by all employees undertaking the works:
456afd26-17c2-4463-a5b8-09ca7552acbc | checklist | CHECK-001 Internal Audit |  | CHECK-001 Internal Audit
639ffc2e-5780-49a5-9626-1a39f9c9849b | section | Details
1d445f04-0006-40b4-a571-6f19ac048fcf | checkpoint-no-value | Organisational Context
8c800a93-cf22-5492-9dd9-2bd48bbc6422 | button | Are issues relevant to GM Fire’s purpose and strategy identified, reviewed, and monitored regularly? | Yes, No
b5016317-6301-5eab-9a8a-6697902bbe46 | button | Have the needs and expectations of clients regarding the Quality Management System (QMS) been identified? | Yes, No
5f880a15-0618-51bd-9baf-2fb5e2d2f7d3 | button | Does the QA Manual describe the required processes, their sequence and interaction, and review criteria? | Yes, No
7b7a525d-3e3a-525d-995b-c8bd6e291604 | button | Have responsibilities, methods, measurements, and performance indicators been established? | Yes, No
a4a2c8be-8b67-4317-9951-1f04d8e8337e | checkpoint-no-value | Leadership
e8c98c28-3a51-5a65-b29a-afd02c1c7abf | button | Has top management taken accountability for the effectiveness of the QMS? | Yes, No
5578edc2-6611-5cee-9894-5be62ad6c456 | button | Have QMS policies, objectives, and responsibilities been communicated and implemented company-wide? | Yes, No
c4ab4629-8d9b-5e06-9700-22eb3205113a | button | Have legal requirements been determined, met and communicated company-wide? | Yes, No
dda00e20-9d8e-542b-8520-27a4893cec57 | button | Have risks and opportunities relevant to the QMS been identified? | Yes, No
32b681fc-8997-4df4-a633-ef614f3ba4bf | checkpoint-no-value | Planning
271c51c9-b085-5386-89cf-0209c377ce2a | button | Have the identified risks and opportunities been actioned? | Yes, No
38869ad1-6f98-5cac-b510-89734f9d4a06 | button | Is there a process for identifying and managing changes to the QMS? | Yes, No
9e473b0b-7841-4d71-a6f9-de14a66e5a04 | checkpoint-no-value | Support
8130f12a-077e-56ce-8455-d92d12c484e5 | button | Have you provided the resources needed to establish, implement, maintain, and continuously improve the QMS? | Yes, No
3672581b-5786-5345-90cb-5c5fd740793a | button | Has GM Fire identified methods to ensure measurement and monitoring evaluation results are valid and evidenced based? | Yes, No
b80ae12c-3aca-534c-83fd-20d8ab4d6352 | button | Have you ensured that all individuals who can impact the performance of the QMS, including office staff, site staff, subcontractors, and suppliers, are competent? | Yes, No
8b468dd8-2417-4e0f-b444-f2e688b2310d | checkpoint-no-value | Operation
01fb0777-58a7-5e0d-97d0-4593376267da | button | Do you have criteria for the evaluation, selection, monitoring of performance and re-evaluation of suppliers and subcontractors? | Yes, No
4160efa3-7a6e-5e66-b268-a437b2c86069 | button | Do you have effective methods of ensuring traceability? | Yes, No
e7422e25-f9c3-56f0-94b9-439dea1ee640 | button | Are nonconforming process outputs managed to prevent unintended use? | Yes, No
736735c3-0018-4611-a8a4-7e69c070e2a6 | checkpoint-no-value | Performance Evaluation and Improvement
2834a9b5-a9b4-59a9-a9b7-e4da9b218ab0 | button | Have evaluation timeframes been established? | Yes, No
6f99151b-b2aa-54f1-b12c-141c919b33a0 | button | Are methods of monitoring customer perceptions in place? i.e. customer feedback, surveys | Yes, No
f4524260-c6fd-5859-92b4-90872218cf1f | button | Is there a management review process? | Yes, No
ad86f72f-a5d9-531c-ad25-90b137dd17ea | button | Does GM Fire have appropriate processes for managing nonconformities and the related corrective actions? | Yes, No
2b3c1a00-1a40-5136-9372-12da1f9074a7 | note | List any further recommendations below.
3913f3a2-4f4f-4deb-ac32-bfeca28dd286 | checkpoint-no-value | GM Fire Sign Off
87b0f9e8-f170-4dfc-a6c3-64165d229bfa | signoff | GM Fire Sign Off
930a3e43-5647-50d1-87f2-966cce2343da | checklist | CHECK-002 Site Inspection |  | CHECK-002 Site Inspection
7604d349-3c9d-59ec-8769-a0cfe4110d87 | section | 1. Administrative, training and risk management requirements
b646b6a2-68d2-5b04-925e-0e13a9bb914a | checkpoint | 1.1 - So far as reasonably practicable, all workers carrying out construction work on the project have been made aware of the content of the WHS management plan, including any updates, and their right to inspect the plan.
6ba63d7d-3b3f-5c31-9434-f4939b574a87 | checkpoint | 1.2 - All workers carrying out construction work have received the general construction induction training.
b9691151-2ecd-5ee2-8ec8-b533204f2fd9 | checkpoint | 1.3 - Workers have been informed of the site-specific health and safety rules.
60ac4aca-7460-564d-ba14-2d3d98bfd234 | checkpoint | 1.4 - Suitable and adequate information, training, and instruction has been provided to workers in relation to work they are carrying out.
66bab419-a393-57f6-9c97-758d79271510 | checkpoint | 1.5 - Personal protective equipment (PPE) is being worn in accordance with the projects requirements.
2ab82d7a-cc3c-56a0-a89c-ba9e4252acc3 | section | 2. Safe work method statements
c145e282-9bf0-58ac-8a85-4500302a4c6e | checkpoint | 2.1 - A safe work method statement (SWMS) has been prepared for each high risk construction work activity that is underway or about to commence.
fe929405-eae8-5ca8-8783-fd58e2de54ac | checkpoint | 2.2 - Workers have reviewed and signed off on the relevant SWMS
7934e80d-dec5-5f41-be0b-42bbfcdd01e2 | checkpoint | 2.3 - High risk construction work activities are being carried out in accordance with the relevant SWMS.
8f0ef03e-318f-5cf3-b827-93b54c1df497 | section | 3. The work environment
e6018bbf-c8f1-5f07-b149-1bf83ae3ef97 | checkpoint | 3.1 - The work environment has been maintained such that it is clean and in a safe condition.
79bdc24c-1c00-5acf-983d-ebaa5ce5fad4 | checkpoint | 3.2 - Work areas are clearly identified and separated as necessary so that work can be undertaken safely.
1825c9fa-24bb-50ad-8b3b-a1e424e13ba5 | checkpoint | 3.3 - Lighting at the workplace is sufficient to allow:
f8272eb3-01c5-5337-a307-f72286a48c32 | note | ○ Each worker to carry out work without risk to health and safety.
1be19c4f-a82e-522b-98e5-e5aa656efb60 | note | ○ People to move within the workplace without risk to health and safety.
aef67d61-2c29-5ed8-9db6-bcf3ceacb0db | note | ○ Safe evacuation in an emergency.
e6860137-88a0-51f5-bab0-d6de14d63cb6 | checkpoint | 3.4 - The workplace has sufficient ventilation to enable workers to carry out work without risk to health and safety.
4ff74d5f-cec6-5c19-bd25-e6838e8f1c56 | checkpoint | 3.5 - The entries, exits, and access ways in the workplace are kept clean and clear of materials and waste.
48066b16-7c21-5768-945d-e4a5cf766b0b | checkpoint | 3.6 - A safe system has been implemented for the collection, storage, and disposal of excess or waste materials.
0b615730-4ffb-51cd-bfb3-02fcfc4435d7 | checkpoint | 3.7 - Sufficient area has been allocated to safely store materials or plant for the construction work.
8dca0770-d2f9-575c-9e8a-bc6b57a4f871 | checkpoint | 3.8 - Protruding objects that are a hazard have been made safe (e.g. exposed nails, vertical reinforcing steel).
b201c421-5b2c-5c48-9704-05cf6113c44a | checkpoint | 3.9 - Adequate facilities have been provided for workers, including toilets, drinking water, washing facilities, and eating facilities.
c51929b0-8776-5f5d-9a2c-3ebcffee0dad | checkpoint | 3.10 - First aid equipment has been provided for the workplace and is accessible to each worker.
18a4e767-8b1d-5672-a5a5-274690a036b4 | section | 4. Confined spaces
2825d9b2-da10-596a-9ce0-b40fcc56a1cc | checkpoint | 4.1 - For each hazard associated with a confined space, a competent person completed ASSES-05 Confined Spaces Risk.
0a584ab9-a5b3-52a1-b882-f4b9709cc8db | checkpoint | 4.2 - Prior to commencing the works, FORM-003 Entry Permit Confined Spaces has been completed and approved.
89309c03-7f35-5362-a583-36791c1dba8a | checkpoint | 4.3 - Appropriate signage has been erected for all confined spaces.
d0a6d31c-65a4-5bf4-bc31-672ba9175665 | checkpoint | 4.4 - First aid procedures and rescue procedures to be followed in accordance with POLICY-006 Confined Spaces Rescue in the event of an emergency in a confined space have been developed and practiced to ensure they are efficient and effective.
ded5ed0a-e444-5b8a-bb7f-fdbe7f8fb660 | checkpoint | 4.5 - Workers required to work in or around a confined space have been provided with information, instruction, and training in relation to the:
bed85791-cdf2-5734-99e5-42eabe40f212 | note | ○ Nature of all hazards relating to a confined space
be7ccc94-3134-5b95-8b20-72fefb415b43 | note | ○ Need for, and the appropriate use of, control measures associated with those hazards
b110c5ef-6275-5bf5-a856-5a63e44d03ea | note | ○ Selection, fit, use, wearing, testing, storage, and maintenance of any personal protective equipment
1a99ce71-7f11-5eeb-a21b-b350ded8d8c3 | note | ○ Contents of any confined space entry permits that may be issued
b0c02c77-ff62-5a00-8a01-e40663b3102c | note | ○ Emergency procedures.
e81da6f2-b7fb-5d0c-920d-ac0985916342 | section | 5. Working at heights
e2a6047c-3469-57d7-a1ee-63a6d2ce1e6a | checkpoint | 5.1 - A SWMS is available for all high risk construction work that involves a risk of a person falling more than 2m that has commenced or is about to commence.
c2fb3d08-8253-53dc-a912-7762ad36b3c3 | checkpoint | 5.2 - Where a risk of fall of less than 2m exists:
15a0bb70-25a2-55ce-8391-f9705261ae79 | note | ○ Each hazard that may result in a fall or cause death or injury if a person were to fall has been identified
098e60b1-4049-5b81-9802-dc44b50477cb | note | ○ The risk of death or injury that may result because of the hazard has been assessed
d8e17ce6-5b0d-5d71-adcb-c9012baa2fa9 | note | ○ Any control measures necessary to prevent, or minimise the level of, exposure to the risk is used.
98b57a94-c6a8-50d7-bb1c-2783d46d3990 | checkpoint | 5.3 - Where a risk of fall of at least 2m exists, control measures have been used which:
df712649-e072-54fe-b908-fe63884b915b | note | ○ Prevent a person falling any distance
28993959-da47-509e-a241-bb45845a83ee | note | ○ If prevention is not practicable:
55b684af-87ab-5194-82b6-3e644dbb1a7b | note | – arrest a person’s fall
7575aa24-7d52-5200-8719-e639552c447b | note | – prevent or minimise the risk of death or injury to a person when the fall is arrested.
6a7044d6-a81e-5157-bf4a-f5cbc210f31d | checkpoint | 5.4 - Ladders are not used to support a weight greater than that for which they have been designed.
d81daed7-0057-50a6-9fe9-8aece2cab495 | checkpoint | 5.5 - Ladders are used where the:
d8458251-f7d1-554a-bcc3-372ab76e7d8a | note | ○ Bottom of the ladder is on a stable surface
c8fdd838-d4e2-5652-83e9-9bc5b3b6145b | note | ○ Rungs of the ladder are approximately level.
3f3316e4-f01d-5a03-a2af-4637d940f52b | checkpoint | 5.6 - Scaffolding has been erected by appropriately licensed workers.
e8760cac-e387-5620-9ab6-470830ad9fb6 | checkpoint | 5.7 - Scaffolding is or has been erected and/or dismantled so as to eliminate or minimise the risk of falling at least 2m to people carrying out the work, in accordance with the regulations
faed25a7-0d74-5c49-bf12-7d35d9c1c221 | checkpoint | 5.8 - Safe access to and egress from scaffold has been provided during erection, use, and dismantling.
06596e0e-a7d6-5ec1-ae87-b458bc352bec | checkpoint | 5.9 - Written confirmation from a competent person stating that the construction of a particular scaffold has been completed, has been obtained prior to the use of that particular scaffold.
a1cf7634-7b7a-503b-98b6-a44b1401c2de | checkpoint | 5.10 - REGISTER-007 Plant and Equipment is up to date and includes all mobile plant in use.
92665bac-aa8b-572e-82c0-08a5392f0bfe | checkpoint | 5.11 - CHECK-004 Pre-Start Plant and Equipment has been completed for all mobile plant in use on delivery to site.
3dd77402-8a87-529b-8183-9c072abbce8a | checkpoint | 5.12 - CHECK-005 Regular Plant and Equipment has been completed for all mobile plant prior to commencing operation of the plant that day.
26a08f78-359d-5909-8059-66675eee2c23 | checkpoint | 5.13 - Mobile plant operators hold the appropriate high risk work licence.
23b709bb-1735-5ef2-90a2-edf28c5eaf62 | checkpoint | 5.14 - Where there is a possibility of powered mobile plant colliding with pedestrians or other powered mobile plant, a warning device has been fitted.
a556791d-1316-51ef-8b5c-74f5158d5808 | section | 6. Electrical
b2dcd8ef-695d-5a07-a1c9-d7a4c42cb637 | checkpoint | 6.1 - Electrical leads are arranged to avoid damage.
d2a5d551-016e-5c24-aaed-9a6546efb65d | checkpoint | 6.2 - Electrical equipment has been inspected, testing, and tagged in accordance with AS/NZS 3012 Electrical installations – Construction and demolition sites.
a3dea501-b49e-52a0-b686-be4f3b199e32 | section | 7. Hazardous substances and dangerous goods
28f006f5-6133-536c-83c5-e5fd046e9474 | checkpoint | 7.1 - All hazardous chemicals that are used, handled, or stored at the workplace are correctly labelled.
d9654d68-e223-5e2a-a924-23ef86d304da | checkpoint | 7.2 - A safety data sheet (SDS) exists and is available for inspection for each hazardous chemical used, handled, or stored at the workplace.
569fad8c-3f02-54bb-9e8d-8a513e63a228 | checkpoint | 7.3 - A register of hazardous chemicals used, handled, or stored at the workplace has been prepared in accordance with the regulations and is kept at the workplace.
73d14d34-271c-5e50-a0cd-036c9275e063 | checkpoint | 7.4 - A spill containment system has been implemented in each part of the workplace where there is a risk from a spill or leak of a hazardous chemical.
a5f93861-409f-57a4-9892-aad365d82b0e | section | 8. Corrective actions
a3895f4e-c7f0-509b-ac43-872a6873bc7e | checkpoint | Corrective actions
fefdfa68-8ae7-5784-8f52-ff31386b2624 | section | 9. Inspection sign off
19075f73-f3d6-5581-b9a9-39135e1c7056 | checkpoint | This workplace inspection checklist has been completed by;
4b32712d-5eb5-5f21-8318-9f10d9fee1e3 | textbox | Name:
8f6f1e26-c9d1-5d5c-beb5-fb775c1e28a2 | date | Date:
75e3ab6c-26b3-5c04-9c56-ec536230e4ac | signoff | Signature
690502ea-7da5-5119-ba91-b2aa394089de | checkpoint | I hereby certify that all corrective actions as identified in the above checklist have been completed;
be7ee8f6-2fdf-5e61-aee6-adf9bbb71704 | textbox | Name:
f58dc23b-c6d5-59c2-9d2a-57694b8eff87 | date | Date:
3e494399-cc9e-5e9f-964d-deff12bc6678 | signoff | Signature
7bd28543-904f-5683-acd7-cdd9184635f4 | checklist | CHECK-003 Site Establishment |  | CHECK-003 Site Establishment
8111ace1-1386-5c1f-8290-3df28e3c8d3f | section | Details
0b4ad232-5674-51d3-9408-aef0b58a609d | checkpoint-no-value | Details:
a9f0eb07-3912-523a-be5f-a802d6ff641b | textbox | Project Number:
be704f51-8345-5d07-82ad-4691b8d46bd7 | textbox | Project Name:
55438198-cfca-5417-84b8-414b08417475 | textbox | Project Manager (PM):
cecfc96f-5250-5907-bbf1-e0562cea155d | textbox | Project Address:
71a86034-b956-5203-b873-8d6f798b33ad | textbox | QA Platforms used:
d76c3f2b-8320-5708-a9da-38fbd066c69d | checkpoint | In house, FER & Specification Numbers
62d9c92d-c1ab-5446-89b1-bf80cbc0d1a4 | date | DATE:
087bf1f2-2a91-5ac0-811b-92888709522d | checkpoint | Site visit & survey
9d598589-23f2-5739-abd1-38084d2be5a8 | date | DATE:
f40bf70e-7c03-562e-9e73-8fbcd929c861 | checkpoint | Review Drawings & print for site
767f52ec-aec3-5775-a064-7229f459323b | date | DATE:
86a71627-b83a-5fe5-827a-1173c7cec5b0 | checkpoint | Review Fire Engineering Report
0d7909f1-54e9-5c90-92e6-074eee42c7aa | date | DATE:
eb035cf3-e47b-505b-b522-f71e191c12e9 | checkpoint | Allocate labour
0a895642-a262-5e46-a17d-2bd265707331 | date | DATE:
dae330e6-ef9c-57c6-9197-103abfd54f8e | checkpoint | Review Principle Contractors (PC) proposed baseline program
1692f978-f249-5f30-958a-396ff70c258b | date | DATE:
a55f05f2-ebad-534b-8cbf-1758e22f0184 | checkpoint | Create Fire Services Proposed Programme
07f60850-c8ec-5c07-8cb3-4760f7a199c5 | date | DATE:
7a356f7b-71e1-5c53-87a9-49ac25d117b8 | checkpoint | Upload to ALL necessary QA platforms
b5b18c80-8662-5430-9ca2-81c6feb62800 | date | DATE:
e81b739e-4825-5367-841f-3db753c333bf | checkpoint | Save softcopy in GM Dropbox
c65d94ba-f3ef-5124-bde6-1efbcc2ca74a | date | DATE:
c2e6bd69-c405-5afe-b004-c8b107fec18d | checkpoint | All employees have attended Induction
f2578d06-522d-52c8-91f5-609e406fe43b | date | DATE:
2630ff26-4768-5012-85c8-d89b8e40b4dc | checkpoint | All SWMS soft copies signed & hard copy printed & filed in the ‘on site’ paper folder
ccf4434e-fcc7-5408-8a54-c9b9b3f5816e | date | DATE:
5674c7a7-848b-557d-a867-52fce0b2bfd9 | checkpoint | PM Signature:
1ec883e5-6967-525b-ae22-80125604b1fd | date | DATE:
c87607a0-8578-5433-aab2-734b6f931e89 | signoff | PM Signature
69aefeee-08ce-554b-ae43-294b50258bd7 | checklist | CHECK-004 Prestart Plant and Equipment |  | CHECK-004 Prestart Plant and Equipment
8111ace1-1386-5c1f-8290-3df28e3c8d3f | checkpoint | Details
7e406bd3-b7bd-5d76-9931-cf25deaf2cc6 | date | Date:
33ad8640-e97e-50c2-9926-3d8f9d76d17d | textbox | Time:
4b42cb1e-2aaa-5b58-bdd7-fe7feab73fb0 | textbox | Location:
9ca4d3d6-254a-5ba0-9a8d-8957073fbe6b | textbox | Supervisor Name:
0b454d7c-2ee3-5e46-a2c9-e543b923b322 | checkpoint | Plant or Equipment
9377ba46-2c69-52a0-8266-b00504d5c27c | textbox | What Plant/ Equipment is being used?
9bf7a4c9-832f-575e-8384-448c444e3b10 | textbox | Person operating today:
36c0a7f9-1db5-5850-8057-101d561a5916 | button | Is this person competent and licenced (if required)? | Yes, No
e66ecb0c-c76c-5c52-8cd3-35c35db0f5b2 | button | Is the operator under the influence of alcohol or drugs? (If 'Yes' please explain in comments and find an alternative operator) | Yes, No
6193eb73-dbbc-561b-9e73-765287ddda57 | button | Is the operator tired? (If 'Yes' please explain in comments and find an alternative operator) | Yes, No
e0c7999b-e3a5-5d94-89e3-454ced95399a | button | Have you added this to REGISTER-007 Plant and Equipment (located in Dropbox) for this project? | Yes, No
5a565160-412c-57aa-9054-d8d08f52d8a0 | button | Have all relevant SWMS been completed? | Yes, No
f9910de1-77f1-541c-876c-35b08d530ef7 | checkpoint | Plant and Equipment Checks
cc198cca-6e0e-5785-a5bb-602a14f43cdc | note | As per WHS Regulations 2011, s206 the person with management or control of plant must ensure the plant is used only for the purpose it was designed and ensure that all safety features and warning devices are used in accordance with instruction. Please check the following:
df692a3d-aa1f-5f5d-8131-c01f7c74b64a | tickbox | Electrical switches, traffic indicators, front and rear lights are working
ac7eb67e-70fc-505e-afe1-a90d9ce7e05d | tickbox | Guarding is of solid construction, unable to be bypassed or disabled, is appropriately fixed and operates correctly (check latches/ locks and interlocks if fitted)
53dc5b9b-50bb-5b60-a5dc-0f3791e623ff | tickbox | Engine, fuel and lubricating systems are as per manufacturers specifications
371bf6af-6812-5875-abcf-eadf13b0be10 | tickbox | Tyre pressure is as per manufacturers recommendations
eb76e347-a548-534e-a1e5-002af739f10e | tickbox | There is no risk to the plant colliding with any person or thing (i.e. workers, other vehicles or plant, energised powerlines)
ff47e380-afc9-5a98-afd6-2d6ddd0f475b | tickbox | There are no mechanical or other failures (e.g. hydraulic failures, release of hazardous substances)
225e23dc-3a59-5aaa-a679-ff77cfa143e2 | tickbox | Seatbelts are available
67c28d37-58f6-5472-a9c4-1ad45b57a05e | tickbox | There is no damage to switch gear and controls and that controls can be locked off
e734dbec-0523-5a6c-afd3-114de7ac0a61 | tickbox | Emergency stop controls are marked, accessible and coloured red
2c10479f-4f61-5fca-a630-bc3773856309 | tickbox | Warning devices are positioned to work effectively
78a0f353-bca8-5dd4-81a0-773a2c902fe7 | tickbox | There are no hazards to the operator (e.g. things that could fall on the operator)
7fae1d5b-edab-5ebb-8300-94c1c1e4300d | tickbox | There is no hazard or risk that could caused the plant to overturn
17fd95bf-1ef6-58cc-90c7-dc5f50fe0a20 | tickbox | Maintenance and inspections have been carried out
2bcc0a89-8c1f-5fe5-958d-a1f1ba7233a4 | checkpoint | General Notes
d7295a42-11dc-51c1-80d1-cf9ed24c9857 | checkpoint | Operator Signoff
c685b88b-9455-5eaa-8271-b512fa65c130 | signoff | By signing I confirm I have participated in this prestart and understand my duties. I know what PPE I am required to wear whilst operating, the load limits and I am aware that it is my responsibility to leave plant not in use in a state that does not pose risk to others.
cc546369-bca4-51b6-ab24-8e4406ba760e | checkpoint | Supervisor Signoff
411f2708-55c2-5469-af77-82675a4393a8 | signoff | By signing I confirm I have conducted this prestart with the operator (above).
b729f711-3c58-5253-b38d-e9e486bd980b | checklist | CHECK-005 Site EOD |  | CHECK-005 Site EOD
8111ace1-1386-5c1f-8290-3df28e3c8d3f | section | Details
e7f3c29e-5e50-58c0-b5bc-209b95434737 | checkpoint | KPIs
585f70ac-f891-5ec2-9fec-3907ac21265d | textbox | What area did you work on today? Specify level(s)
2713e942-f90f-5435-af15-1d6fbba7acb4 | tickbox | Detection - In Slab Conduits
f52c0ebe-2c09-539c-9947-6117795f056e | tickbox | Detection - Rough In
fbb0ea32-c601-59bc-88be-be05948af914 | tickbox | Detection - Fit Off
29c8dff3-c12b-55ac-b6d2-a73300e1ed7f | tickbox | Sprinkler - Rough In
c55ba5d1-aae0-51b8-ad32-57ff46604b0c | tickbox | Sprinkler - Fit Off
b1fd0c79-a38b-5a75-97ca-ffe5a806fb22 | tickbox | Wet Weather Stand down (List names and duration of stand down per person in comments below)
802ef479-6714-55e6-aff0-98bb99502030 | tickbox | Safety Stand Down (List names and duration of stand down per person in comments below)
2659755a-4486-536a-826c-8fef4160249d | tickbox | Industrial Action/ Techs chose to leave site (List names and what time they left in comments below)
d6aa768d-18cb-5397-9287-98d25f058d4d | checkpoint | Productivity
2980cfee-9117-5285-b140-c09b634fcd84 | textbox | In terms of production, did the team meet the site goals today? | Yes, No, Partially
908bdb00-b673-5b2a-b157-127f5cc0e1f1 | button | If 'No', what hindered the progress? | Time management, Lack of training, Fatigue, Equipment issues, Other
83e2eb78-f524-577d-a553-431c8cdfeb3e | textbox | If 'Other' provide detail:
0da64418-8a08-5008-a58c-e5368b811be6 | checkpoint | Clean Up
a4b56289-60a7-5560-850b-cd779255b1da | button | Is your work area tidy? | Yes, No
ff4bf463-c7bb-5394-8c34-5d4b09caf45d | button | Have Chemicals used today been returned to secure storage? | Yes, No
66fadd24-fe5c-5935-bde3-47e79cb67ed4 | button | Have all tools been returned to toolbox? | Yes, No
9e969daf-8063-5f74-9d64-a2c822d49172 | button | Are all tools (including site iPads) charged and ready for tomorrow? | Yes, No
02aad785-bb47-52a7-a76d-2a92d59363f0 | button | Have you completed all necessary QA paperwork for today? | Yes, No
557047d2-63fe-5a87-a8bd-bcca7cdaf061 | button | Are all employees aware of where they are working tomorrow? | Yes, No
d3342bf8-6a33-5449-a30e-8053c0e49d7b | note | If 'No' contact management now
e2e5fcbc-fa6d-54e5-9ef7-e045364f2d00 | button | Were there any incidents, injuries or near misses on site today? | Yes, No
be74a426-676e-589a-a1d6-1a7817885208 | note | If 'Yes' complete the necessary reports
42c21dbd-9bff-5051-bd1f-f936237b2320 | checkpoint | Signoff and CLOCK OUT
5d29489d-1335-55db-945d-fe7621bce49f | signoff | This EOD has been completed in consultation with our employees and has been read, understood and signed by all employees on site at the EOD today.
47a05a8f-01d6-5308-b319-09c8bfef63a9 | checklist | CHECK-006 Daily Prestart |  | CHECK-006 Daily Prestart
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
af98ba3f-7105-4c3e-be07-e2ab6454306d | checkpoint | CLOCK IN
c58e65ab-a72b-4fed-85ca-080ec1fa3336 | signoff | Sign here to CLOCK IN to your shift
0b4ad232-5674-51d3-9408-aef0b58a609d | checkpoint | Details:
c67a5ad6-470a-5e2f-997a-f5f60b5e37f6 | date | DATE:
be60c24b-9584-50b3-85e7-c97aac850d9f | textbox | TIME:
5309490c-3518-5494-8898-6b41003721aa | textbox | SUPERVISOR NAME:
694414d8-1e1b-5f09-a0ec-7b8d590ad762 | checkpoint | Issues
29d3d625-f08c-54b1-bf3c-b22dfa3fbd75 | button | Are there any issues arriving from yesterday? If YES, detail in comments below. | Yes,No
88bc1641-daee-577f-b7e3-efc84c9a3236 | note | NOTE: If this requires a change to the SWMS then please ensure this is captured and relevant personnel inducted.
0662f670-ac3d-5439-af86-c1336a2b3861 | checkpoint | PLANNED WORK ACTIVITIES / TASKS
89e3b170-750e-51d8-a682-a426806358d3 | textbox | ACTIVITY / TASK
63009163-b71f-5d74-88ab-182d0339fbec | note | SWMS that relate to today's task/s
3217cd42-d7b4-5c06-8925-f508bd3b2eb4 | tickbox | 001 – Working with elevated work platforms
4e6ff252-595a-527a-99b7-8b0d317de7fb | tickbox | 002 – Wiring Rough In Minor
cd7e73e3-d703-52b7-9d32-c59cb15791e0 | tickbox | 003 – Fit off fire alarm system
b8ad95df-8b35-52b0-9faa-5efb930c096d | tickbox | 006 – Installation of pipe and fittings
2fc333ec-8649-5094-9bac-e7db22722260 | tickbox | 007 – Manual handling
793477a1-ebab-528d-ac0f-4cf5e41a28fa | tickbox | 009 – Pressure testing of pipework
abf682f7-668c-584c-add3-69603f01ffe9 | tickbox | 051 – Using platform ladders
aab532fe-44ab-58ce-84b2-320c641c1eca | tickbox | 060 – Inhalation of Respirable Crystalline Silica
55efd7fe-fc29-5217-af4c-3858f7a3124e | tickbox | 061 – Working in Major Area of Concern
774a66c3-3fea-5200-a769-32e4e0d72e01 | tickbox | Task-specific Safe Work Procedure
23c8da75-1795-5395-a9d2-b738a880bbe9 | checkpoint | Is a SWMS in place for ALL high-risk construction work and work procedures in place for all other works?
018251a3-fdc4-5187-821b-085ee9060fc3 | note | IF NO, STOP AND DEVELOP!
ebf4ce4a-0774-58f0-a144-522ec96b5a15 | checkpoint | Are you subcontracting out any works today and will you be interacting with other trades?
95fe8c17-73e5-5a12-84ab-0e88db6ce7aa | textbox | If YES, please list
279dbae7-8c1f-5553-98d3-d60918e8eade | checkpoint | Permits
ccbee4d0-b0fc-50f9-aba7-187627b00d3a | button | Isolation Permit | Yes, No
e9e5dd68-707a-5644-8f38-af984c59f3e6 | button | Have conditions changed since permit approval? If YES, please note changes below. | Yes, No
498988e2-fa90-543d-abe2-62bbc0b59d3d | button | Hot Works | Yes,No
49f83c80-5eec-5445-acf1-c5c9e01af072 | button | Permit to cut or drill | Yes,No
26129dde-acee-57f3-b54c-c083077e591c | button | MAC Permit | Yes,No
1d20b088-7c9c-5436-8f27-c1ecd33f79fd | note | Please list Permit numbers with description below, and upload photo/ attach file if available.
cae12b06-72bd-55e9-a701-9b47a7fdd5d7 | checkpoint | Environmental Risk
d043a4ae-8752-53fc-bcd7-920e72521388 | note | What controls are in place to manage environmental risk on site, specific for today; e.g. Wash out areas, maintenance of sediment fences and drains, monitoring of dust?
be468b16-df19-537b-854e-46bbd3df7b89 | tickbox | Clean up the general area
03b3f67c-e939-50e1-8cb2-87e19dbe9fd7 | tickbox | M-Class vacuum
054df62a-5657-559a-8159-5ed36c7947b6 | tickbox | Fit test and appropriate fit mask
3640b7ac-10ad-5ec3-ab6e-ae1284393ae1 | tickbox | Spill kit onsite
9bbc93b8-7fb5-5515-8c51-902ff1a50612 | tickbox | Other - detail below
903e1008-c734-5d92-8e65-be1215f53964 | checkpoint | Checklist for Activities
f1e2b79e-aefd-53e7-bcd3-7868bdf06e49 | number | Number of people in your Work Group
57c8c5eb-69d5-5928-bcc8-b3fe0690aa3a | button | Daily Risk Assessment Completed | Yes,No
d198e689-340f-595d-aa6c-5796b9e55eea | button | Qualifications/training of staff adequate for work activities | Yes,No
a89c730d-f0a5-5583-9141-f6861600debc | button | Plant and Equipment on/off site | Yes,No
c2abc099-5048-5862-be7e-69276e515d47 | button | Equipment safe to use | Yes,No
c35b1cc8-2353-5462-9376-b66fbffbe2eb | button | Work area inspected and safe for staff to enter and work in today | Yes,No
446e2139-b3e3-5032-b3b7-4b2ecf6682f2 | button | Appropriate and adequate PPE supplied to work teams (SWMS/SDS) | Yes,No
1297b9fc-83fc-5f03-8c96-a7ef0df8cad5 | button | Weather conditions for work to be conducted assessed | Yes,No
50775e4c-331c-5bcf-9d61-90de79b49eb6 | number | How many workers have been allocated for today’s clean up?
31b028e3-39b4-5b10-96c0-301d4210e7d4 | button | Pre-start communicated to all work teams including all trades & subcontractors | Yes,No
00d26647-1805-5512-8e68-9d14a06237f7 | button | I acknowledge that all Plans on my Dropbox shared file are up to date and I have confirmed this with management | Yes,No
f21451ba-8bea-5c8f-a381-24f716ce840c | checkpoint | Builders Briefing Notes
96ad1a92-eed7-5574-b446-3263c628aa29 | note | Attach a photo of the builders brief
2bcc0a89-8c1f-5fe5-958d-a1f1ba7233a4 | checkpoint | General Notes
79c2dc13-619c-4cd7-80ac-60aa3e45c613 | checkpoint | Mental Health Check-in
cd31bf4e-e2d5-5d58-b35c-fd75f58de3c1 | note | Prior to commencing work, ask your fellow workers: Are You OK?
0c6ae895-4776-5618-ae00-20be5d041a11 | note | Mates in Construction 1300 642 111
bd2c90e5-3cd6-5a5f-aefc-f4f34c1caf48 | note | Beyond Blue 1300 22 4636
3ecf9d4d-a367-5b79-a67e-d473daee966d | note | Gambling Help 1800 858 858
065e825a-d2be-5f52-accd-f30095264611 | note | Drinkwise 1300 858 584
462a3bfd-f982-5f3f-95bf-2a3e5632bbde | note | GM Fire Management 07 3519 7573
42c21dbd-9bff-5051-bd1f-f936237b2320 | checkpoint | Signoff
ad0d0126-8a7e-5cc0-84b3-32f1ee14e2ef | note | Remember to clock in and out of your shift.
2c27aaf3-a648-56ea-92c9-e1e22f200a26 | signoff | By signing I confirm I have have partipicated in this Prestart and I understand my roles and responsibilities today.
f915e0e6-f46a-4136-b82e-44dfc3d4420c | checklist | CHECK-007 QH Capital Infrastructure Requirements V.4 |  | CHECK-007 QH Capital Infrastructure Requirements V.4
1d6af0a5-343a-4da2-9767-b0699a40d468 | section | 3.4.1 Schematic design
d8d032e0-bf23-41a0-aac8-bec11efe49aa | checkpoint-no-value | General
d33d4eb7-84a9-5ecf-aa47-b570c02eaf94 | textbox | Project Name and Number:
98b2d698-bf8e-55e5-a2e5-a066c80bc4d6 | tickbox | Carry out on-going checks for compliance with regulations.
781dda55-baed-58fe-9438-fb99a24b2160 | tickbox | Monitor compliance of the developing design with the project brief.
971e6443-7ded-50e2-b02b-289d07a7d2f7 | tickbox | Draw up a strategy for fire safety and define the parameters for fire detection and suppression systems, and review with other design consultants, particularly the architects.
5d57da2f-938f-58ac-8ff7-8ae0432a5315 | tickbox | Confirm design criteria, scope and extent of fire services.
c71cd982-db9d-5365-a56c-55d3c500e9b9 | tickbox | Update recommendations to Queensland Health for their development of an operating and maintenance strategy.
2af3cef7-79ec-599a-b446-3b887d926566 | tickbox | Carry out initial overall spatial co-ordination.
7ea69ac8-648d-56b4-ab10-d55d64f24b5b | tickbox | Provide information for RDS, where these are used
1280191e-792c-5537-af3d-04504dbc81d9 | tickbox | Identify client requirements which will necessitate design input from a specialist designer, sub-contractor or supplier, and the timing of their appointment.
f6245023-754a-5be3-bf73-010768316b62 | tickbox | Define the essential performance requirements of systems. This may involve establishing numerical criteria for the nominal capacities of plant, the range of operating duties anticipated and consideration of the requirements for submitting samples and prototypes.
524adbf8-ec2d-59dc-bfd8-6399b82371fa | button | Have you advised significant allowances or constraints incorporated in the main design that may affect the specialist design? | Yes, No
39e3e565-089d-5fff-a079-e89506ab449b | note | If yes, detail in comments
73f7f6d5-69e3-5075-a4b1-abdfdbe6b3ed | button | Have you consulted with Queensland Health stakeholders concerning any risk management/WH&S issues? | Yes, No
7c339304-7656-55f1-a655-97089221df89 | note | If yes, detail in comments
96ab67ce-8196-46f6-836e-7e7e75c6aeb6 | checkpoint-no-value | Fire Services Design
213a9b49-4fbf-583f-a81b-fbbb2495cfed | tickbox | Determine main pipe routes around floors to and from risers.
acf17afd-a68c-52a0-a935-651315e2b1e2 | tickbox | Determine approximate pipe sizes, head types and locations, valve sizes and locations, and sizes of ancillary equipment (such as pump sets).
5695ec4d-9700-50f2-be79-b3749f2a483a | tickbox | Determine FIP locations, SIP and pump room sizes and locations.
50acc2e2-53db-5227-a2cf-323a330d0bb4 | tickbox | Design automatic controls systems as required to meet with the operational, functional and spatial requirements of the specification.
89efebcc-84ce-4a0a-9518-aa7674c4717c | section | 3.4.2 Design development
990021f0-cbed-40b2-b3aa-03c23ed68d0e | checkpoint-no-value | General
a46bd755-e3c1-5b03-81e0-6b173780c10e | tickbox | Carry out on-going checks for compliance with regulations.
f7e4dec6-f4ba-5a07-a2e1-a858fdf1e9bd | tickbox | Negotiate with public and other utility authorities for the provision of incoming services and agree spatial requirements.
e6e7ab40-c4b8-5ff0-b318-259a6357dc18 | tickbox | Monitor compliance of the developing design with the design philosophies.
1cb43195-3600-537c-8ba8-013d6a158972 | tickbox | Review design against NCC
f0a3e56e-b71f-5c1d-bb1d-d45a0a629b71 | button | Has a team-wide design review been conducted to signal the end of the design development stage? | Yes, No
3b0912c4-f616-4077-9c56-0d82965e23ef | checkpoint-no-value | Fire services design
5a66f06d-4f87-542b-87fd-da16fb105d8e | tickbox | Confirm design criteria for fire systems.
a98154ac-fab5-5fa7-a1d9-22bea42fcbe3 | tickbox | Establish indicative plant and riser sizes for fire systems and plant room locations/sizes.
f941ecee-aef6-415e-b81c-22e9257b3192 | section | Contract documentation
00219d00-eac7-4b84-8b94-b621fdd492d7 | checkpoint-no-value | Team liaison
9fcac840-785c-56fa-9db7-5a812027813b | tickbox | Check the provision for and adequacy of the preliminary builder’s work information previously issued by others.
470429df-8748-56aa-aef6-0c5ec7265bea | tickbox | Confirm builder’s work information for specified equipment or materials, or where alternatives to those provisionally or pre-selected are agreed.
48305564-5a7b-5cc6-aee5-42e24d5c4555 | tickbox | Co-ordinate the design so that the requirements for all access platforms, stairs, rails and protection elements required for future maintenance and operation of plant/equipment.
5dc2f038-6d8c-5547-a762-ffc3a18470a8 | tickbox | Carry out spatial co-ordination associated with major spaces: plantrooms, risers, depths of ceiling and floor voids.
aeaaa0ab-e79c-5244-a19c-a050b2c9d5b4 | tickbox | Consider requirements for installation.
ce5bfaf3-e4f3-5ad6-9395-df195c6b1dde | tickbox | Carry out final detailed spatial co-ordination between the building services and the structure/architecture.
7736dce6-42d7-527a-8684-88aa02412d86 | tickbox | Modify the final detailed spatial co-ordination for approved alternative equipment or materials.
1abef4dc-ae1e-4bee-978f-88c6024588b5 | checkpoint-no-value | Fire services design
e33106dc-dfad-54a9-8ac9-d090b4fc1a2c | tickbox | Carry out final detailed design calculations for all remaining services in accordance with relevant standards.
6cf43b5a-a183-5912-b7c8-6f3ebba7ed36 | tickbox | Carry out detailed design of pipework systems.
cfec3144-407b-5912-b69a-2a4482551eae | tickbox | Carry out detailed design of anchors, guides and other provision for movement of services and systems due to building movement.
951530df-30a0-51a5-b23a-a4f4fed6915b | tickbox | Modify distribution systems and equipment capacities as may be required as a result of final detailed spatial co-ordination.
aa1055ea-c872-500e-ad37-f51286d648b0 | tickbox | Check pump system duties based on the final equipment selection and co-ordinated installation drawings.
e7e9c3b7-54c8-5e24-ae4b-1c368170ec65 | tickbox | Specify final location of access panels, and other equipment required to facilitate maintenance.
c46a2598-28a3-5f04-b992-edfc151b03a7 | tickbox | Carry out final coordination with hydraulic engineer for all drain points
bb7484ee-a4e1-59f7-8fe3-88d028fe545c | tickbox | Carry out final selection of all terminal devices – sprinklers, detectors
f19d707d-8c35-54b8-8bba-f57d57b4090a | tickbox | Confirm designs for pump rooms, booster systems, brigade connections
e142baa0-a8d0-49f2-ba87-7b95fd2cb8d7 | checkpoint-no-value | Commissioning
bdaad973-c391-5d34-a28f-25a827cf297e | tickbox | Identify and incorporate into system designs the essential components and features necessary to enable the proper preparation and commissioning of building services.
2020fcd7-95de-5011-ab7a-caf434bd3faa | button | Have you reviewed all designs to ensure that systems are commissionable? | Yes, No
c245f664-f030-59ef-acfe-3c5d54f657c6 | button | Have you reviewed commissioning requirements? | Yes, No
2ccbbdd1-f387-59a4-8445-8ce7884b6fc8 | tickbox | Coordinate fire services statutory and authority testing requirements for the project
ac8e642f-402b-54a3-bc3e-d5503e68293c | tickbox | Integrate commissioning activities with other services, particularly mechanical and electrical services for shutdown and interface testing.
77916b04-4400-42f0-a29e-9d1f721f882a | checkpoint-no-value | GM Fire Sign Off
e0269d66-edc1-4290-a119-9b4e0afca6ca | signoff | GM Fire Sign Off
02c79fcf-456b-4318-9eb5-f809a80ceace | checkpoint-no-value | Consultant Sign Off
0146543f-22f0-4911-8805-e08b45b8b98a | signoff | Consultant Sign Off
c6634066-d1ac-42d2-a5aa-1e25e6c5cd7b | checklist | Communication (empty) |  | Communication (empty)
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
b8ed0eb1-7a01-48ef-9217-9bb946740e6b | checkpoint | Communication
28f62a6a-ed06-5a62-8deb-c8bd8334f680 | note
127dacb5-d0f3-5005-8b8c-418d2bbccc30 | checklist | FORM-001 Tool Box Talks |  | FORM-001 Tool Box Talks
0e50f726-5e25-5b32-be5e-0af50c2a4fbb | checkpoint | Tool Box Talk
e3272aff-5ad7-5584-9f05-601db13efeff | note | Project: Ripley Hospital
c4982672-0b0f-5087-ad36-2079a30053d4 | textbox | Tool Box conducted by:
b862c72d-bb88-5890-9585-9eb1d66d73f3 | date | Date:
201ee0d5-9875-55e5-a6b4-cf9a175f45ee | textbox | Attendees:
272ef767-b0f9-5d40-860f-37667165b540 | checkpoint | Electrical tools Tagged & Tested
de358699-2ee1-5f01-a52d-02e78a8f5dcb | note | ACCEPTANCE CRITERIA: Completed Onsite
9031bd57-1d4e-547c-b0ec-b6fb0b1da5db | date | DATE:
605677f5-661a-5bc3-a836-02384d30df5c | checkpoint | Tools checked for wear & tear
d34b0a75-d62c-564d-93ac-a1912bd32f6b | note | ACCEPTANCE CRITERIA: Completed Onsite
8aa8c1f1-8235-59cf-9f29-b950ab07c005 | date | DATE:
acfc8acb-9e64-5733-af2a-b8ca4ea1ea81 | textbox | Items for Discussion:
eabcda0d-be6f-512a-b32a-8bddf5fcbc83 | textbox | Items for Review and discuss at next meeting:
95cb37b4-7a6f-5ffc-99b0-5d11fbc535e8 | signoff | Signatures
ef9e0985-0562-5c9d-af07-52a3f1a33826 | checklist | FORM-002 Tool Box Talk Platform Ladders |  | FORM-002 Tool Box Talk Platform Ladders
106e79f1-1888-598d-99d2-b5a1def7ffd3 | checkpoint | Tool Box Talk - Platform Ladders
887bab57-3216-58e7-9dd5-6974b3a623f9 | note | DO NOT use platform ladder unless you are familiar in its safe use and operation.
ac68153f-7547-5f9f-b14c-f8801309e330 | note | Always complete as much work as possible at ground level before using the ladder.
3271903a-2c15-5d14-ac31-800aa151f93c | note | Make sure the platform ladder is stable before climbing.
5c4a49ee-d931-5509-bdad-bc64c1ca1617 | note | Project: Demo Project
00a320e9-986f-593f-bfe8-d25f2931da45 | textbox | Tool Box conducted by:
d0208122-f03a-5610-bde4-6bcb1a760f97 | textbox | Attendees:
da9865ac-d3b6-579f-bb6b-472d8b97b3d7 | date | Date:
fe834967-5fae-5142-ad41-d9de6147f88c | checkpoint | Potential Hazards
3674f2b7-e39a-58bf-b062-1209a407d5a0 | note | The folllowing potential safety hazards and risks have been explained to attendees:
5ea57c24-c9ef-5ac2-aae7-14b6543b15e5 | tickbox | Falls from height
e35ecb4b-a22f-5bcd-833f-fe852d10554a | tickbox | Falling objects
a3d70cbf-4729-5583-aee4-bcf73f29102e | tickbox | Awkward posture
016ab889-7fd8-5c55-95e3-1cf5f8ca44c5 | tickbox | Duration of task
674a0483-b78e-5388-ad6a-db7ac2554b1c | tickbox | Repetition of movement
3f4946f8-8fdd-526a-bb60-7b0d27db4098 | tickbox | Sprains/strains
a6af3874-9657-5afa-ac7b-5c30211f6885 | tickbox | Over-balancing
75d35ab2-1c77-568c-80f3-d9d45ae93ef3 | tickbox | Slip/trip/fall
4a7ce000-11b4-5942-9d59-57beec09de90 | tickbox | Electrical hazards
70790ef5-6074-57a2-b56e-987747b11967 | tickbox | Climbing with loads
1bd92719-b7cf-583c-a096-9b04e390c7ae | checkpoint | Pre-Operational Safety Checks
6ffbd377-bf17-5fba-98aa-8caef52856d1 | note | 1. Familiarise yourself with the safety instructions on the ladder.
a2ea6641-1eb7-56a0-a6e1-7e49d7e16115 | note | 2. Wear slip-resistant footwear. Never wear sandals, high heels or flip-flops. Wear appropriate clothing (e.g. no loose or flapping clothing, or clothing that restricts movement when climbing
aaf65bc0-57d6-5a03-b04a-8610a6416a50 | note | 3. Do not use if affected by a medical condition or medication.
2ba95fdc-b818-55eb-8e98-76f82b92f60b | note | 4. Keep ladder clear of live wires, electrical hazards and ceiling fans.
2c22d256-80a1-5046-8b5e-69ef43b328e9 | note | 5. When transporting your ladder check for overhead power lines, live wires, service cabling or electrical hazards.
93412ad9-195b-58ad-a5cc-688db75dd770 | note | 6. Carefully inspect your ladder to ensure there are no worn parts or damage before climbing:
ffc562ba-2d4e-5c0c-923b-aee111b51e69 | note | • joints between steps and side rails tight, all fittings secure, moving parts operate freely
639c69e6-a3c5-5051-a7d0-e2ca755bc18b | note | • rungs and platform are free of paint splatter, grit, oil and grease, welds are intact, and
5dc33034-ebb6-5e46-8386-62410b6d7321 | note | • all components of ladder intact including side rails, rungs, platform, feet, hand grip.
c1ec81fc-3779-5bbb-99e7-d74bdce4d420 | note | If any component is found to be worn or damaged, rectify any faults before use.
b6eb527a-c4c7-5a69-bb85-a66da835bc7d | checkpoint | Operational Safety Checks
df307b10-6066-5dfe-b2be-ccdabe4b711c | note | 1. Complete as much of the task at ground level as possible.
50ceb36d-3a89-51e0-a79d-8e7534c96b76 | note | 2. Ensure the ladder is placed on dry, firm, level ground/floor. Uneven footing may cause the ladder to rock. If this occurs re-position the ladder until all feet have firm contact with the floor. Always check there is no rocking movement before climbing the ladder.
2b10f449-9e31-58fa-8e70-0fe01b8c3789 | note | 3. If castors are fitted to the ladder, ensure rubber feet have firm contact with the floor when the springs are depressed.
37b91bc5-cb01-56fc-9108-0102c7c4058a | note | 4. Ensure the ladder is fully opened and the spreader bar is locked into position. Check for overhead obstructions before climbing.
7cac46ae-5fc7-5ee4-994f-75dd2980ea6f | note | 5. Only light work is to be undertaken on the ladder. Always face towards the ladder when climbing, and always maintain three points of contact with the ladder. Use a tool bag or tool belt to help to keep hands free.
64f23374-768a-5597-b8a4-9427fc451328 | note | 6. Only one person is permitted on the ladder at any time. A second person may stand alongside the ladder and help to steady it, or pass materials/tools up if required. Do not lift heavy weights that unbalance the ladder.
cea9f832-60c9-5a6a-8373-7c2c02db8309 | note | 7. Never stand or sit on the top cap or use the rails around the top as a step. It is not designed to be used as a tread/seat or step. Always stand in the centre of the platform.
c5338561-5326-55d2-8865-025c5fc7aa76 | note | 8. Do not over reach whilst using the ladder. Maintain the majority of your body weight inside the perimeter of the platform.
6a5bcd9f-5002-5193-afd2-5687e1f860a2 | note | 9. Do not ‘walk’ the ladder while on it. Always get off to shift position.
19c1d6b4-49ea-5f94-9658-6f1b832f0141 | note | 10. Before moving a ladder, take care to ensure that all tools and other items have been removed.
2d257990-358a-561e-bc89-f01924822341 | note | 11. Be mindful of your concentration and fatigue level. Avoid becoming overconfident when using ladders during repetitive tasks.
9d5b0bf0-53b6-5af8-a766-a7d78d594580 | checkpoint | Housekeeping
b7b52c7c-7b6c-5b22-8666-70b57f43c8ee | textbox | Items for Discussion
5c711e95-86eb-5f70-9f58-45404bea1e34 | textbox | Items for Review and discuss at next meeting:
0d24abf6-09a7-54db-913a-af58fcfdb176 | note | All attendees have been made aware they should:
fdb2ffa5-48c5-5b86-a475-b5e212b244b3 | tickbox | Return ladders to secure storage in a clean and in safe working order
ac8f4780-7d87-5234-98fe-0fee60585788 | tickbox | Regularly check ladder feet for excessive wear.
61838543-8502-5082-8baf-f0fa703ab465 | tickbox | Enter any maintenance in an equipment maintenance record
3015ae9e-0d1b-58a3-bfcd-57a87f411d9a | signoff | By signing I confirm I atteneded this ToolBox Talk.
f5798bfe-50a9-45ce-9e99-74bf659f1a22 | checklist | ITPS-100 Cast In and Penetration Installations |  | ITPS-100 Cast In and Penetration Installations
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
dc8dc4ec-0175-4c32-b6cb-411b1c089464 | checkpoint | 1. LOCATION - ENSURE
fa84a645-237d-5694-88df-13303662c59d | note | CIBSE C5.2.2 Set Points
8856d4f8-d887-590c-9746-947ddb4e7b95 | button | Is the device setout correct and accurate as per RCP and installation plans? | Yes, No
365f51a0-23f4-5ba2-9cab-fff8a8c85a81 | note | Add Photo
ad06b07b-8f87-45be-98ac-f6767f9dc513 | checkpoint | 2. CONDUIT INSTALLATION - CHECK
a1da785c-bd6a-5405-ae78-7fd10a4e4ec1 | note | AS1670.1, AS1668.1, AS1670.4 and AS3000
36178cce-8dd9-57b3-ba94-81d53f364b6e | textbox | Drawing Reference and Revision Number:
a74e4e42-804d-548d-9434-daa59265ac7a | note | CIBSE C5.2.2 Set Points
3fde345b-5a76-5bd8-9050-105f61855e74 | note | Are Conduits routes are correct as per IFC Drawings?
43acea78-15b4-5c04-a066-3b214b52fdf6 | note | Are Conduits are joined correctly and glued using approved PVC piping and glue?
1e1d5b8a-d6c5-53c4-bfb7-43b5a02d5199 | button | Are Conduits are tied in properly to prevent movement and damage? | Yes, No
62e93803-0128-501a-ad45-346f406ae078 | note | Add Photo
1f3b7f36-a447-4c87-b993-dc6c87e6e26c | checkpoint | 3. SLEEVES AND PENETRATIONS - CHECK
de28e181-dd76-5a6c-aa43-af90be8136b4 | textbox | Drawing Reference and Revision Number:
55a8c205-e474-5e44-bebb-88bd82b55a8f | note | CIBSE C5.2.2 Set Points
75d225e8-a4fa-5692-b591-3360ec4747c4 | note | Are sleeves the correct type, size and quantity as per penetration drawing?
42eb5719-0542-52d5-8d30-008a95ed2f3d | note | Are sleeves routes correct as per IFC Drawings?
4fa7a045-1f9b-5808-b4b5-35bfa86c9f0f | note | Are conduits joined correctly and glued using approved PVC piping and glue?
2beaae99-fa71-5c2d-b78f-f1f29688231f | button | Have sleeves been tied in properly to prevent movement and damage? | Yes, No
ff06a625-ae90-55b2-ace6-091bd880b673 | note | Add Photo
95717b78-837d-4466-b036-e82e4cb0c0de | checkpoint | 4. PRINCIPLE CONTRACTOR - CONFIRM
4c1bc059-dc12-5480-a499-ccb5f4a4ae41 | note | CIBSE C5.2.2 Set Points
61f60b54-4573-5041-9d0b-50d96b7ade10 | button | Is the Principle contractor's sign off required prior to pour? | Yes, No
304c8ece-c1cd-5cef-945a-44e0c207b820 | note | Add Photo
16f42117-c5b9-41b3-8355-6b714bb0c0ba | checkpoint-no-value | GM Fire Sign Off
d8008e6a-45e8-42e8-bac3-f1f58d76e990 | signoff | GM Fire Sign Off
fa160aa9-3b27-4aaa-9a0d-3e19257f17bc | checkpoint-no-value | Principal Contractor Sign Off
00cd0df0-d3bc-4f21-8646-96327675e270 | signoff | Principal Contractor Sign Off
94df26f3-fcbc-4fc9-bda6-e329cd1cb37e | checkpoint-no-value | Consultant Sign Off
e8bc19b1-0823-4a0e-829a-b80bc16b8eed | signoff | Consultant Sign Off
b90ea83d-ebfd-4240-bd81-84aa7826a4a7 | checklist | ITPS-101 Fire Alarm and EWIS Rough In |  | ITPS-101 Fire Alarm and EWIS Rough In
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
45b46ff3-5947-46e8-894e-30956edce56c | checkpoint | 1. CABLE - CHECK
d407c667-900b-50d1-9aea-d851a0d09ab6 | note | CIBSE C5.4.0 Wiring
dcef8a34-27ec-58c5-8fdd-bfb47199ef96 | note | AS1670.1, AS3000
45cd4aeb-9763-5905-b316-41fc41ccfb3b | note | Is cable installed the correct size and type?
731396c1-d892-59ff-a964-e45c9a32dd77 | button | Is cable secured at regular intervals? | Yes, No
ed4775a8-25ce-5e1b-98a9-c90556948b15 | note | Add Photo
59989314-6bda-59e4-ae9e-25a4c907fb3e | button | Have you attached a photo of cable markings for Green Star Compliance? | Yes, No
e0be73ac-3067-5737-8c8a-5b7825998290 | note | If no, stop and attach now
dde749f2-628b-4112-9ad7-5a7033df431c | checkpoint | 2. FIRE RATED CABLE - CHECK
7b0f8ec4-63e6-511c-8a7c-eb4b3b2ecf1a | note | CIBSE C5.4.0 Wiring
a35d09fe-d837-59e1-96ee-e8560af032ad | note | AS3000, AS1760.1, AS3013, AS/CA S009
bd45a580-dd3a-5c77-9aed-9bfed1dda49f | note | Have fire rated cables been secured with fire rated fixings at a minimum of every 1200mm?
5ab6d838-5190-532a-b811-1d43d4214e8b | note | Have compliant fire rated cable and fixings have been used for required circuits?
6f8aba49-d041-5e4a-900b-4ce3e2f1827d | button | Are fire rated cables installed as the highest circuit? | Yes, No
ae268211-86ad-5720-9710-e4fc22654e54 | note | Add Photo
fb5bfd19-029d-4e51-938b-9606f1cdf416 | checkpoint | 3. CONCEALED SPACE DEVICES - CHECK
79213002-d4d1-5555-a7c7-56be73520c14 | note | CIBSE C5.6.0 Sensors/Detectors
06592493-3b60-5d3e-b311-77b78009b3bd | textbox | Drawing Reference and Revision Number:
e6f3e624-ec84-5e53-8b3a-3da2503ae049 | note | Have all concealed space devices been fit off?
3cdceb5d-948e-5bb8-840b-5585027f7aa6 | button | Has remote indicator cable been left with adequate length? | Yes, No
2cdba614-9f5e-5260-bb61-24d6cff26a9e | note | Add Photo
8765a293-da3b-4d68-8f22-0517ce1b1eea | checkpoint | 4. ROUGH IN - CHECK
6dab3198-dd8e-553d-b777-343a4b2cf500 | note | CIBSE C5.2.5 Control Loops
fdea5388-92c3-55ef-b54d-b48e4bd35a5a | textbox | Drawing Reference and Revision Number:
97faac36-472e-593f-a6ea-24cd4aad5897 | note | Have all devices been roughed in?
705c4d4e-4a94-528b-b3f4-f91fee7a87d1 | note | Is there adequate length left for fit off?
cd816343-1142-55da-bdcb-36c4c5aeda15 | note | Are device locations accurate as per the latest RCP?
c5231c96-8474-5420-b200-89e3f7e9257b | button | Have circuits been metered for continuity? | Yes, No
43b1a8cc-832b-5fd0-8d93-a2e6bfd16024 | note | Add Photo
4c7765d3-b4ca-4c90-9974-df8c21d56d20 | checkpoint | 5. MAG DOOR HOLDERS - CHECK
2f0f4012-47aa-5d08-a279-0640c1ec3c76 | note | C5.2.2 Set Points
a0b39c7f-3082-5262-9a1b-7149af582d33 | note | Have wall noggins have been installed?
d8aaa683-ed95-5c8a-8790-b6f05d693468 | button | Are cables roughed in to the correct location in wall? | Yes, No
272a5277-6bfe-4a73-9585-88efb6d89e46 | checkpoint | 6. SEGREGATION - CHECK
42abc833-7219-52e4-99c4-741112e44ba4 | note | C5.2.2 Set Points
ba973233-c4c3-59a8-b368-08edf32f9dcd | note | AS3000
1c9c8ca1-2e31-533a-8429-ae60f0e7c5d8 | note | Is there a Minimum of 25mm from water & gas pipes?
f3f5bc88-7521-5461-86e3-286a8b0abc8c | button | Is there a Minimum 50mm between ELV & LV installation or a physical barrier? | Yes, No
ec2d9832-baab-4c8e-9d9b-cfb673b2e4be | checkpoint | 7. AS WIRED DRAWINGS - ENSURE
17ed4f04-39b2-54a4-b619-2ddf630691f8 | note | C5.4.0 Wiring
80da41fe-bd9b-5646-acad-62c16a7df9bf | textbox | Drawing Reference and Revision Number:
e6a446e9-cc0c-59f8-808c-3c76eb8ffea6 | note | Are As-wired drawings complete and accurate?
b5922c2c-2f1d-5041-a779-c6e13a5c2e70 | button | Have photos been uploaded to Dropbox? (as well as below) | Yes, No
2a5d3121-b058-5a33-8cd1-41f1390dccbd | note | Add Photo
cdb613db-f123-4107-9e03-d5ed55a30340 | checkpoint-no-value | GM Fire Sign Off
277467ba-4df6-4360-aaae-99aa1c783dc5 | signoff | GM Fire Sign Off
2f5d4c6a-4cf5-427b-808f-804b51d2fa18 | checkpoint-no-value | Principal Contractor Sign Off
8fb69481-1a57-43a5-a64a-9e367db36022 | signoff | Principal Contractor Sign Off
0a3afe04-4db6-4032-8bdd-7565d9511022 | checkpoint-no-value | Consultant Sign Off
4b0573f5-746c-4329-a5d2-1967bd54fe3e | signoff | Consultant Sign Off
b284d79d-0f6c-4a37-b3dc-77b04948d448 | checklist | ITPS-102 Fire Alarm Fit Off AS1670.1 |  | ITPS-102 Fire Alarm Fit Off AS1670.1
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
1d8e45f9-c410-4033-836c-30db7cc4a3d5 | checkpoint | 1. DETECTOR TYPE AND LOCATIONS ARE AS PER THE LATEST RCP
016f8650-28a3-52c0-a9b6-827a75f8be1d | note | CIBSE C5.6.0 Sensors/Detectors
af1b8588-c8f0-53b9-9c4f-8b2b0177d834 | textbox | Drawing Reference and Revision Number:
e3132df4-e742-57a1-8319-77f35f9b2639 | note | Add Photo
5bda0b20-78c9-49d3-84e4-5f2e6e47c13d | checkpoint | 2. DETECTOR ADDRESSES ARE MARKED ON AS BUILT DRAWINGS
0fec06c4-fc16-593d-b241-20425d010ddc | note | CIBSE C5.2.2 Set Points
02e3ed53-df61-529c-8db0-c9133e1c18b8 | textbox | Drawing Reference and Revision Number:
6b88e687-bbe8-5348-8ba2-d38976f4a1fc | note | Add Photo
362a5407-6741-4f3d-9420-19566378ad46 | checkpoint | 3. DETECTORS MAINTAIN MINIMUM CLEARANCES FROM WALLS, PARTITIONS & AIR SUPPLY OPENINGS
62e9cd7f-9d73-5ccd-b31a-a915ba9d9ae3 | note | CIBSE C5.6.0 Sensors/Detectors
e2e3aecc-b8dc-51cc-8b64-9831bd2fdce7 | note | As per AS 1670.1 - 2018 - 5.1.4 & 4.1.4;
ca546bae-2a91-58f0-b9bc-08d91ae4a21b | note | Is there a minimum of 300mm from walls & partitions?
03a74e1b-599d-5523-b90c-a0c5684b3621 | button | Is there a minimum of 900mm from air supply openings for smoke detectors & 450mm for heat detectors? | Yes, No
bcdc3bf4-e145-56fa-bed0-655e7820d39b | note | Add Photo
50f14b95-8df0-42f8-b60f-d4b6f3ed6699 | checkpoint | 4. DETECTORS MAINTAIN CLEAR SPACE AROUND SAMPLING POINT
9f225659-f303-5215-9b8a-86b347e9c296 | note | CIBSE C5.6.0 Sensors/Detectors
3f94fc63-e82c-50c0-8723-64df8c0d572a | note | As per AS1670.1 - 2018 - 3.27.1;
5db903c8-5dbb-50d2-9701-7ca2f64a8202 | button | Has a clear space of at least a 300mm radius and 600mm depth been maintained from the sampling point? | Yes, No
b5611574-04b0-5a2f-abf3-340a1f2c988d | note | Add Photo
7a5e090a-f1e6-40bf-a034-b0ab00814ac5 | checkpoint | 5. PROTECTIVE CAPS ARE INSTALLED ON ALL DETECTORS
7e3323c0-4efd-52c8-aa36-26817e077b5e | note | CIBSE C5.6.0 Sensors/Detectors
918b7a71-7bb3-54de-95fe-82a8ef50c599 | button | Have dust caps have been installed on detectors to prevent contamination from construction work? | Yes, No
5c5b54db-66e7-5be4-a52f-d2079526d5a0 | note | To be removed once dusty works are complete, or at commissioning.
a9c14150-6bc2-5e21-86bb-e5a8792ad638 | note | Add Photo
37e6f846-f0b8-4248-8cb7-46df2edbb1b2 | checkpoint | 6. MANUAL CALL POINTS INSTALLED AS PER LATEST IFC DRAWING.
cbed881e-3474-59ac-a14a-60d55f901eba | note | CIBSE C5.10.0 Manual Call Points
3c011069-f024-5938-982e-3f39c05784ae | note | Have MCPs been mounted between 750mm & 1200mm above floor level?
a6f76f0c-07ad-5db7-ba10-d28c9c3957d0 | note | Is there a clear space of 300mmm on both sides?
05407bf2-a729-53e2-a14a-1dc246553b57 | button | Is there a 600mm arc directly in front of the MCP? | Yes, No
2eedc637-c3e1-5827-90b6-9300582d9e0b | note | Add Photo
db9a18f9-791d-46ce-b8a6-f10b639c71de | checkpoint | 7. MANUAL CALL POINTS SPECIFIC LOCATIONS
b70fb5b4-826d-547d-b99c-384e8e2f7cc1 | note | CIBSE C5.10.0 Manual Call Points
3d500cec-b5f1-56df-a633-70d22b19851e | note | As per AS 1670.1 - 2018 - 3.14.2;
52dc7655-21a0-5ab2-a0a5-f2cdb99729f5 | button | Is at least one MCP installed in a clear and readily accessible location in the circulation space of the main entrance of the building? | Yes, No
7461bea4-bf4b-579d-82c3-baa6e31580e2 | note | As per the NCC2022 - S20C4;
2df8848f-a04c-57e5-a0d4-67416a23f7f8 | button | If in a Class 9a building, have you ensure MCPs are located in evacuation routes so that no point on the floor is more than 30m from an MCP? | Yes, No, N/A
720a497f-faaa-54f3-9f6e-9d1626f0c095 | note | Add Photo
ccc9d2db-5b82-482b-9186-3a4e41e63746 | checkpoint | 8. FTRS
30cbcf92-8466-59c7-bcb8-ce3840b74567 | note | CIBSE C5.8.0 Modules Input/Output
692be321-a7ce-5017-ac1f-36a53d887ace | note | Have all FTRs been installed in correct locations as per latest drawing?
8535eb60-7d38-592f-ae6e-fb4212f66705 | button | Have the right quantities been installed to ensure correct operation as per the fire & mechanical matrix? | Yes, No
c9fd3aff-c7da-5e89-b56d-42897e044323 | note | Add Photo
748c4f93-3a04-4afe-b445-d2dd0d010ba0 | checkpoint | 9. MAGS
e4cb82b3-fdc2-5f80-a074-94950bd537ed | note | CIBSE C5.8.0 Modules Input/Output
424e97cc-861e-55c0-8b41-3efe50397f1c | note | Have the mag door holders been secured properly to withstand the weight of the door?
93afc210-c352-5318-8602-6ee6ede953fe | note | Have they been installed at a uniform height on each door leaf?
aaec8728-b6c4-526d-98ea-dfc67be16124 | button | Has a release switch been installed? | Yes, No
cce6bb9b-70e1-5380-a3b8-2a97e2f0bf4f | note | Add Photo
031992e3-d3da-4b46-8966-4a06b1f40745 | checkpoint | 10. MASDS
6789c272-b813-53f7-8438-dd69fbfe40b7 | note | CIBSE C5.6.0 Sensors/Detectors
ce608cb6-46ea-5997-93b2-dbf67f4452eb | note | Has all pipework been installed in line with the Aspire calculation & design?
568242e8-6db7-5164-956d-3a906b26f002 | note | Has all pipework been glued?
5dfe8f56-2d75-5ad7-a215-2d82b12bc706 | button | Is the head end unit installed in an appropriate location? | Yes, No
e2b913eb-d127-5bdf-ab70-f14ff0f945ef | note | Add Photo
a6f578a0-5a72-4d67-8f37-d9ef215d9ebd | checkpoint-no-value | GM Fire Sign Off
ea739bc9-486d-4296-b721-8d3a1e91afcf | signoff | GM Fire Sign Off
a87ba7d5-31f9-44b4-b3bc-54ecb442022d | checkpoint-no-value | Principal Contractor Sign Off
ed9465ff-c843-45be-b55d-d608838617cf | signoff | Principal Contractor Sign Off
a4706a81-8646-4552-bdf5-bf590b6378b3 | checkpoint-no-value | Consultant Sign Off
95db4bf5-72bf-466f-a9c5-ac2660ca6835 | signoff | Consultant Sign Off
59c6608f-364a-4dd4-a210-550d65a21059 | checklist | ITPS-103 Ewis Fit Off AS 1670.4 |  | ITPS-103 Ewis Fit Off AS 1670.4
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
8354bacd-e20f-437c-8f64-a1c55f50c817 | checkpoint | 1. WIP
80213851-0771-5c00-ab59-8045803f0d3b | note | CIBSE C6.2.8 Warden Intercom Phones
ab8333be-6505-500c-8ecf-35e94de0abae | note | Are the Warden Intercom Phones mounted at a height of not less than 1200mm & not more than 1800mm?
ee32d9a0-6dfd-59a5-8a1c-3e408bd3a619 | button | Is there one WIP per EWIS zone installed within 4m of the exit? | Yes, No
5c85a3cf-033f-5a88-b104-0318d6fb5e96 | note | Add Photo
6f25cd62-fe35-4da4-b7ed-1720eaf72d9a | checkpoint | 2. SPEAKERS
43be6720-ba5e-502e-a079-8113ef5869c9 | note | CIBSE C5.2.2 Set Points
22c8a62a-037e-5672-a53f-9601d97eb434 | textbox | Drawing Reference and Revision Number:
bf7515c5-b563-5142-9f20-ef4a10a5d079 | button | Have all speakers been installed to the latest RCP? | Yes, No
72c2ada4-c5a8-545a-b674-ca646d017a79 | note | Add Photo
a9d79c7e-268d-4094-8ae6-e86db1173fa1 | checkpoint | 3. STROBES
77d0ad25-c9dc-5ea6-a18e-5c8b5d91da49 | note | CIBSE C5.2.2 Set Points
ddead425-9e85-51d7-8c20-d6543b151046 | note | Have all strobes been installed to the latest RCP?
0d6a1b64-5c82-52ee-9963-732408fc5646 | button | Have all strobes been labelled "EVACUATE" with 25mm lettering? | Yes, No
e85486bd-aba1-5e33-b5cd-424d90cb08c9 | note | Add Photo
ac57f7aa-33c8-4e28-9f1a-4ab9fc6763f9 | checkpoint-no-value | GM Fire Sign Off
a2348c0c-bc59-4339-9b32-9ffeb2c90eb8 | signoff | GM Fire Sign Off
4dba8580-58f7-42c3-b021-563a21def44c | checkpoint-no-value | Principal Contractor Sign Off
cacdcad3-f731-474d-b75d-f43a18f92b05 | signoff | Principal Contractor Sign Off
2a2dcfb3-1e4e-4b44-b1ab-2469ee4a235a | checkpoint-no-value | Consultant Sign Off
29f1fabf-8180-49c6-ad7e-3efc51b49cf7 | signoff | Consultant Sign Off
b1b4ddb4-4eac-4605-b209-46f75ea1f792 | checklist | ITPS-104 Fire Alarm Cable Tray |  | ITPS-104 Fire Alarm Cable Tray
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
643ec408-ccb2-4d60-a28a-d4b2b541294a | checkpoint | 1. LOCATION & INSTALLATION
9e93d15b-2910-507a-acce-09887e0cb4fc | note | CIBSE C5.2.2 Set Points
4b57f018-dfca-5368-9b28-67f1c4700f01 | note | Is the tray as per drawings and model?
db53a595-d2ad-5912-8c8e-7b03d0f35801 | note | Have all sharp edges have been removed to prevent injury or damage to cables?
0bf98f9f-a38d-5779-a5ff-ebb3daa178f4 | button | Is the tray supported at intervals of no more than 1m? | Yes, No
fd9e504e-775a-5a83-9a48-3e63b2984e70 | note | Add Photo
3c905cd3-a523-4733-9a0f-7548d0c27c84 | checkpoint | 2. FIXINGS AND FITTINGS
079b835a-416d-556f-a259-b79fbeac806d | note | CIBSE C5.2.2 Set Points
50f4f1ed-c7f3-599f-8c75-cf6b764a6bda | note | Have the appropriate fixings and fittings been used (for indoor/outdoor use as applicable)?
b2e06748-cab2-56c7-9847-aa0c07f3c3d5 | button | Are Seismic fixings as per the design documentation? | Yes, No
156de863-cb7d-5382-958d-774fc4f2fe6b | note | Add Photo
5fd09522-127b-41e1-88d4-4e095b3195a4 | checkpoint | 3. CABLE SPACING
acab9265-e6fb-547f-a438-43dc7fe4627d | note | CIBSE C5.2.2 Set Points
f282c869-f874-5969-8332-38ab27a4c2d6 | note | Generally, where possible install in the following groupings:
20aeb6c4-a336-562c-b7d2-ed4c237e87c0 | note | Detection Cabling & 24v Cabling
4ff6017a-f86e-5879-9124-9e775f1f965e | note | EWIS/OWS Cabling
ddbf99f4-8808-5972-a9af-6e57fc2a31c9 | note | WIP Cabling
eb2343f5-c63c-521f-842c-3b5efe58cbe7 | button | As per AS3000, 3008, and S009, is the segregation of ELV and LV cabling at least 50mm? | Yes, No
fb35b075-88be-547c-aed8-53f33e1c43e9 | note | Add Photo
65ec1ada-8ed0-4b0a-9e9b-4d5c7685e9fe | checkpoint | 4. SEISMIC
8fe53ce5-8309-59a1-99f3-907e23fde1c6 | note | CIBSE C5.2.2 Set Points
78a282c9-4375-53ba-8a47-2493844135bc | button | Has the cable tray been installed as per the seismic drawings provided? (Use of stablity strut or catenary wire may be required) | Yes, No
641b444b-32bd-50ea-95b9-e51e667ccb23 | note | Add Photo
c7306678-7229-45e4-84a5-aabc23ad625a | checkpoint-no-value | GM Fire Sign Off
16a275c8-5024-46bf-a6bb-4341df1dfdab | signoff | GM Fire Sign Off
56436dc3-439f-4efc-9d39-e5ea024f0ee4 | checkpoint-no-value | Principal Contractor Sign Off
1feda29d-b124-433f-9202-bc221fc31cb4 | signoff | Principal Contractor Sign Off
2e301c61-d906-4f88-b925-4b56a365dc5d | checkpoint-no-value | Consultant Sign Off
6b73d4e6-1632-43ba-9ddf-7ac0b56d72fe | signoff | Consultant Sign Off
0c8258a2-001c-4ed0-8446-ace0f209482a | checklist | ITPS-105 Fire Indicator and EWIS Panel Installation |  | ITPS-105 Fire Indicator and EWIS Panel Installation
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
382f3b7e-86e3-4ac2-928e-c4ec20f302cd | checkpoint | 1. LOCATION
e4591957-7984-5bf2-bbb3-c3215b7d0c28 | note | CIBSE C5.2.2 Set Points
2e414a32-3757-53c3-8807-97bc7517aaab | note | AS1670 (Section 3.9)
a5f10b72-9073-55f9-a191-f557e7b34521 | note | Do you confirm the CIE is:
8cfcca23-d822-589c-ac01-178fbcc0769a | note | Not in an area used for storage of combustable material; and
582b08e3-9b52-5278-9459-6e5136a74fed | note | Not obstructing evacuation of the building; and
21c5e602-eba7-564d-a73f-1985dec64b13 | button | Not in a room containing sprinkler valves, pumps and motors? | Yes, No
3d746227-ccfb-544f-b819-629adf46cee2 | note | Add Photo
e48dbbe7-caa6-44b5-8bd6-7c257db97b4f | checkpoint | 2. LOCATION
93f0e31c-8be0-5e6b-a68d-3c53c62c5ec4 | note | CIBSE C5.2.2 Set Points
d72881cb-7294-5f0f-ba45-8cdba42d6fd6 | note | AS1670
1e509d00-374a-5d58-9a92-ee683f564dbe | note | Has a minimum clearance of 1m in front and 0.5m to each side been maintained?
ca581566-63f9-5e48-8fac-c176166f5639 | button | Where obstructed by a door, are the words "FIRE PANEL" in contrasting colours? | Yes, No
20150295-4622-5656-9e6f-3718b2141065 | note | Note - Where the door reduces the sounder, an external sounder may be required.
4697bc17-7043-5cc5-837f-95475e925d45 | note | Add Photo
e2100741-0235-4a5d-bd45-b81cfdd4eaf8 | checkpoint | 3. CONTROLS AND INDICATION
394fead3-29e8-5809-bdfb-3aae0d67a3a9 | note | CIBSE C6.6.0 Brigade Interface – FFCP
60b11447-4323-543b-92f9-f856abbdc59c | note | AS1670 (Section 3.9)
68be0137-d824-5763-8f58-5d207aac908e | note | Do you confirm CIE has controls that are:
03631b3f-698c-5b30-9d61-1f566f4249d9 | note | Not less than 750mm from floor level; and
acfd8358-75db-5a22-a61e-04a18f99599b | note | Not more than 1850mm from floor level; and
72fc9aab-e229-5c27-8d96-9e90f482989a | button | The access to controls is not obstructed? | Yes, No
d1f0d865-926b-5eaa-8cb9-c15c386a21da | note | Add Photo
0ea40c70-9c31-4808-b1d7-2e22f2dc0a33 | checkpoint | 4. CLEARANCE
9b8b4ce0-75b9-52ea-9694-a67ae1818367 | note | CIBSE C5.2.2 Set Point
71d0f556-2e42-5202-b0eb-810743db5a19 | note | AS1670
57f4cb7b-04c1-555a-bfe6-c107842e7415 | button | Is there a minimum clearance of 1m in front and 0.5m to each side? | Yes, No
210022cb-cd94-5c37-8efc-f5bcbece59e0 | note | Add Photo
acf4c4a0-3fff-4096-b154-b7ab94274de8 | checkpoint | 5. EXTERNAL ALARM
4a6ac7ad-c5bf-5f06-84d6-e5acd3cbef5f | note | CIBSE C5.2.9 Alarm Functions
bdfe5fa6-7e53-5922-8300-f86665ea56a0 | note | AS1670
e8011532-eaeb-595a-a1fa-4d2de949672d | note | Is an external wall mounted VAD is located on the front façade no more than 10m from the DBEP?
51803b2d-774b-55f3-a5cc-2f84b8a7919f | button | Is it visible from at least TWO directions, and mounted with the words "FIRE"? | Yes, No
0c44d543-e048-56bf-b80e-7e280e562413 | note | Add Photo
7f8ffa39-82c6-41ce-8e70-835a800260c2 | checkpoint-no-value | GM Fire Sign Off
65eec966-cfad-42d2-919f-f00847c58621 | signoff | GM Fire Sign Off
14f98fbe-049f-48e4-a25f-ce52ae83296c | checkpoint-no-value | Principal Contractor Sign Off
587522a2-bbbc-4264-bb5b-cb1630121eda | signoff | Principal Contractor Sign Off
8803dd27-fc25-43ce-bbd1-f575d0ce6ff8 | checkpoint-no-value | Consultant Sign Off
15a15b8d-bc25-47e7-aa83-7556934896d6 | signoff | Consultant Sign Off
30a5c300-afb2-4b05-9e9a-7fd01ffbd3fd | checklist | ITPS-106 Sprinkler Pipework Rough In | itp | ITPS-106 Sprinkler Pipework Rough In
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
bd2be394-4262-4c4c-9778-475823007700 | checkpoint | 1. PIPE LOCATION & HEIGHT
362b2584-e9cd-5258-9b37-7ca6521f2752 | note | CIBSE W5.2 State of the System
e2fc4368-e99a-5bef-8999-4b8c8154de17 | note | AS2118.1-2017-Section 14.14
e8b8724b-74a1-5452-8dcd-673ad2bb9a17 | textbox | Drawing Reference and Revision Number:
dc37f4c6-d28a-5213-95ac-5ad02dce525d | button | Have you reviewed the Fabrication Cut Sheets? | Yes, No
469233bc-61d8-554b-9b4f-bcb2cf955d4b | note | Is Pipework setout as per dimensioned install drawing?
52bd183b-944f-5eb0-810d-fac6c0c80f21 | note | Are Pipe heights correct?
0e325544-8ad6-57a5-9c40-c7f4068d8d5c | button | Have Pipework alterations been approved and recorded for as-installed records? | Yes, No
7e7c74b2-a8ff-5c11-8261-f58abe476940 | note | Add Photo
1d014011-6030-4050-8a67-c6feefbf3f9d | checkpoint | 2. PIPE SUPPORTS
1de519d8-0f00-5f7b-95fb-f41e7c66ad43 | note | CIBSE W5.2 State of the System
103b3048-2dc9-5c2f-aba9-ae9f357d66ae | note | AS2118.1-2017 - Section 7.8
1131d07b-c524-5f22-ab77-02051dd34551 | textbox | Drawing Reference and Revision Number:
c00896fd-5f9c-5909-986f-f9a6ce5e15b5 | note | Is the Pipe hanger type as per the install drawing?
bb9eeb96-0671-5a4f-be87-12afe9faaa08 | note | Are Hanger fixings as per the install drawing?
f40b3f75-3561-58ee-a2c9-2fc6c84dae8c | button | Are hangers spaced correctly? (not exceeding minimum spacing) | Yes, No
ebd289da-a4a8-5a61-bc79-c53be2b8cd74 | note | Add Photo
48088cfd-51cf-49dd-a8f2-8a2ea1a64e52 | checkpoint | 3. CHECK GROOVES DEPTHS
26478549-7dc9-5116-9b35-6fadb30d9c57 | note | CIBSE W5.2 State of the System
07785411-51b1-5941-b774-21c522698c69 | note | AS2118.1-2017 - Section 7.1
67e20c95-bd3e-5aa6-9eef-3f30cbaebbe8 | note | Are groove depths within tolerance?
ba5d2d76-6ef2-5923-a4e4-18d3a07340dc | note | Are pipe heights are correct?
143958f1-dc81-5921-9390-eb7043562a21 | button | Have any pipework alterations been approved and recorded for as-instaslled records? | Yes, No
95039819-b7bb-5cbf-a291-cae1e0f7ab72 | note | Add Photo
aceebcdd-5de6-4988-96ed-a91067625c38 | checkpoint | HOLD POINT
46e3f177-f2d4-577b-ae06-c9ccbc85ff8e | button | Confirm Safe to Proceed | Yes, No
43b1a51d-8a82-42b0-a838-dcc5c4ae576a | signoff | GM Fire Sign Off
97afd42e-6810-4b7c-97cf-b108cdf0a7f7 | checkpoint | 4. VICTUALIC COUPLINGS INSTALLED
c54050f4-9a29-5051-949a-cfe84b68f678 | note | AS2118.1-2017 Section 7.10.2.2
a44e8484-c098-5b14-b821-d3adaf014416 | note | CIBSE W5.2 State of the System
fce3854d-b33c-5195-bac0-59af80c7f0a3 | button | Have ONLY Victaulic brand couplings been used? | Yes, No
5a0c4326-aec4-5508-a52d-38d1857d5f0a | note | Add Photo
f8de08d4-6408-45a2-9511-aea20cedd546 | checkpoint | 5. CONCEALED SPACE SPRINKLER HEADS
eee3f026-cdef-56d3-9483-b396bc7ddd3d | note | CIBSE W5.2 State of the System
80633ecc-9758-5f92-9bb1-2ef38510b53e | textbox | Drawing Reference and Revision Number:
626a8e96-996f-5327-bc73-86a4ea08367a | note | Have ALL concealed space sprinklers been installed as per dimensioned install drawing?
c30fbdb8-8be8-586f-a976-508e4bdb0cce | button | Have the correct sprinkler types and temperatures been used? | Yes, No
ee98a821-4b7d-52bc-84ee-c20b08c0a0c9 | note | Add Photo
ad600b8d-1bb9-4e30-be93-e0d2050fc71e | checkpoint | 6. EXPOSED SPRINKLER HEADS
6a96b0a8-0f9a-5abb-b824-d846f68dfa4a | note | CIBSE W5.2 State of the System
bd865a88-3aec-58ee-9043-3ffe41034986 | note | AS2118.1-2017 - Section 5
b0462861-86c3-5c63-b05f-7126b6b6d2e7 | textbox | Drawing Reference and Revision Number:
adce8c38-7f02-5ebb-9031-860f4a26db0a | note | Are exposed sprinkler heads installed as per dimensioned install drawing?
82c5582c-629d-52a9-bfb1-fb213a493ce6 | note | Are sprinklers clear of obstructions?
bb1b7157-4265-5e9e-8807-e6b34a3260fb | note | Have the correct sprinkler types and temperatures been used?
1f40998c-0832-5ca9-a4e8-6b6fed97dea5 | note | Confirm sprinklers do not exceed the maximum distance from the soffit?
f94ef75c-ecad-575e-ab78-e5f15b0e4cd8 | button | Have sprinkler guards been fitted where risk of damage exists? | Yes, No
70b48cd6-01fd-50a1-a853-7b7f462b9ee2 | note | Add Photo
b764e2c4-3406-4762-ba13-d5e581cef345 | checkpoint | 7. FLEXIBLE DROPPERS
b55edcb5-0252-55b7-a907-6c3ccc8568bd | note | CIBSE W5.2 State of the System
a4db1d26-d664-58dc-b2c3-3e06dff57a54 | note | AS2118.1-2017 – Section 7.6
3d8f9910-7703-5658-bbf1-258956d07ebe | textbox | Drawing Reference and Revision Number:
63055443-d63b-5ae8-a8ba-cfb49218e04c | note | Is flexible dropper installed in correct location?
153c6525-c6a4-515b-85ff-644a661b2e6f | note | Correct sprinkler type and temperature?
d01c28ff-22f2-5f9e-90e3-4d9fc1473814 | button | Is there sufficient length to reach on-ceiling location? | Yes, No
1d065d27-5894-5633-8015-f68cead04869 | note | Add Photo
efe88da6-16a4-4a55-aa64-1ac4049c8362 | checkpoint | 8. SPRINKLER INTERFACES - VALVES, & MONITOR SWITCHES
195dd91e-8eb7-5ee0-9a70-5f0edb47f0df | note | CIBSE W5.2 State of the System
e6f12339-b9d6-550a-9058-46d8eca315d1 | note | AS2118.1-2017 – Section 8.13.5
e853e74a-e9f5-5ad2-9f10-bd733ba3001e | textbox | Drawing Reference and Revision Number:
4a4f03e7-67a2-5b51-ab56-2b988c3a7db7 | note | Have Isolate valves & flow switches been installed?
06fc9e6c-1989-5f7c-81c0-d5fc0831531d | button | Have labels been installed? | Yes, No
709ddf1d-c9a4-5ae3-9bfb-a39238aaccc0 | note | Add Photo
f8001fdb-38a3-43c3-ad8e-0203ec90a75a | checkpoint | 9. REMOTE TEST DRAIN
82f28b2d-f541-56c6-bea9-0fad952588f1 | note | CIBSE W5.2 State of the System
f288c8e8-5255-5e53-a1b5-2745bf71c866 | note | AS2118.1-2017-Section 8.14
4e0898e7-c1d6-5f58-bdda-d6c7df19bd2d | textbox | Drawing Reference and Revision Number:
4138a00e-ae1c-5a02-9ef1-e98c21ebdc9e | note | Is the Remote test valve installed as per dimensioned install drawing?
1963e6f9-5359-516e-a157-28172089ceb8 | button | Restricted orifice installed? | Yes, No
feeb3030-5eac-53c4-98d1-d77179c7d695 | button | Have labels been installed? | Yes, No
423d55a0-7f4e-52a3-803e-1df2dc01e69a | note | Add Photo
7915c8f7-6e37-438e-bd2c-c3b985140c7d | checkpoint | 10. SEISMIC
86561ef8-732c-5364-9450-3e98fc081f3c | note | CIBSE W5.2 State of the System
24383946-2192-589e-a5ba-fc1dc6fefb2d | note | AS1170.4-2007 (R2018), clause 5.4.6 and section 8. AS1170.0-2002, AS5216-2018 & ETAG 001 PART 6, ANNEX 1.
f76f45e2-dca9-5343-b33b-2fbae8e3d83c | textbox | Drawing Reference and Revision Number:
bc2a155b-6a57-5c10-9d4f-94ebfb0f80f3 | button | Are Seismic braces installed in accordance with Engineered drawing(s)? | Yes, No
adc4559b-741d-5b71-85e7-4e4e18be3e9f | note | Add Photo
62bf3167-7ce3-570e-9696-66939e8d1e80 | note | CIBSE W5.2 State of the System
b419edea-9b68-59b3-8b04-d69970ec2468 | note | AS2118.1-2017 Section 7.9.6
69f4374f-8647-5ca3-bb7d-a04e04e1adc3 | note | Has painted pipe been inspected for damage?
49943a5e-8d3b-5d07-97ed-89e3f3866c4c | button | Have Repairs to paint been completed where required? | Yes, No
18f1b288-353a-5237-8c5e-16978da92e5f | note | Add Photo
ef5785ec-55c0-4fd6-8bd1-cfcc2fb6be5c | checkpoint-no-value | GM Fire Sign Off
7d62e40d-a352-4ba5-826f-d951f3b5d1cf | signoff | GM Fire Sign Off
49d2ec49-bbbb-448c-a779-7b1aa7db5861 | checkpoint-no-value | Principal Contractor Sign Off
b070821a-626a-4875-8167-8069a9fe9904 | signoff | Principal Contractor Sign Off
1b75d496-6f49-49c3-be45-9a8e10a59107 | checkpoint-no-value | Consultant Sign Off
8b066685-4ef2-4f9b-97a2-5aba98f9aaca | signoff | Consultant Sign Off
acabee75-224a-43a3-9a58-b17ee005c075 | checklist | ITPS-107 Hydrant Pipework Rough In |  | ITPS-107 Hydrant Pipework Rough In
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
7df397ab-7393-4132-9ebb-1620a4a459b9 | checkpoint | 1. PIPE LOCATION, HEIGHT & SIZE
6c833c56-e40d-5dd6-ba21-7d465263773f | note | CIBSE W5.2 State of the System
e2096094-2fbb-583f-87fb-d1ca2eb5f9b2 | note | AS2419-2005 Section 2
f51d6ff6-2209-591f-a7e4-0f4a43154699 | textbox | Drawing Reference and Revision Number:
697af167-4c7e-534f-9e05-4d39727f3d07 | note | Is pipework setout as per dimensioned install drawing?
0ad07d32-239a-58dd-8477-f2d2cc52b6c8 | note | Are pipe heights correct?
ad06fa2a-68ba-55f1-96b5-0d2e6230f0d9 | button | Have pipework alterations been approved and recorded for as-installed records? | Yes, No
776add20-d8e2-5822-aa29-15e667524796 | note | Add Photo
3a908283-ede0-469d-aafb-f80c269e1f7d | checkpoint | 2. PIPE HANGERS
8601b4c5-d41d-5f65-9d0f-dc724e3278a3 | note | CIBSE W5.2 State of the System
b6b0acc4-afae-5099-8a3c-f2020459007b | note | AS2419-2005 Section 8.7
40aa6925-3802-517e-8a05-dbbfb0060137 | textbox | Drawing Reference and Revision Number:
75829282-4ea6-53da-9466-abc2b80108d9 | note | Is the Pipe hanger type as per the install drawing?
7d167a28-56cc-5636-a6d5-4a91d741802f | note | Are Hanger fixings as per the install drawing?
d47f09e5-9234-56f3-a698-cb61e9d674d3 | button | Are hangers spaced correctly? (not exceeding minimum spacing) | Yes, No
96d5a002-f6e6-5b01-b6c3-6f00f92b6647 | note | Add Photo
48c53723-593a-4937-8851-756d5d629c85 | checkpoint | 3. CHECK GROOVES DEPTHS
7437aeda-5aa2-5dfb-83e6-f83a5f263389 | note | CIBSE W5.2 State of the System
30981747-ff5c-5f0c-8f21-2756a04305a2 | note | AS2419-2005 Section 8
21d55615-4ccb-590f-9120-7c590e7ec9ad | note | Has Victaulic Groove Tape been used?
d3ebc28f-ec92-589a-a20b-517370d0daf5 | note | Are Groove depths are within tolerance?
0b47094e-7998-5c6e-be7c-7ef20803188a | note | Are Pipe heights correct?
3ac031f6-15b0-5572-ac1c-9f417488ba3c | button | Have Pipework alterations been approved and recorded for as-installed records? | Yes, No
9b580644-30d2-585c-9a66-3ac41df9c953 | note | Add Photo
51d53289-df2f-4489-a7f3-37f7dc6e3427 | checkpoint | HOLD POINT
10b3a20a-ed79-53ce-a83e-784c45ead8cf | button | Confirm Safe to Proceed | Yes, No
f5036e79-125b-4263-af31-c231f9d671d5 | signoff | GM Fire Sign Off
ad8c1445-32c7-4efe-92e0-2a7abee0692f | checkpoint | 4. VICTUALIC COUPLINGS INSTALLED
e71a2c46-d7ba-50fc-acd8-bd0af68f80ff | note | CIBSE W5.2 State of the System
758951e6-3ec1-538b-8188-31d5ddb035b3 | note | AS2419-2005 Section 8.3.2
c769292a-0cda-5ae9-ae8d-ba5a810236ca | button | Are Victaulic brand couplings the only couplings that have been used? | Yes, No
8920b1e4-52ed-53f5-a13e-1e3922d49375 | note | Add Photo
bf05d845-72e5-40bb-b881-c314e5dfb7c7 | checkpoint | 5. ISOLATION VALVES INSTALLED
ad51a80a-cc06-5788-b096-c9976bbf0e0a | note | CIBSE W5.2 State of the System
b692fbe1-e78f-52db-a91f-56d16a484dce | note | AS2419-2005 Section 8.5.8
1f8db4dc-2e8c-5bf2-824a-66ff7e204d04 | textbox | Drawing Reference and Revision Number:
26b0e7bf-1537-52d8-a318-0d434cf5b534 | button | Are Isolation valves installed as per install drawing? | Yes, No
d058b68a-b74a-5790-8c19-1543b2d80f52 | note | Add Photo
01d8738d-a54f-4526-98db-e50dc4c8d1f2 | checkpoint | 6. SEISMIC
3b759eb2-a24e-50a4-9807-cc7cac239b8c | note | CIBSE W5.2 State of the System
99b24e9f-f806-502b-b636-199dd6148e00 | note | AS1170.4-2007 (R2018), clause 5.4.6 and section 8. AS1170.0-2002, AS5216-2018 & ETAG 001 PART 6, ANNEX 1.
93c5a4b2-22de-53be-be19-95fd2bff91f3 | textbox | Drawing Reference and Revision Number:
294d066e-24ae-5962-9b07-45a999e06903 | button | Are Seismic braces installed in accordance with engineered drawing? | Yes, No
94180e95-f634-520b-81f7-44a9a5cce711 | note | Add Photo
b2dbd8b5-bbe2-4961-951e-7228ed87e287 | checkpoint | 7. CLEARANCES
67d7f392-ff54-537c-9943-cd29aa58c67a | note | CIBSE W5.2 State of the System
a09a01cd-1aa7-5ff9-bac0-33e45ac754a1 | note | AS2419.1-2005 – Section 3.2
54fc32cb-d9e2-58b0-90c7-37fca454ca6b | button | Is the Hydrant positioned so it does not obstruct required clearance for egress path? | Yes, No
4d1f5b47-238c-5572-8c76-16231deb0f57 | note | Add Photo
29fc3da2-626f-467b-94a1-65b291db1f4a | checkpoint | 8. LANDING VALVE FIT OFF (CLEARANCE HEIGHT/ ANGLE)
eec22d5d-be0c-5b15-b771-de103f368693 | note | CIBSE W5.2 State of the System
2a6266b9-e8b5-5503-8dee-5964edd986cc | note | AS2419-2005 Section 3.5
ac2b9477-11d4-502d-b286-f4480d10145d | note | Have you checked:
59e83a9c-00c9-54ee-b435-fdb87cb61035 | note | Landing valve height; and
50e88d77-feea-5769-91c1-04dd86a01235 | note | Landing valve is at the correct angle; and
3abe7c38-e48d-5dd9-8f4e-a7816cdfe9dc | note | Coupling angle and orientation is correct; and
e58c48a1-9cfc-554d-9b83-df6faeafe9f7 | note | Required clearance for the handwheel has been maintained; and
86ede15b-401e-54d2-bd58-a7f8c6354c93 | button | The required clearance for the nozzle has been maintained? | Yes, No
7786a9b9-0cfb-5e73-88cc-06cfdf41fb00 | note | Add Photo
535e231b-0dae-40c2-8c59-968dcdf1c55f | checkpoint-no-value | GM Fire Sign Off
0cf28e79-32ca-4fe3-b3d6-ab210a9248ed | signoff | GM Fire Sign Off
492cf08c-4640-4680-bfd6-9426715395cd | checkpoint-no-value | Principal Contractor Sign Off
b40888fa-922c-430d-8b96-746566265405 | signoff | Principal Contractor Sign Off
6ab15962-2b1b-405c-ae9b-0bed94e2fbec | checkpoint-no-value | Consultant Sign Off
bc0d71e4-c6fe-439b-9f41-2fb9b4a860f4 | signoff | Consultant Sign Off
1573ef5b-cca4-4747-835f-ce2f3e514293 | checklist | ITPS-108 Sprinkler Fit Off |  | ITPS-108 Sprinkler Fit Off
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
232e5f65-3a75-4602-8362-fc2945dfd354 | checkpoint | 1. SPRINKLER LOCATION
b3fa6360-be97-582d-a301-832e127e874a | note | CIBSE W5.2 State of the System
a1be2813-8e6f-586a-809d-e0550cc527f7 | note | AS2118.1-2017
da9dbf1f-d763-554d-94ef-3c7c46d7b8bb | textbox | Drawing Reference and Revision Number:
d9277144-5c81-5d1f-9f19-5a3ace73baaa | note | Is the location as per dimensioned reflected on the ceiling plan/ install plan?
0477bc7e-8434-524f-8519-b79a9aadce12 | note | Are the Sprinkler temperatures and finishes appropriate for the environment?
b18f6bff-9793-5554-bc4a-cacaa97d1ff8 | note | Maximum spacing from walls is not exceeded
170ab3d1-a8fc-5ab8-9a91-b4ca1b3b5bf0 | note | Is the wall spacing within requirements?
d2b09d16-e1ea-5faf-bae6-b0f2f6fa3cab | button | Is the spacing between sprinklers within requirements? | Yes, No
43ce98ce-3e3c-5509-9e14-e732d7ffb6b4 | note | Add Photo
aec0a882-8f0e-4619-9c2f-1bf6c4a7d099 | checkpoint | 2. SOLID SPRINKLER DROPPERS
7648243b-cd08-5240-b4c7-4c9f3941d3f0 | note | CIBSE W5.2 State of the System
c96f0353-9e39-5df2-b58a-5a699d21ec6c | note | Is the arm piece supported by hangers?
075b0891-8f4d-5fa1-938c-de43d16ea4bf | note | Is Dropper square?
a340dcf0-5e73-5301-9af5-328aef531b6c | button | Is the finished sprinkler height compliant? | Yes, No
a519aff2-af40-56ce-b56e-220887f7e565 | note | Add Photo
e1f590e7-690e-4ee6-887b-7e497d11b990 | checkpoint | 3. FLEXIBLE SPRINKLER DROPPERS
a9191999-d93f-56a3-b67c-27d47249a1d7 | note | CIBSE W5.2 State of the System
7661ddb0-2369-5209-9cff-d2b10c731d37 | textbox | AS2118.1-2017
877640c7-43e0-5745-8cd0-58e50b8133bf | note | Has the appropriate lengthed dropper been used?
63b955ad-f4c7-556f-919a-362c2e2cebad | note | Are Sweeping bends within tolerances?
4e425356-d9ef-56e7-92d3-dc2a27533d9f | note | Was the correct bracket used to secure nozzle?
945ba60d-8e40-5c82-aeb6-7e00cd67775b | button | Is the finished height compliant? | Yes, No
d82652e1-7259-5752-b21d-d0e3590ea22a | note | Add Photo
42bbcc8f-e535-491b-b8d4-cbdef773597e | checkpoint | 4. OBSTRUCTIONS
2eaba71c-6725-57d8-9f4f-c184198de600 | note | CIBSE W5.2 State of the System
3b5c936a-4c0a-59d0-b004-abef5bdb0bab | note | AS2118.1-2017
002c87a6-e5a6-54b2-8f6b-302ec8b9c135 | note | Has minimum clearance been maintained for 'On Ceiling' obstructions?
347429d7-4449-581a-8248-3c499b6f6be0 | button | Has minimum clearance from sprinkler been maintained for 'Below Ceiling' obstructions? | Yes, No
e3a8bc07-76f6-5b53-9cd2-be81950ef8ba | note | Add Photo
89d4b820-4387-4877-af10-7fc22223f68c | checkpoint | 5. ESCUTCHEON PLATES
f8cd3802-45d4-595c-bf38-6f0a911237b2 | note | CIBSE W5.2 State of the System
c292c61e-492c-574f-8fae-2a2d6d3ac772 | note | AS2118.1-2017
9592726e-7012-5d90-9380-66bab2176181 | note | Have outer escutcheon plates been fitted?
be64be58-eb60-5e69-9f21-89fab70cc225 | button | Is surrounding ceiling clean? | Yes, No
aa5bce25-3b99-5110-b127-e017acce5b02 | note | Add Photo
5db880e5-47b8-4bd4-82f6-b0f63aefd4f1 | checkpoint-no-value | GM Fire Sign Off
50bbb680-3efa-47bb-9994-62dd56cda987 | signoff | GM Fire Sign Off
234ea422-90ea-4dc6-a7cb-816c79e887dc | checkpoint-no-value | Principal Contractor Sign Off
604c23bb-7e92-45f6-a189-3697cbf686a4 | signoff | Principal Contractor Sign Off
00aa089c-7edd-4e95-b843-8cd023fe5bed | checkpoint-no-value | Consultant Sign Off
e9017937-7326-43a9-b870-b39dd39417cc | signoff | Consultant Sign Off
a31c9755-65cc-4268-8804-7517870a6bd6 | checklist | ITPS-109 Portables Fit off |  | ITPS-109 Portables Fit off
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
5cbd0af6-4a25-4ec7-8e63-64eb705efc9a | checkpoint | 1. FIRE EXTINGUISHERS - GENERAL LOCATION
1d9e9598-ba84-599e-800e-5fbd27e44758 | note | CIBSE C5.2.2 Set Points
2298e01c-af62-53ed-b65c-1fe050cb342e | note | AS2444-2001 - Section 3.2 states extinguishers shall not be located in positions where access could present a hazard to the potential user.
a2dcbbfd-7a1c-52ae-bd89-72f88a006c51 | note | Is each extinguisher located in a conspicuous and readily accessible position?
b8f90cfe-5d9d-5210-91c9-524b57d3e6c6 | button | Where practicable, are extinguishers located along normal paths of travel and near exits? | Yes, No
8e8e58c9-e69c-5905-9686-9e2047275cf9 | note | Add Photo
d6a5fa7d-d83d-4c19-9fd4-94a14c55f1ab | checkpoint | 2. FIRE EXTINGUISHERS - MOUNTING DETAILS
92d65257-2d17-51a5-a0e1-3d107f601b6d | note | CIBSE C5.2.2 Set Points
7e4a91ea-4911-5083-bec9-a954573331d1 | note | AS2444-2001 - Figure 3.2
98c4fc3c-064c-5968-b9d1-7b361a38a5fa | note | Have Location Signs been installed at a Minimum of 2000mm off the FFL?
a84f94cc-4090-5d47-a896-66a749846bcc | note | Are extinguishers installed at a maximum of 1200mm to the top most part of the extinguisher?
6b1866d2-7ee3-5c69-9335-4365f98b6e59 | button | Are extinguishers installed at a minimum of 100mm from the FFL to the bottom most part of the extinguisher? | Yes, No
5f380176-d32b-5f3a-82b1-b1a61d08948a | note | Add Photo
7b34f162-6e68-4ecb-b244-d35bbddb2698 | checkpoint | 3. FIRE EXTINGUISHERS - VISABILITY & SIGNAGE
695355f5-e142-5690-a0f9-efe767ca8072 | note | CIBSE C5.2.2 Set Points
205d9d93-3c1f-50f4-ab77-7dcdecae4567 | note | AS2444-2001 -Section 3.4
6d303978-f2cc-53fc-955c-bbc99f8fcf86 | note | Are extinguishers, or extinguisher location signs, visible from a distance up to 20m in all directions?
a7811976-f994-58a9-91f8-0163b197fe5b | button | Are the location and type of extinguisher signs installed as required? | Yes, No
76407db0-aef1-51f6-81c7-4b9dca537e95 | note | Add Photo
c92504e4-5749-49dd-958b-9849ac358a23 | checkpoint | 4. FIRE BLANKETS - GENERAL LOCATION
8c86fb0e-1f1a-5bd6-98c1-c5707ee49d1e | note | CIBSE C5.2.2 Set Points
41d5a29c-0c51-5bb3-bc69-cd163cb6a87f | note | AS2444-2001 - Section 6
dd190606-abcd-59a6-bd2e-d43d0a7fbd76 | button | Are Fire Blankets installed in a readily accessible position, and not in a location where access could present a hazard to the potential user? | Yes, No
0d049b97-cc44-5e2d-8106-ad61be052e5a | note | Add Photo
2f796755-4f09-4816-8ffe-9f6adf6a4e08 | checkpoint | 5. FIRE BLANKETS - MOUNTING DETAILS
4d653bbc-eca5-5330-8cc4-929eee92d98b | note | CIBSE C5.2.2 Set Points
e17dc16e-e3be-52eb-a134-80a080e022bd | note | AS2444-2001 - Section 6
c16e2b82-720b-5424-9ad8-4fbca92bf72f | note | Have Fire Blankets been mounted to withstand the loads imposed when removing the fire blanket from its container?
d518129e-11b2-5358-bab7-06377c5fb77c | button | Is there sufficient room so that fire blankets can be quickly removed without impedance from nearby obstructions? | Yes, No
6714b0c5-5af0-568f-b0aa-44affae80b6c | note | Add Photo
054b5650-59b6-4a72-93f3-c877e1f4bbf8 | checkpoint | 6. FIRE BLANKETS - SIGNAGE
4eee0aef-1c5c-5023-9fec-3fdf8fe12ec2 | note | CIBSE C5.2.2 Set Points
340a9475-af30-5558-bbb8-12d7ade5ecbd | note | AS2444-2001 - Section 6
38fc0663-9b6b-5de8-8a1f-1a8806bd4746 | note | Are signs located above or adjacent to fire blankets?
a3925e17-1f85-53d5-8d35-0c8fd18c0955 | button | Are signs 2.0m above floor, or at a height that makes them most apparent to the average person? | Yes, No
c60fef89-8eae-5a45-8be0-a5efa8ba06ed | note | Add Photo
c1ac0bbe-8094-415e-84c3-d0fd3bd75dcb | checkpoint-no-value | GM Fire Sign Off
23a64104-9cdb-48ea-aff0-a95763ef58b2 | signoff | GM Fire Sign Off
f6c41aa6-dcc6-4380-b5fd-e955f8c0b5f1 | checkpoint-no-value | Principal Contractor Sign Off
a3a44376-805c-4ff7-8d48-2d68eff4dc6b | signoff | Principal Contractor Sign Off
52939220-a320-4b5d-a61d-27fa694c7e05 | checkpoint-no-value | Consultant Sign Off
cbe264ce-04f2-4608-b6a1-5dc621e5584f | signoff | Consultant Sign Off
f30543cd-e08d-4b1a-9ce7-44f6c3dbe52d | checklist | ITPS-110 Valve Set Installation & Fit Off |  | ITPS-110 Valve Set Installation & Fit Off
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
cb0b2a55-b669-40d2-b83b-92991409c396 | checkpoint | 1. UNDERGROUND SUPPLY
ab6d053c-b0fa-5e44-9e81-9fcf576d767b | note | CIBSE W5.5.2 Flushing Procedure
3bde4fba-aabc-529e-ac57-8d191b80a6d6 | note | AS2118.1-2017 - Section 7.9.7
3065cb38-4da9-5972-b0df-49cf0ce1de4f | button | Has all supply pipework has been flushed by a hydraulic contractor? | Yes, No
6c1870e1-87f0-59c9-a066-5f31dd3243a4 | note | Add Photos
c7874098-8f90-4301-82fc-598b7f3df027 | checkpoint | 2. CHECK GROOVES DEPTHS
0d6b0d0c-7256-503b-94ca-556e1ce8418b | note | CIBSE W5.2 State of the System
9e298ec2-0c42-514f-a49f-3a1a3470bd67 | note | AS2118.1-2017 - SPRINKLERS: Section 7.1 | Yes, No
6d0d4f9f-50a4-56dd-8c68-9609f1a7b762 | note | Has Victaulic Groove Tape been used?
71c9e612-3a51-5830-8622-579b68589a3d | note | Are Groove depths are within tolerance?
7d4f1940-7abb-531c-8b86-9031037fde94 | note | Are Pipe heights correct?
1d487a78-b1ab-54b0-8001-b10bb0cf6415 | button | Have Pipework alterations been approved and recorded for as-installed records? | Yes, No
da1c6a42-77e2-5c2e-aac5-df35af1895c1 | note | Add Photo
f7e70c97-40bb-45aa-a3cb-0d663f353414 | checkpoint | HOLD POINT
2e901a6f-b9a0-5050-84a0-8a5c207ac123 | button | Confirm Safe to Proceed | Yes, No
8df0412f-17d5-47d5-9311-a7e64907000a | signoff | GM Fire Sign Off
2002d3b5-f549-4fd5-968f-b9f0a97f8a1d | checkpoint | 3. VICTUALIC COUPLINGS INSTALLED
13d26cad-3876-57ea-a566-64c3c9497a78 | note | CIBSE W5.2 State of the System
ea6feb13-c869-5feb-8e4e-efee3c5490ac | note | AS2419-2005 Section 8.3.2
946f089b-ca81-5bfd-9a6e-49803b21d7a2 | button | Are Victaulic brand couplings the only couplings that have been used? | Yes, No
edaaa0c7-cafd-5fe7-926e-664377f131a9 | note | Add Photo
16947bf1-cec9-4a4c-b3f2-9dc6bcc2fc91 | checkpoint | 4. CONTROL VALVE ASSEMBLY
1f0b8473-7e85-58f4-8223-9dfde076548a | note | CIBSE W5.2 State of the System
17cc2f3a-ebaa-58ae-95e2-d119b4dd74b3 | note | AS2118.1-2017 - Section 8.1
d8e77838-38c3-5d7f-91be-47204d8435a5 | textbox | Drawing Reference and Revision Number:
981a89bf-a4c6-5252-a031-8ecdd140fed3 | button | Is the assembly is installed as per drawing? | Yes, No
afa398e5-37de-5849-9134-6dee55707190 | note | Add Photo
8006412e-c430-4e6c-b0db-d31becf651ac | checkpoint | 5. PIPE SUPPORT
f25464f9-6310-5e25-b03c-4621b10b0c7d | note | CIBSE W5.2 State of the System
dfd3fd6b-7ccc-5f1c-9fb0-142cdd7b4af4 | note | AS2118.1-2017 - Section 7.8
f2567ae8-b9e7-51bc-8027-ea6cfe334789 | note | Are pipework supports as per drawing?
a2bc9ebf-bec4-538a-af00-1470c90bd942 | note | Are the supports capable of supporting assembly weight?
8b8deb25-0710-5d3d-bcb2-f710678a3545 | button | Are the supports capable of withstanding forces during operation? | Yes, No
1e1b48db-174d-5960-9b69-a304cd7ecf18 | note | Add Photo
a677943a-f22d-46d7-a17c-9c62e06e7ff4 | checkpoint | 6. VALVES
652bd2ca-6c37-5d3a-8af3-7fde62f0003f | note | CIBSE W5.6.2 Mechanical Checks: Automatic Control Valves
cb6f0cd7-ee29-5fc9-ad2d-2f4b43936278 | note | AS2118.1-2017 – Section 8
3de6fcf9-b550-52d9-916c-d4cb8f3b2766 | note | Are Valves installed as per drawing?
b0ef41e6-4eab-5dc9-b37d-097b3619d606 | note | Are valves are installed in the correct orientation?
9617883d-1ce1-5016-9fed-e1c664e0937b | button | Does the clearance allow for manual operation and future maintenance requirements? | Yes, No
aeedc7cd-791b-5aac-ba98-648d689745e4 | note | Add Photo
a669086f-3449-4ee3-85da-96efcabae149 | checkpoint | 7. INTERFACES
2a303ad4-1a02-5eba-ab14-6d9050a21a10 | note | CIBSE W5.6.2 Mechanical Checks: Automatic Control Valves
8946c354-f5da-5084-a3f6-a04da30f3a8a | note | AS2118.1-2017 – Appendix H
1f9d7841-1728-5f93-9afe-b9c3a32d0158 | note | Are valves/switches installed for connection by other trades?
d9e9e66f-2139-55bd-a9e1-eecd3cfc7add | button | Have clearances been provided for connection? | Yes, No
805db500-bb42-506d-9ecd-f53c6a921085 | note | Add Photo
e14ab540-5afa-4a96-8ec3-1ee44fdc805b | checkpoint | 8. PAINT / FINISH
2e8e466f-3c41-54c2-ab19-6099995f4b87 | note | CIBSE W5.2 State of the System
dcb4c57e-45e3-508c-a946-a76cce6dc0bf | note | AS2118.1-2017 Section 7.9.6
8de4baea-b103-5f51-bc1e-b74510d46f92 | note | Are exposed mild steel pipes painted gloss red (unless specified another colour or galvanised pipe)?
cbf92ae5-8775-512c-8cb6-83be0b00c502 | button | Have threads been de-hemped and tidied? | Yes, No
760ad170-25d1-5b8a-a072-33be8ac892a6 | note | Add Photo
ceaa4b57-0e88-5a6b-86ad-aa63f3c3343d | note | Add Photo
1b861279-a2b5-4641-9a6d-24007ae4e476 | checkpoint | 9. SECURING VALVES
32021c4c-5b1a-5aec-bdec-d61ee001ba0f | note | CIBSE W5.2 State of the System
3420aa67-5fdb-584e-a408-ced13fd33646 | note | AS2118.1-2017 – Section 8
4d7b98ac-ec2b-5136-a50e-17e4218c0dac | note | Are valves secured by 003 locks?
a25d5d0e-9da7-5cfc-937b-b081481cc201 | button | Have straps and chain been installed? | Yes, No
b978e165-2f7f-5404-9075-f4d57dffc26a | note | Add Photo
d1f61246-d7b2-4557-85f3-c6a0b2654444 | checkpoint | 9. SECURING VALVES
4f5df6d4-5ef2-5d20-9b10-cefb7af51736 | note | CIBSE W5.2 State of the System
e4aaac1d-734c-57c8-9aaf-9c02b509db21 | note | AS2118.1-2017 – Section 8
e4182899-5a63-5d9d-adfa-ea7345a8d928 | note | Are valves secured by 003 locks?
34f62a9c-cc8c-5b26-8a37-fa66b0623bbd | button | Have straps and chain been installed? | Yes, No
da95329b-cbe8-5d9e-8e45-cc8d43681e4c | note | Add Photo
49bcdbf5-c063-4a84-8817-7c324bb46540 | checkpoint | 10. LABELS & SIGNAGE
00c56d6e-c6d4-567d-bfa2-6aebe69f109c | note | CIBSE W5.2 State of the System
fe6038f9-3cd6-50f2-a9d2-8b36816d5bd9 | note | AS2118.1-2017 - Section 3 (3.3.4)
ed896abd-ef3e-5c4b-8c76-1b32ead19959 | note | Are Equipment name labels secured?
d2e5d792-38e3-5721-9365-f99d9566da15 | note | Are Valve position labels secured (normally open / normally closed)?
cf88ef6c-aa24-573c-a90f-14cc5e6c3682 | note | Have "Sprinkler Stop Valve Inside" signs been fixed at the valve set enclosure entry?
4f45604f-deba-566c-b042-406cbe3eb7ad | button | Has the Sprinkler Block Plan been installed? | Yes, No
55c1e66c-e57f-5c56-93d2-66d25e2b0b22 | note | Add Photo
8db290c8-e1ca-478f-9f90-edff6a378bbf | checkpoint | 11. SPARES
8e03ec0c-809f-5cf8-b931-1201e269e6fe | note | CIBSE W5.2 State of the System
0ff80e02-de48-566f-be19-750b7739161e | note | AS2118.1-2017 – Section 6.7
83a84e4d-1441-5915-a578-69ab1cb8e96a | note | Has the correct size sprinkler spares box been installed?
d2f7d0e6-1cb7-5c5c-86a6-05f6adc3edd4 | note | Have the correct number of sprinklers been provided?
e8fd257e-0a74-579e-930f-d287f2ad829d | button | Has a sprinkler spanner been provided? | Yes, No
fef79b04-8e05-566f-b7ee-fad4275d8cc7 | note | Add Photo
89d05ec9-9854-4acf-a988-f4ec7a9f8409 | checkpoint-no-value | GM Fire Sign Off
dc5d3828-04b6-4f3d-a9f5-aa71059fb102 | signoff | GM Fire Sign Off
3b357797-42e9-4ad7-855a-f90c0007a4a0 | checkpoint-no-value | Principal Contractor Sign Off
8a23e1d2-ea33-4cb0-9ba0-543df86d7cc9 | signoff | Principal Contractor Sign Off
40cc2133-74dc-4fe8-90d2-5c843d81a132 | checkpoint-no-value | Consultant Sign Off
4463092b-5891-4aeb-b29e-b50c5fba1ec7 | signoff | Consultant Sign Off
ce0e680e-92c0-4717-8391-8fe8d25826ec | checklist | ITPS-111 Tank Installation |  | ITPS-111 Tank Installation
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
c2d2ccff-6487-4ecf-aef9-19426fb7bf43 | checkpoint | 1. LOCATION, CLEARANCE, ELEVATIONS
05c2c961-4a11-5626-9dc1-a0ec172915a2 | note | CIBSE W5.5 Pre - Commissioning
824c7dae-a513-5567-89f5-6965e0ffc830 | note | AS2304 - Water Storage Tanks
75cf320d-b365-5c44-8f0a-aa178b474e90 | textbox | Drawing Reference and Revision Number:
a071db8b-7aff-5dd3-9303-a6eccdbbf7c4 | note | Are Structural Elements as per AS2304 – Section 3?
f7bf7f21-540a-573e-97d7-73d6e7d40458 | note | Is the correct Installation drawing onsite?
4ab33404-a85c-5ee8-a5a7-6b665fabb175 | note | Is Ladder selection and orientation as per the submitted design drawings?
21563277-1132-5dbc-8dd7-6b6a66e3c1d2 | note | Is Nozzle selection as per submitted design drawings?
5d5b028e-17fd-5dea-850c-5640e3702316 | note | Has the poisition of the Tanks been confirmed with the Principal Contractor onsite?
4e14aca6-96f0-578a-bd2d-4ab1476e2883 | button | Have you check the subcontractors Competencies and Authority to work? | Yes, No
dba3cac6-5dd8-5734-b0de-e357e44bad86 | note | Add Photo
8c12ccf1-964e-4a72-87a8-9b647d134bb6 | checkpoint | 2. COMMISSIONING
1d39b332-5eea-5ac7-97b9-2ae58aa3375f | note | CIBSE W7.10 Commissioning Certification
d26c1249-240c-5793-a30b-53ab73809495 | note | AS2304 - Water Storage Tanks
060c5624-1bdf-5d85-918f-e35ad2b6ace9 | note | RECORD, CHECK, INSPECT
80df0bf9-8b5f-5510-8882-87016cb126b0 | note | Structural inspection was complete prior to filling; and
5e3ed888-d292-59ed-9222-60235f0f4930 | note | All ladders have been inspected for conformance and clearances and position of tank accessories (AS2304); and
a8367a5c-e0fb-5471-97ee-cc536168d180 | note | Hydrostatic inspection was performed after tank is filled to maximum capacity; and
d578d1ed-658c-5192-a6f5-6bf8a7dce8e8 | note | Any defects have been recorded; and
6a352cda-ea52-5fee-b198-8b7c7f338f67 | button | Have Certificates and warranty periods been submitted? | Yes, No
3ced4027-8c52-56f8-9cd7-693c3e5732e2 | note | Add Photo
758e76f1-9838-4a4f-b01a-c517df7533fd | checkpoint-no-value | GM Fire Sign Off
fd47ee99-0335-4151-b74d-374472e8d2eb | signoff | GM Fire Sign Off
2d87f87f-6638-4914-92f0-7674cdaeefae | checkpoint-no-value | Principal Contractor Sign Off
c1f96e6b-cb60-4829-8de5-2ebcd9692de0 | signoff | Principal Contractor Sign Off
cdc0def8-c427-481c-ab19-df43e77d9dc7 | checkpoint-no-value | Consultant Sign Off
899e9545-6d92-4133-a9fa-8938ded4057a | signoff | Consultant Sign Off
f60653fe-5b21-4e43-b678-20c5ee351735 | checklist | ITPS-112 Deluge Rough In and Fit Off |  | ITPS-112 Deluge Rough In and Fit Off
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
1782a0c8-311c-4c4d-9f9a-946c8ecf9bec | checkpoint | 1. LOCATION - VALVESETS
279b67ef-dad3-549a-9767-0d72161c5329 | note | CIBSE W5.2 State of the System
c76a41b3-cc28-57d0-b7ae-f31186a9d1be | note | AS2118.3
d617e822-1cd2-5ee2-b040-93ab3cd73fcf | textbox | Drawing Reference and Revision Number:
f410fc2b-be42-5538-a3a7-226b33d81d76 | note | CHECK:
1b30f9b8-7fb9-5752-ba0f-7f487ac0b500 | note | Valves located outside building shall be considered protected if the external wall has a FLR of 60/60/60 or be situated at a minimum distance of 10 m from the wall.
1ecf91dc-35a6-598f-9bf8-3b1667fe9094 | note | Valves located inside the building shall be situated at a minimum distance of 10mfrom the perimeter of the protected area.
a7be6079-d19d-570e-826e-c7b4af72aaa9 | note | TRANSIT TIME:
93191d34-2936-5d3f-9046-af70b17d7c9e | note | Deluge valves shall be located as close as practicable to the system they are controlling. This will help ensure that the transit time to the most remote zone is no more than 30 s.
f838ab16-ff66-5f90-9c66-34afe8a8c5bd | note | Add Photo
0a2aadbb-955d-4257-9803-c96bc93fb2ab | checkpoint | 2. LOCATION- DELUGE HEADS
f93c6341-32fc-573e-98ab-1b7753f2684f | note | CIBSE W5.2 State of the System
245d33b4-3f35-5c0b-8fae-7aa3f1a1387c | textbox | Drawing Reference and Revision Number:
af881bda-569e-5f2f-8b7b-8495bfeb6734 | note | Are Deluge heads located as per dimensioned reflected ceiling plan / install plan?
5effacd5-ca51-59d5-af7e-73d947764e68 | note | Confirm sprinkler temperature and finish are appropriate for environment; and
012099ae-8214-5741-acd0-617cb9efed0b | note | Maximum spacing from walls has not been exceeded; and
c9c56975-f4c7-5710-9693-1227aa40ad51 | note | Maximum spacing between sprinklers has not been exceeded; and
d37c96cf-8fb5-5b90-99b3-a903a3bb5d2c | button | All is as per manufacturers detail and FER? | Yes, No
bbe7d05f-5c85-5762-abac-2726fb72e028 | note | Add Photo
e0f0086f-a2bd-4030-ae1e-2999d977b697 | checkpoint | 3. DELUGE HEADS & PIPEWORK
cd44941e-7d6f-54f1-b603-9bde0cbf1848 | note | CIBSE W5.2 State of the System
7e5720c1-03f8-542d-bb84-d364b403876b | note | AS2118.3
67e2c456-7ad6-594d-aeb5-658d2409c983 | note | Open sprinklers are be nominally 15 mm or 20 mm diameter, and either upright spray (SSU) or pendent spray (SSP) pattern only.
0653a69b-c9ea-5708-9ca0-710ae6ceabb7 | note | Deluge system pipe and fittings not normally filled with water or foam solution shall be hot-dipped galvanized.
dae58800-d4fb-53fe-abaa-134adf81377e | textbox | Deluge Sprinkler Head Type:
ce2fce1a-80fe-5227-ba84-76315bc7eee8 | note | Add Photo
dc29286c-3264-4f56-9991-656c4b998b80 | checkpoint | 4. WHERE SPRINKLERS ARE USED AS DETECTORS - SYSTEM PARAMETRES CHECK
8de3a191-5ada-5dce-aa64-beb9e773a189 | note | CIBSE W5.2 State of the System
2cf8c555-52fa-5529-a935-8915aa38393b | note | AS2118.3 Section 2.9
a057e076-66ef-5fad-8b8a-ad8e9e212073 | note | Where sprinklers are used as detectors, ensure the piping layout shall be designed to ensure a response time of no more than 20sec after the operation of the most remote sprinkler or manual operation.
7f1137ba-99a1-543c-8324-fc7713c46a6c | note | Manual control shall be located at each deluge valve and at a strategic point/s within each zone.
a45c2404-a342-5b9d-89ed-f0e01da215de | note | Deluge valve trim shall be in accordance with figures 2 &3 in AS2118.3.
af3e26e5-ffb8-5e5f-9473-8da5b6d49344 | button | Ensure a remote test drain line is installed (close piping deluge systems) | Yes, No
b46748a9-3c1e-5363-8f58-0c654a7dc13c | note | Add Photo
1c6f2144-b569-4a81-8ff5-60fadcf70bae | checkpoint | 5. SOLID SPRINKLER DROPPERS
2553d8b7-32b2-5af1-9f41-0d1d99736850 | note | CIBSE W5.2 State of the System
b1d803a9-3443-5777-b8c9-c09897224c79 | note | Is arm piece supported by hangers?
ccc10ec9-c6ab-549c-b75b-c095fc8a5c7c | note | Is the dropper square?
f82db4e2-bbc4-5a6b-aa86-3afbfc32fc96 | button | Is the finished sprinkler height compliant? | Yes, No
ec558dd8-d196-5889-acae-d659a37bfa54 | note | Add Photo
897c3617-2d4c-4488-bffd-d5530f92a11d | checkpoint | 6. OBSTRUCTIONS
c6e9b458-066e-5907-80af-b4530339a01f | note | CIBSE W5.2 State of the System
e96ea1c9-ce44-5385-9810-af039216ed2f | note | Has minimum clearance been maintained for "On Ceiling" Obstructions?
785bf0ba-740a-571e-a61e-7b80125729a2 | button | Has minimum clearance from the Sprinkler been maintained for "Below Ceiling" Obstructions? | Yes, No
6df25313-1937-4a16-9428-49b37cb90a37 | checkpoint-no-value | GM Fire Sign Off
04c7b3ce-cc86-43f9-b452-88f77c9305c1 | signoff | GM Fire Sign Off
c8f488cd-cd5c-48df-97b7-be714e2f4250 | checkpoint-no-value | Principal Contractor Sign Off
cec3a9d3-c651-4f51-8ed1-3bb53c2518a6 | signoff | Principal Contractor Sign Off
d003c79b-1cab-4e58-8d4a-cddd471124dd | checkpoint-no-value | Consultant Sign Off
1ece2457-224c-4352-9671-2b2d8e98ff6e | signoff | Consultant Sign Off
f87b4bab-e664-4537-8f00-158a9501fd5f | checklist | ITPS-113 In Slab Sprinkler Sleeves |  | ITPS-113 In Slab Sprinkler Sleeves
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
b5bc160b-43d6-4820-97ad-fcf8bc5f7ca0 | checkpoint | 1. TYPE, SIZE, QUANTITY - CHECK
dfeef891-8c46-5592-a017-8edfd680744a | note | CIBSE W5.2 State of the System
eff5517d-ecc6-5d7e-9b99-893e386bc5ae | note | AS2118.1-2017
bbf920cb-6357-5be4-a360-12e3f16a61b6 | button | Are sleeves the correct size, type and quantity to criteria and specified drawings? | Yes, No
e85df1f2-d921-54f7-b968-b6eeb6c9adab | note | Section 9.5.2
6041be90-62cb-5116-9549-4467d15174e1 | note | Has pipe with a minumum DN 25 been used;
5ecaa96d-fc5d-57b3-9fe3-36b0867b44b6 | button | Or where a pipe supplies a single sprinkler protecting an external balcony, canopy or carport, or supplies a single exposure sprinkler, a minimum of DN 20? | Yes, No
6021b5ad-e4da-5bab-adec-695f89261a57 | note | Add Photo
082377f6-0496-4320-a7e2-afd4a1701aae | checkpoint | 2. LOCATION - CHECK
929969c2-6bea-5b6c-a9e6-757658e630cc | note | CIBSE W5.2 State of the System
ddbbed0b-a45a-54c7-9251-e180a4595158 | button | Have sleeves been installed as per specified layout and design criteria? | Yes, No
7b6e74a8-7386-50fe-85fc-20b5152525c9 | note | Add Photo
ecf07362-cd03-467d-9a70-1a6a70f06adf | checkpoint | 3. INSTALLATION - CHECK
aaa221d4-c7c2-58f5-adbf-bb20d2a5687f | note | CIBSE W5.2 State of the System
94977e18-3cd3-56d9-b9b6-74e805ef7ee5 | note | Are sleeves joined correctly and tied in?
8fe28e86-aa09-5a85-b638-3024c8d59254 | note | Have sleeves been checked for damaged?
6899295b-6147-56c8-9b3e-d6872f901f0f | button | Have you ensured sleeves are not resting on form work? | Yes, No
35ddcdd3-5674-5756-aa10-3ff89d6ebf8b | note | Add Photo
2dd058f4-59fb-48b9-916d-88b17ff22ab8 | checkpoint-no-value | GM Fire Sign Off
f699e773-b586-4f9b-83ea-ba874f693ce2 | signoff | GM Fire Sign Off
2e528787-4c32-492f-8d5b-a5166ca8cde5 | checkpoint-no-value | Principal Contractor Sign Off
2b541bb4-b86e-4159-911d-9242254d5ce4 | signoff | Principal Contractor Sign Off
6f36f0c2-458e-4432-a86b-e0c497ce9057 | checkpoint-no-value | Consultant Sign Off
0aa2d6fb-cadc-43dd-bfe3-160a78e6279c | signoff | Consultant Sign Off
99e71d5b-8e9f-4976-b58b-8f036a6dfb06 | checklist | ITPS-114 ASD Rough In |  | ITPS-114 ASD Rough In
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
a511bed8-4cd3-425b-824a-5fefb5bf920b | checkpoint | 1. LOCATION
018d95da-faae-51ac-a201-e4e3af2febef | note | C5.2.2 Set Points
9140e16b-7dd8-588d-9aac-f009faac4fec | note | AS1670.1
ea9d9fdd-6997-55b1-81f4-1f70a59b3152 | note | Have you check that the ASD device does not cover an area great than 2000m2?
504e5030-ce44-5acc-a7a3-2946bafe6798 | note | Is the ASD unit in an accessible location with no obstructions?
8c1f710c-1022-5772-a37c-1b3ff33be31e | button | Is the ASD unit free from damage? | Yes, No
e217988f-14b0-503d-9de6-f3d6e7ab4562 | note | Add Photo
d718d4ac-1086-4a32-a314-e5c8eafb5306 | checkpoint | 2. SAMPLING POINTS
59ec03c0-bc3b-59f9-a72f-ff56f4bac01d | note | C5.6.0 Sensors/Detectors
88b7765b-8b40-5e16-a60c-875d0eea1d9e | note | AS1670.1
a2af129f-271e-5db9-8aa1-ae86ceaabe01 | note | Are ASD points unobstructed, unpainted and free of burrs?
8fedc610-4f6e-5b19-8145-0aa185702a42 | note | Have ASD points been labelled and identified as required?
1d9f39c5-1cb8-5b7d-b2a6-76accdd45ab9 | note | Are ASD points installed in accordance with spacings of point type detectors?
54e6a930-d3ce-5899-8100-cfadfbdf4e7a | button | Have you confirmed ASD points are no more than 600mm below ceiling? | Yes, No
648f2bd7-ee77-53ec-a0e4-4300bd21a65d | note | Add Photo
e80127fb-9139-4423-8b83-569fe4c62cbd | checkpoint | 3. EXHAUST
d27c6be9-9a97-5376-a01f-62eb4e8e8e5a | note | C5.6.0 Sensors/Detectors
0b3aa6f6-6d6f-5eb9-9b07-7a739d23841f | note | AS1670.1
1ad633fd-f1ee-5e44-b5b3-8634cd040bfa | note | If the ASD is mounted outside the protected area and the potential for pressure differentials can occur between the sampled and exhausted air:
c5ba144a-9b13-52b2-a967-2d30aeb2db91 | button | Are the exhaust outlets returning back to the protected area, or as per system design? | Yes, No, N/A
e661245a-d2e3-519b-9b6c-696647f6de4b | note | Add Photo
9e8dabaf-b5db-4bd9-bc99-4a9af951264d | checkpoint | 4. OTHER INSTALLATION REQUIREMENTS
1170e0a6-6b3a-58ee-9b92-0da450f9da20 | note | C5.2.2 Set Points
f595a86c-abe3-5ef6-b75a-e13ccd859893 | note | AS3000, AS1670.1, AS3013, AS/CA S009
a02645ce-ce91-5d59-90b0-6ba47dc21135 | note | Are all sampling points AND capillaries red in colour OR have visible red stripes at least 2mm wide at intervals no more than 2m?
e5cf4551-2c15-5e63-9a4c-28522c507af1 | button | Is the pipe orientated to ensure identification of markings is visible? | Yes, No
8c9ef8c5-0b55-5383-9583-c8ac2d7d87eb | note | Add Photo
8cce3084-7138-435b-96b8-e6d8f6ac3070 | checkpoint | 5. CABLING
64ede16f-6731-56e2-a6ca-6862133ca7a2 | note | C5.4.0 Wiring
2416c99a-1d30-549c-b98c-2998ad40d711 | note | AS1670.1, AS3000
01eca074-9601-5a76-a658-14ab90568b45 | note | Is the cable installed the correct size & type?
367f318b-e1fc-51f4-a610-5d31c420b13d | note | Has cable been secured at regular intervals?
3866b93c-e891-5512-80f2-030564e851f0 | note | Has 24v cabling been installed where required?
a1f0db2b-4966-5565-b918-03539f1deffd | button | Is the power supply in accordance with AS1670.1 Cl 3.15? | Yes, No
ffbc5cac-26ed-56a8-8cd9-adf369243abc | note | Add Photo
6c938257-7669-48c8-9f70-ae4265e9cf55 | checkpoint | 6. PIPE LAYOUT
591d3cb7-6873-553a-bc3a-2b87f4ff241b | note | C5.2.2 Set Points
9f0178a6-bdbf-517a-8268-bc2ebf5c0a07 | note | AS1670.1
8d840cba-8b37-574f-8ee0-7e8f9a4e9903 | textbox | Drawing Reference and Revision Number:
07922c64-61d9-56fd-9eab-052d691cdc81 | note | Is the ASD pipework as per Aspires or Calculations?
80924579-8a9d-5aa5-9703-0941d32fc277 | button | Have you confirmed the pipework layout with measurements? | Yes, No
a0ff1ac4-c3e8-5ff7-90e1-17a3264ab648 | textbox | PROVIDE measurements:
0b165a3a-953e-53de-bd48-eacd33535dc2 | note | Add Photo
c0da0dbd-b6fc-4fc7-8bce-c97194a908e9 | checkpoint-no-value | GM Fire Sign Off
d4eacca9-336c-4b26-8049-0d97d5996891 | signoff | GM Fire Sign Off
a1534f1a-123c-4362-ba4a-2a9f9030cae6 | checkpoint-no-value | Principal Contractor Sign Off
2171e78c-0716-4f1e-9fa1-9ebc1a54dce5 | signoff | Principal Contractor Sign Off
b9100871-dc9a-4a08-afe0-56a8364ea16b | checkpoint-no-value | Consultant Sign Off
6bd68062-8e81-4be8-aa96-9cd5f221001f | signoff | Consultant Sign Off
8b49c949-02c1-4efa-b642-ebf484a4b3ee | checklist | ITPS-200 Fire Detection and Alarm Commissioning |  | ITPS-200 Fire Detection and Alarm Commissioning
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
8e77e6c4-a18d-4ed7-8a6c-673141e91335 | checkpoint | 1. CONDUCT 100% TESTING OF ZONING
0e35d70a-be22-5693-a2ca-5b85af27fae0 | note | CIBSE C5.2 Dry Fire Commissioning – Automatic Controls
8d94776f-2c3e-5b52-9840-1c1e5ac8f34c | note | CIBSE C5.2.9 Alarm Functions
05cb258b-8323-5f22-a6b9-25d468fad7dd | note | CIBSE C5.6.0 Sensors/Detectors
e60a4fbe-b29b-50cf-be82-24fad6a38447 | note | AS1670.1-2018
2c7bac6e-5541-59d0-b17b-73ae28f6d829 | note | Are Detectors activated when tested?
e67248c7-6baf-5b8f-905a-c25280cbc261 | note | Do indicators function correctly on Detectors and FDCI?
b4e3b7f4-a037-5519-a9f2-9b2041c6da74 | button | Has "GMF-COMRPT-001 Fire Detection Zone Commissioning" been completed? | Yes, No
32bb26de-64ea-57d3-b11a-9c44b34af8c2 | note | Attach relevant photos and a copy of GMF-COMRPT-001 below:
4b9327e1-f494-4f7f-8c8d-830560cde386 | checkpoint | 2. CONDUCT 100% TESTING OF SMOKE AND THERMALS
9ec6e64c-354d-57dd-b880-77db12cfa4d9 | note | CIBSE C5.2 Dry Fire Commissioning – Automatic Controls
462cd57a-f79e-5065-a917-35085978adfc | note | CIBSE C5.2.9 Alarm Functions
d236b7c1-f1c1-55ab-9930-340484c62daf | note | CIBSE C5.6.0 Sensors/Detectors
8217100b-1594-5424-8b77-333be03d8c57 | note | AS1670.1-2018: Ensure Detectors are activated when tested and correctly indicates on the detectors and at the FDCI
37b8f0e6-20e8-5e00-ab82-d134547163ad | note | Are Detectors activated when tested?
fcd7a4dc-fced-5e5c-ad40-a918e13ae83d | note | Have all dust covers have been removed from detectors?
c0e621b2-a3a9-54b1-b01d-7d50d44becbd | note | Do indicators function correctly on Detectors and FDCI?
5bb3a169-203d-5798-973a-5ae16aee4772 | button | Has "GMF-COMRPT-002 Fire Detection and Alarms (Smokes, Thermals, Duct Probes)" been completed? | Yes, No
7dd1a23e-7782-5b27-8ea1-b36fffa5466a | note | Attach relevant photos and a copy of GMF-COMRPT-002 below:
f71a14d1-51ce-42e7-8df7-08f926c1b41e | checkpoint | 3. CONDUCT 100% TESTING OF MCPS
17df2458-e159-59ed-98ae-3d36f03034c2 | note | C5.2 Dry Fire Commissioning – Automatic Controls
9c9ff771-02b9-597d-9122-b52f173df581 | note | C5.2.9 Alarm Functions
ce7962f1-7141-5664-8d22-e59c64b3deb3 | note | C5.10.0 Manual Call Points
bfce5fbd-c35e-58d3-99c8-532386cbddbc | note | AS1670.1-2018
65261d23-3e01-5ae0-a1d7-8689ffeadc2e | note | Have you checked:
a6420129-7f3b-5d9a-a875-6230d8619f3e | note | The correct operation of each manual call point; and
61999d87-a492-560e-8791-61dd99540a15 | note | That the activation of manual call points on the same circuit as other actuating devices does not cause existing detector alarm indications to be extinguished; and
0ca04cd2-3230-578b-a1f8-6aee5e7bbe1b | note | That manual call points are not subjected to alarm dependency; and
102ac8d1-4bf8-5ea6-b137-8feb37a6686a | button | Has "GMF-COMRPT-003 Manual Call Points" been completed? | Yes, No
cf462bd9-65c2-5816-96b4-61fad4131e6c | note | Attach relevant photos and a copy of GMF-COMRPT-003 below:
af39f8c8-1c5d-4766-9d8c-85523ab1515e | checkpoint | 4. CONDUCT 100% TESTING OF DOOR DEVICES
594b217c-6f9a-55c3-92d1-da05a6a61baa | note | C5.2 Dry Fire Commissioning – Automatic Controls
5eb2cee9-5cdc-5793-8575-05e2ab5146fa | note | C5.2.9 Alarm Functions
2674939f-aa7c-58b8-9dc0-a5c6ce3cf26b | note | C5.8.0 Modules Input/Output
f409763c-aea2-5b68-aa28-46fbbc738c94 | note | AS1670.1-2018
24a89da4-45e1-5364-8596-660b4caf38ba | note | Has the operation of each device/door release been checked after install?
70ce64e3-aac3-5034-a598-52ead760c6f1 | button | Has "GMF-COMRPT-004 M.D.H / Auto Door Commissioning" been completed? | Yes, No
1f468956-8869-532c-9bac-43342d58c98e | note | Attach relevant photos and a copy of GMF-COMRPT-004 below:
73df5432-b5aa-4ddb-84a8-5f5b3b730051 | checkpoint | 5. CONDUCT 100% TESTING SPEAKERS AND ZONES
1da6fbd9-f191-5c92-b194-7ae983f25d50 | note | C5.2 Dry Fire Commissioning – Automatic Controls
44b80e03-e116-5282-becf-8b99cbaf7a88 | note | C5.2.9 Alarm Functions
f8c675ea-8ec1-549e-b1de-6e0c777b7dd8 | note | AS1670.4-2018
d78fc89c-d459-5e5d-878f-a1f75aee9217 | note | Have the audible signals, visual and tactile signals been checked? (automatic operation)
6f977890-c895-54c6-89a0-96dbc89e8b93 | button | Has "GMF-COMRPT-006 Emergency Warning Commissioning" been completed? | Yes, No
4674b28e-ba5a-5ca1-8da4-48cce96793af | note | Attach relevant photos and a copy of GMF-COMRPT-006 below:
da8bb009-1956-45c9-a12d-a0fc7da42008 | checkpoint | 6. CONDUCT 100% TESTING WARDEN INTERCOM PHONES
7421e5cf-fe33-543b-a76b-67615ea82d55 | note | C5.2 Dry Fire Commissioning – Automatic Controls
cc0851f3-0918-5fcd-a3b4-c756a1b3f7fa | note | C6.2.8 Warden Intercom Phones
e23086c1-8669-5490-9ad3-2ca6ca80a10b | note | AS1670.4-2018
8e0c3678-143f-5461-ad24-cc00caa1f1c7 | note | The WIP audible call signal shall have a SPL of not less than 80 dB(A) when measured at a distance of 1 m from the WIP.
e76daece-9b84-50e9-9749-4ecb4ccb1720 | note | The SPL of the WIP handset audible call signal shall also be met when the WIP handset is mounted within a security enclosure.
0caa5414-d059-5cca-9f53-9c7ccf9158f1 | button | Has "GMF-COMRPT-007 Warden Intercom Point" been completed? | Yes, No
ff067782-15eb-518f-aaa0-14b2f1fb110e | note | Attach relevant photos and a copy of GMF-COMRPT-007 below:
ddcff21e-94e1-4850-b24d-1922f60e056c | checkpoint | 7. CONDUCT 100% TESTING CASCADE AND EWIS ZONING
0c487f65-f820-5114-b6bd-7e3e4d402b9e | note | C5.2 Dry Fire Commissioning – Automatic Controls
318ce5c4-c679-52ca-ad10-5f3de99940f3 | note | C6.2.5 Cascade Sequence
06ed8442-a37a-529e-a016-22a501a37a9f | note | AS1670.4-2018
14c98ec5-c4b3-5350-9ac9-e7c96b17d104 | note | Have the audible signals, visual and tactile signals been checked? (automatic operation)
fe6e9809-b998-5ba9-96cd-1362459e79aa | button | Has "GMF-COMRPT-005 Emergency Warning Cascade and Matrix" been completed? | Yes, No
bf86c973-2f77-55ae-a135-28add6ab648d | note | Attach relevant photos and a copy of GMF-COMRPT-005 below:
8368cf74-147b-410b-a9fa-c315d4971a40 | checkpoint | 8. CONDUCT 100% SPEECH INTELLIGABILITY TESTING
0164c6a1-3667-5730-9acc-75ef4fd017be | note | C5.2 Dry Fire Commissioning – Automatic Controls
5686719c-fcc0-55ae-b3d7-d9689344068d | note | C6.2.5 Cascade Sequence
0e5b7251-5c6b-5dc9-ad33-b642f87531e1 | note | AS1670.4-2018
ec1118ff-d518-500b-901b-15406c6c1e66 | note | Have the audible signals, visual and tactile signals been checked? (automatic operation)
630aad5e-33b9-53f0-ab4d-6a49a862c9c4 | button | Has "GMF-COMRPT-008 Speech Intellegability Readings" been completed? | Yes, No
e41c5958-902c-5207-9a5a-86148252934e | note | Attach relevant photos and a copy of GMF-COMRPT-008 below:
2611541d-65b2-4ae9-bdf2-1bfdfb12cc79 | checkpoint-no-value | GM Fire Sign Off
ae1f87df-7f01-4d59-8c08-696b8b3b5992 | signoff | GM Fire Sign Off
4b7ea19e-4ec1-4f8a-9016-79cc14322bfa | checkpoint-no-value | Principal Contractor Sign Off
dd7be1bc-fe69-476c-92f5-b6167cc41369 | signoff | Principal Contractor Sign Off
f705478c-39e0-457b-866b-0ea0e7a506f2 | checkpoint-no-value | Consultant Sign Off
67d5ff8e-6ab3-43d2-b9fd-763cb2a95c10 | signoff | Consultant Sign Off
5119f6b4-6c29-48c9-a75a-bc0ec8382f57 | checklist | ITPS-201 Interface Commissioning | itp | ITPS-201 Interface Commissioning
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
b21307fd-1f5c-47da-be20-c7e00c1bfd59 | checkpoint | 1. CONDUCT FIRE MATRIX TESTING
e40a97cc-ec24-5fdd-b105-7a901bbdfc74 | note | CIBSE C6.2.4 Fire Matrix
da5f8aae-a7b5-5b59-99c5-bab728c2d064 | note | AS1670.1-2018
ef3dedab-67dd-5504-bc72-1c152b794956 | note | The ‘end-to-end’ test should include the activation of associated detection devices to confirm that all required functions operate correctly in accordance with the system interface matrix.
0c01d155-f8b9-5c93-aaa3-5e6b35bf5ae8 | button | Has "GMF-COMRPT-009 Systems Interface Matrix" been completed? | Yes, No
bf0a9da4-1bfb-5b36-880e-a3271da637ee | note | Attach a copy of GMF-COMRPT-009 below:
324f8729-7ac0-4fab-af3a-a9371d333bf1 | checkpoint | 2. CONDUCT FIRE FAN CONTROL PANEL AND BRIGADE INTERFACE TESTING
a9eddf23-2b1c-5507-b05c-0fdddead1c84 | note | CIBSE C6.6.0 Brigade Interface – FFCP
eac2a80c-1179-5c9b-ac92-80b41d3fcefc | note | AS1670.1-2018 Appendix A
69ef7e04-f00e-5a33-98a5-e7185c91296f | note | Check Fan Control Operation as per Matrix.
8b594c7a-a9a1-5f70-a813-22081b5652c3 | button | Has "GMF-COMRPT-010 Fan Control Matrix Testing" been completed? | Yes, No
e075b23b-6d52-59ec-8157-c7244832a2d0 | button | Has "GMF-COMRPT-011 Fan Control Overrride Controls" been completed? | Yes, No
957d16d8-38d1-5143-af5b-31f048a48b0f | note | Attach a copy of GMF-COMRPT-010 and GMF-COMRPT-011 below:
e55a6ff6-3408-4510-986f-b6f2e6a0f277 | checkpoint | 3. SPRINKLER INTERFACES FITTED OFF
b25513ef-dca5-534a-af81-f93a92559f27 | note | CIBSE C5.8.0 Modules Input/Output
28b0b075-5e6a-5d78-b70f-89775ecdfb3a | note | CIBSE C5.2.9 Alarm Functions
048c89d5-5155-540f-ad7a-faf2e0a6474f | note | AS1670.1-2015
142d578d-36d0-538b-89c6-1e07ace4987f | note | Prior to any interface testing, have you checked all systems listed in the system interface schedule are complete and operable?
58f38d40-c666-53f5-bda1-d584769b0267 | note | Have you checked all systems interfaces to the FDAS?
da76c833-0b9c-5907-a064-d8dadf96538d | note | Has "GMF-COMRPT-020 Sprinkler Zone Commissioning" been completed?
da828634-d47d-58e8-8586-7a11818ea85f | button | Has "GMF-COMRPT-021 Pump and Tank Indication" been completed? | Yes, No
e89e8129-5576-59cf-a676-4daafdf2f2b7 | note | Attach a copy of GMF-COMRPT-020 and GMF-COMRPT-021 below:
7e9eba19-82bb-4a1f-b97a-52e0a32111d7 | checkpoint-no-value | GM Fire Sign Off
cd36ab30-e58b-43d6-8875-0f50aac226a0 | signoff | GM Fire Sign Off
94fc2855-925a-4ba9-b8bf-f408b4089d1e | checkpoint-no-value | Principal Contractor Sign Off
373d913c-b324-495f-923a-6ba20cd0ffa7 | signoff | Principal Contractor Sign Off
d022aaeb-b40a-444d-8966-e8d08f3f40d4 | checkpoint-no-value | Consultant Sign Off
5ef435f1-7dc8-450c-99eb-2426b403359e | signoff | Consultant Sign Off
185c60cd-8bc7-4de9-b034-16876bb2f836 | checklist | ITPS-202 ASDS Commissioning |  | ITPS-202 MASDS Commissioning
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
80f9107e-c5bc-4b75-a8ea-df4aa666ceab | checkpoint | 1. VISUAL INSPECTION
814e388e-52d0-58eb-bed4-859df1004947 | note | CIBSE C5.6.0 Sensors/Detectors
242a6fc7-2600-568f-8265-b799ec689315 | note | AS1670.1-2018 Appendix A
8501ab06-7170-5aeb-bd84-3703a58953a5 | button | Have you visually inspected every sampling point to ensure it is not obstructed? | Yes, No
6d45da97-eda1-52ad-bb54-3f5109646c0b | note | Add Photo
1999e822-9452-47d7-9583-0aa749a688a2 | checkpoint | 2. ALARM TESTING AND TRANSPORT TIMES
a3359e40-c836-55e5-a430-e0eac24e75ce | note | CIBSE C5.6.0 Sensors/Detectors
c98eb2bb-f64c-5799-92b7-23c7fc7e38d5 | note | AS1670.1-2018 Appendix A
e9c7bf96-941f-5f1f-bd22-2567d6ccef67 | note | CHECK AND RECORD
44f05811-595f-5d56-8d88-95953dbb72d7 | textbox | The response of all capillary sampling points using a test medium placed at each sampling point:
c118ca81-08ff-5ee0-9788-4555d1a3ad41 | textbox | Measure and record transport time (TT) from the EACH sampling point:
3dbf83bc-3344-51fc-9f8b-c2737537412b | button | Has "GMF-COMRPT-012-ASD Commissioning" been completed? | Yes, No
fab7c242-4863-5ddc-b8b4-ecd6f50573c8 | note | Attach a copy of GMF-COMRPT-012 below:
fcfb0755-5e68-4b25-a230-81cb2597d972 | checkpoint | 3. OPERATION - ALARM, FAULT AND ISOLATE
f7a2a78e-fc94-5cef-a916-2ebbf5dc1016 | note | CIBSE C5.2.9 Alarm Functions
22ee586b-0f53-5a32-beb3-a91e8c30a297 | note | AS1670.1-2018 Appendix A
3d271fc7-21b2-5402-b06f-74779be1f1d4 | note | Have you checked:
98ebd64a-175a-51da-97aa-06cea8cb243c | note | The operation of remote indication of alarm and fault signalst; and
ee698bab-a429-5744-8bb1-c8217a1b8f78 | note | The operation of airflow failure indicators; and
856c8d79-2fa8-5a3b-a4ba-104e0c00a33e | note | The operation of the system failure indicators; and
6b5f5bd1-b43c-50ec-a8f3-74d0d761b002 | note | The isolate and reset functions; and
a8ea02f0-6b9a-5572-a59b-61483a9bcb88 | button | The fault and alarm test facilities (where provided)? | Yes, No
6f319d38-43f2-44b2-a44b-2e5fa38a21e1 | checkpoint | 4. ASD MATRIX (If Applicable) - Including Thershold Testing
82d54aee-7d4d-5914-a4e0-7817f8501656 | note | CIBSE C5.2.9 Alarm Functions
255cbf59-225a-53be-818e-1ffb5f68a101 | note | AS1670.1-2018 Appendix A
4181d465-71e8-54e0-8a5d-3e7d8be0827b | button | Has "GMF-COMRPT-013 Double Knock Testing" been completed? | Yes, No
4994f2f1-64b5-5094-91dd-53c0ae6b85b0 | note | Attach a copy of GMF-COMRPT-013 below:
31c8c949-28f7-47f1-be22-45a4441baa98 | checkpoint-no-value | GM Fire Sign Off
0582ce7b-e0b9-4505-8bd9-c9563b7df8c7 | signoff | GM Fire Sign Off
63debe2c-fd7a-442d-85aa-2c686fea1036 | checkpoint-no-value | Principal Contractor Sign Off
7f3a400d-907c-41a9-b799-065056957cc2 | signoff | Principal Contractor Sign Off
ef72c45b-9c00-4a01-99d4-14831c646753 | checkpoint-no-value | Consultant Sign Off
82047bf5-25e8-43bc-bc94-835a0e297036 | signoff | Consultant Sign Off
fc7ce04c-c799-4af2-8860-41f1dd3a737e | checklist | ITPS-203 Pipework Pressure Testing |  | ITPS-203 Pipework Pressure Testing
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
f6491c03-3c03-4ed8-af1b-b45a2c5e6da4 | checkpoint | 1. SCHEDULED TEST IS APPROVED - CONFIRM
711559eb-2780-559d-b80b-1614511e7bd1 | note | CIBSE W5.5 Pre - Commissioning
ea3c8a4a-950e-5690-bf29-637f54feeab0 | note | Have you received Approval for test time and location?
9de199c0-6eee-5b84-b41e-3eb07e89ac67 | button | Has the site been notified? | Yes, No
454776ed-b9b9-5a5a-b8b4-d54e55d5cecb | note | Add Photo
08ce5945-0506-4e33-ab37-f84b8a465252 | checkpoint | 2. EXCLUSION ZONE - CHECK
cb0a6f37-89ef-53b2-b704-acecd4685ef4 | note | CIBSE W5.6 System Checks
20d80c82-c0e2-53d3-9076-64a88de339ab | note | Has an Exclusion zone been set-up?
4c2e4cb1-2110-5a62-aa5f-afe1e71d92ef | note | Have you erected appropriate barriers and signage?
4aaaec45-713e-5466-8911-f3f28ff27ac5 | button | Have all workers/occupants been notified and have they exited the area? | Yes, No
aec94ecb-9fd4-50ba-9db6-0a9b190c70eb | note | Add Photo
ab628435-99e9-42d5-bf36-66dd437c1f92 | checkpoint | 3. VISUAL INSPECTION - CHECK
99798143-1251-5eff-a76e-3b6fe2f09014 | note | CIBSE W5.3 Check before Filling
d9fd6f2f-552e-5d7a-93da-ca369556ed72 | textbox | Drawing Reference and Revision number:
fcd3b69c-da8a-5edf-912c-0bc00dcd5e3c | note | Is Installation complete?
fbc787a3-b239-5085-93bb-6862ff669dc9 | note | Have End Caps been fitted with lockable ball valves? (BLANK END CAPS MUST NOT BE USED)
2bd2fe17-e74c-5e27-a49c-97342c9760c8 | button | Are all outlets sealed? | Yes, No
26fb1101-f7c5-5078-b01e-a2dff9ea3026 | note | Add Photo
b5091f5a-312b-4887-9b6b-9f9d21b4e100 | checkpoint | 4. FIT TEST PUMP AND CALIBRATED GAUGE - INSTALL
012f6428-b793-5bf8-a10a-0064699d22fa | note | CIBSE W5.3 Check before Filling
0338b214-b289-55db-ac08-5a97a1d0f9db | note | AS2118.1-2017
cec63ea8-ab0e-5912-83ca-5cb3a3164727 | note | Is the Pump installed in a safe location?
dbb4fb6c-c3fd-5ebb-8996-c279b4c0cde9 | note | Is the Callibrated gauge in visible location, and accessible to photograph?
49024145-1e67-5ab6-bd7e-f5625d9a3960 | button | Have the Pump and Callibrated gauge been tested? | Yes, No
c814378c-3e74-5f85-bdb6-b86f29716a5e | note | Add Photo
e4ba9322-cc3c-4a2f-adba-1f7151a8cb1d | checkpoint | 5. CONDUCT BREATH / LUNG TEST
6bc1897f-e04a-5c13-a0a1-580417a47324 | note | CIBSE W5.3 Check before Filling
39369833-75e4-5e10-bad1-65b55f29a028 | note | AS2118.1-2017
16c2597d-eab2-56be-b1ec-03972f5af02d | note | Perform Lung/Breath test where possible;
7a2e2f52-81f6-5dcc-889f-d11a13763ad5 | button | Is the system sealed? | Yes, No
77220dcb-112c-5e95-baab-d041634da5de | note | Add Photo
98fd5334-302f-421f-898b-69bef3a75722 | checkpoint | 6. FILL SYSTEM - STATIC PRESSURE ONLY (OR AIR PRESSURE)
2cab9061-5a7e-5731-9eaf-6ca93842eef6 | note | CIBSE W5.4 System Filling and Venting
b014362a-55a5-5fd8-82d0-7e3e4d03edce | note | Prime system to towns main pressure OR 300kPa (depending on test);
8b0fb4e8-8731-5cc8-9c0b-cac467d6d8be | button | Are there any leaks in the test area? | Yes, No
abe6f3f9-b2e2-5087-b820-8544d5e99eae | note | Add Photo
d457625e-14b3-47da-8d76-d905157623ad | checkpoint | 7. START PRESSURE TEST - CHECK
76a7b190-d774-5766-bed4-1cee8001b283 | note | CIBSE W5.4.1 Pressure Testing
a3cda305-cac5-59d8-b333-586a36792ca5 | note | Increased pressure to 600kpa start pressure;
17d0bb8f-6fb7-53f0-bbe8-61f85c1f48a9 | button | Are there any leaks in the test area? | Yes, No
fdf873a0-87e0-5967-b227-e47e0180fd52 | note | Add Photo
8612e37b-4567-42b4-91d8-00a41aca99aa | checkpoint | 8. INCREASE PRESSURE
4ea07c45-bdc4-5ccd-b0fe-c9673a8379bd | note | CIBSE W5.4.1 Pressure Testing
63242ed1-7752-5c42-86c2-df744caa8ff5 | note | Progressively increase pressure in 100kPa incraments; and
d40425a0-fd50-5fe8-97b0-4881dc93865b | note | Inpect test area for leaks at each increase; and
4b1c2e38-8e9a-55e8-b423-abbedcbf15d6 | note | Repeat until pressure reaches 1600kPa;
4c00d570-99ca-569e-8c9a-484f96f9ae96 | button | Were there any leaks in the test area? | Yes, No
4a94fa3a-06b2-516d-9062-c03b3c9eb2fa | note | Add Photo
95fa8361-b3bd-4596-9e85-cf123bc35e9a | checkpoint | 9. HOLD PRESSURE
2b106e93-8778-58b3-97e7-840d763403c2 | note | CIBSE W5.4.1 Pressure Testing
a90c7188-d675-56d5-a728-137e144e0eb9 | textbox | Record Start Time and Photograph Guage:
46fabe82-845f-596d-bff1-df035a4b11c6 | note | Hold pressure for 120 minutes.
e75ff54b-3b7c-53b3-bcde-f393a8b24999 | button | Was there any pressure loss? | Yes, No
84e26eef-ce96-56ac-9d72-949f23fc5dd6 | textbox | Record Finish Time and Photograph Guage:
f80d5c71-8468-54bc-8522-aaed0b547b36 | note | Add Photos
11c717c0-9cc2-4e19-a1c3-f0675a8ad13b | checkpoint | 10. DE-PRESSURIZE SYSTEM
05508627-6bb9-50fe-b295-e422f38152d1 | note | W5.4.1 Pressure Testing
dcc83702-9e45-54ca-9e42-4117fe94a5f4 | note | Release test pressure from system.
0a4a151b-d4ff-5132-b113-1d16a8f3722a | note | System remains primed with towns main pressure.
742eaf14-36d9-5b8b-a258-b94cd4c8149e | note | Add Photo
48033f9a-5d5d-45d5-8123-c55731f82097 | checkpoint-no-value | GM Fire Sign Off
1a830642-f25a-4539-8f63-235ba9ee74c9 | signoff | GM Fire Sign Off
b710ad61-fcb8-40c3-84b9-183de151ad8d | checkpoint-no-value | Principal Contractor Sign Off
eb7e9b1d-56b2-42c3-8d9b-4716159f4faa | signoff | Principal Contractor Sign Off
421fdbfe-9edf-4917-a35c-13b215bc7a3b | checkpoint-no-value | Consultant Sign Off
9989031b-8f23-4f8e-8031-6f3ff3515d5f | signoff | Consultant Sign Off
e5601da9-39ea-44db-b5b5-830e00edc988 | checklist | ITPS-204 Electric Fire Pumpset Installation and Commissioning |  | ITPS-204 Electric Fire Pumpset Installation and Commissioning
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
1401a72c-e781-47b1-94e1-b6e5856ff253 | checkpoint | 1. CHECK AND CONFIRM - LOCATION
93ec039b-4ae4-566c-ad0b-0d4b891fb403 | note | CIBSE W5.2 State of the System
a23660f9-7623-56c6-8bd7-a67f099eb7d4 | note | AS2941.1-2013 – Section 11
43b6c11d-0a8f-50ef-a172-09f362b8cac0 | button | Has the Installation Pump been installed in a position that is protected from falling debris, and vehicular and mechanical damage? | Yes, No
35c9d95a-fedf-5091-a985-323b0a7f06ca | note | Add Photo
a9719397-82ed-4fa0-b9df-f73c3c1b8fdb | checkpoint | 2. CHECK AND CONFIRM - CLEARANCE
9b978971-0d3e-559f-afb4-3a8bf1f7ec71 | note | CIBSE W5.2 State of the System
9a85ba1c-14cb-5721-8f2c-c4a8efc760c0 | note | AS2941.1-2013 – Section 11
6132ed28-ec6d-53fa-9657-73d87dbd3e7f | note | Is there at least 1.0m of clearance around the perimeter of the complete pump setup; and/ or
1f55af21-f204-593d-8c1d-c16ff035ff8b | button | for multiple pumpset installations, there is a clearance of atleast 600mm between each of the installed pumps? | Yes, No
6e59f343-9b2b-56f2-bd87-93c7a6176158 | note | Add Photo
837be147-b371-4d9d-98fd-601a9223ca37 | checkpoint | 3. CHECK AND CONFIRM - ELEVATIONS
34392b4d-e9ce-54bb-ba9c-6639ad3eb49e | note | CIBSE W5.2 State of the System
77cddf6c-32f2-5611-b294-33873f8cf63c | note | AS2941.1-2013 – Section 11
dd794cb7-aa66-5708-80ab-7b20e4373197 | note | Have pumpsets been installed with the centre-line of all suction pipes at the same elevation; and/ or
e9ca00a3-78b5-5667-ae5b-ce21ad7cd106 | note | if the pumps have been installed at different elevations, the elevated pump is installed on a properly constructed mezzanine floor; and
a8b57da2-7512-5421-bed2-be10f67c9071 | button | with head clearance of minimum 2.1 m to the underside on both levels? | Yes, No
edb825fc-c15a-517f-97da-053bfdb86787 | note | Add Photo
0c0df48b-5a10-4c1d-859a-0ec7dabbc43d | checkpoint | 4. CHECK AND CONFIRM - PLINTH
6ca70430-5931-590c-90a9-6d73c5b04686 | note | CIBSE W5.2 State of the System
319e67ff-fc9a-54cf-beb2-54b58310e099 | note | CIBSE W5.6 System Checks
3fedac7b-6de8-5652-bf77-27cc724c0a6b | note | AS2941.1-2013 – Section 11
980feef8-dd74-5ab9-85df-d255e7233445 | note | Have pumpset baseplates been mounted on concrete plinths with a height not less than 150 mm above the floor?
f9447368-1f9d-5ff5-89b9-729ac95bb3e4 | button | For fixing purposes, does the concrete plinth extend 150 mm past the edge of the baseplate on all four sides? | Yes, No
aff0ebf6-56aa-5853-9545-3308fda4b52d | note | Add Photo
d5a42842-a3e2-4d4f-89c3-b1524053b606 | checkpoint | 5. PRECOMMISSIONING CHECKLIST - CHECK
c2025f7d-cf95-5b57-84b5-532b24dbeddb | note | CIBSE W5.5 Pre - Commissioning
7c9685f1-09c3-55ad-865d-3441a2974b5e | note | CIBSE W5.4 System Filling and Venting
4e463e95-7367-565d-acfb-e08c708144bf | note | AS2941.1-2013 – Section 12
7710ee6d-0fc7-5e57-9e26-3ee96fc2a07b | note | Have you checked the coupling alignment to ensure that the unit is aligned within the manufacturer’s specified tolerance?
bb139bdb-3010-5e29-a08a-438cab765e84 | note | Have you confirmed the direction of rotation?
e39295d0-0a87-59fb-94d1-68a4ebed5f0c | button | Has the battery electrolyte level, and the battery leads and connections been checked? | Yes, No
72d52741-69c3-5c45-987c-af0317457cd3 | note | Add Photo
fb5b4689-e273-46b2-b321-3d686f8d0959 | checkpoint | 6. PRECOMMISSIONING CHECKLIST - ENSURE
9ecc9bfc-2a83-5f24-aff2-1f313970bec1 | note | CIBSE W5.5 Pre - Commissioning
1c398f31-069b-51b6-bc6e-242e0ae5dfc2 | note | CIBSE W5.4 System Filling and Venting
c406b122-f81d-5d36-ae29-c2a7d43ceb61 | note | Is the delivery from the pump under test the only supply to the measuring device?
cdd5e872-72df-5ee6-a12f-f5d056b8871d | note | Does all flow from the pump passes through the device?
74e49a6a-a67a-5275-b192-5ca14c7c56b0 | note | Is the pump primed and lines are clear; and
bf0aefdf-5f25-5f3a-8be6-d0d9ba62351d | note | valves are correctly set (open, closed or adjusted to required pressure); and
3d27f72d-a40e-5a5c-a0de-021ed1cacf66 | button | is water available? | Yes, No
50f6c047-4354-5331-af36-5afb63c825c8 | note | Add Photo
62d49da1-9698-4e71-b893-adb1f3ecc776 | checkpoint | 7. PRECOMMISSIONING CHECKLIST - ISOLATE
61276998-3462-5717-9bce-fe802eddc54c | note | CIBSE W5.3 Check before Filling
f5fc2965-b085-5a78-aeed-f49862cc4072 | note | CIBSE W5.4 System Filling and Venting
04086f2e-3d8c-5b87-9a4d-75761aba7d18 | note | AS2941.1-2013 – Section 12
7914846c-d6db-5cc2-8956-1b8fdad3fa35 | button | Have you isolated all other water supplies to the fire protection systems, such as the automatic pressure maintenance pump and any other compression-ignition engine driven pumps in the system? | Yes, No
91dceaac-6925-5239-894d-ce17ffcbdbd4 | note | Add Photo
66ec0ce6-fd24-477b-bae8-ef12b5251072 | checkpoint | 8. PRECOMMISSIONING CHECKLIST - REPORT
83ab05c6-d858-555e-985a-2bf13bb567a6 | note | CIBSE W5.5 Pre - Commissioning
66d64f04-ccab-5b1e-be6f-550f12ed80c3 | note | AS2941.1-2013 – Section 12
9653deee-2449-59d2-a510-aa7a621a478a | textbox | Pump plate details:
a7cae91a-51b4-5d12-a0af-070141083360 | note | Add Photo
ca64d6d6-a0da-4cd4-b417-d7cd722ab7e3 | checkpoint | 9. COMMISSIONING CHECKLIST - RECORD
dc72df96-a8f8-5956-a935-1d0f4a12fba9 | note | CIBSE W7.10 Commissioning Certification
2039dfbf-ee0d-5208-9909-09036e943b12 | note | CIBSE W7.2 Flow Rate Measurement Tolerances
fc6fef21-5845-5406-bf03-029c37dac7e4 | note | AS2941.1-2013 – Section 12
5bd98a82-22d3-518c-91dc-e8c75f3d3645 | textbox | What is the pressure in the system at which the pump starts automatically?
2deb9cdf-6428-54e8-939c-44c8e1255a70 | textbox | Pump shutoff pressure:
b0d9cf72-7ceb-50d3-9e78-3406c60719f7 | textbox | Motor shut off pressure:
48ee8f06-7161-5ada-acb0-53b1ac4896e0 | textbox | Delivery pressure at maximum flow:
46f2bfd1-1537-57e2-b010-1685d7317125 | note | Add Photo
3abef9a7-19c0-49a5-afb1-81d05b568f2a | checkpoint | 10. COMMISSIONING CHECKLIST - RECORD
c89bbb3f-ab1f-5679-b9cd-2ac04f374777 | note | CIBSE W7.10 Commissioning Certification
55acdf1c-8f22-5fc9-aa9a-dff2ed94aa16 | note | CIBSE W7.5 Preliminary Flow Rate Check
92de8957-a71b-5582-8ecb-b3931f6297ed | note | AS2941.1-2013 – Section 12
8363d403-5a00-55cf-848a-7f0db1112a10 | textbox | Record the pressure on discharge gauge and motor current at three other flow rates between shutoff and maximum flow, one of which should be at the duty flow rate:
9bda7e33-1e0c-58d6-adb4-09b188568b2c | note | Add Photo
f68791a9-58e5-4cdc-8f8b-7c5365b93b26 | checkpoint | 11. COMMISSIONING CHECKLIST - RUN AND RECORD
454faa4e-f910-5fd9-8c08-2bbaf107b7c9 | note | CIBSE W7.10 Commissioning Certification
e1be9bc6-802d-5509-af93-347c7ddbcaa3 | note | CIBSE W5.7 Static Completion Records
d2879826-767a-5d27-aace-879ccef9d940 | note | AS2941.1-2013 – Section 12
c02b28f7-c7cd-5ff3-be67-4d7243c319f8 | note | DURING OPERATION:
b21af1be-cef1-5928-9875-791541cf2d19 | note | Have you checked the temperature of the bearings and stuffing box leakage and noted any abnormality?
38a013c8-9eeb-5d73-8ee4-6e5b66c3c117 | note | Have you checked that all alarms and indicators, both visual and aural, have been activated; and
317268a0-4040-51ae-8b5c-69d86b0f2151 | button | Alarms and indicators, both visual and aural, revert to normal stand-by status when pump is stopped? | Yes, No
df193def-8fee-5e25-b662-2fcb7b91ad31 | note | Add Photo
912553ab-2075-4b32-9425-30fdc49d0b15 | checkpoint | 12. COMMISSIONING CHECKLIST - RUN AND REPORT
d62218f2-497a-5f43-90ed-2c83156d7364 | note | CIBSE W7.10 Commissioning Certification
ca2e8b81-08dc-532a-a36f-790045b83c77 | note | AS2941.1-2013 – Section 12
655de2de-0d9f-58d1-806a-f51618d581a6 | note | RUN AND REPORT:
67fa3124-bc38-5f7e-8ea2-8d0201241ed7 | note | Is the electric pumpset, together with its associated control gear and ancillary equipment, functioning correctly?
42acdd30-f098-5831-acee-6f8521a67eba | button | Does the pumpset satisfy the intended performance conditions? | Yes, No
440638c3-8820-5338-991d-f631b1c7813b | button | Are there any operational abnormalities? If Yes, detail below. | Yes, No
46c80522-d94b-569a-9697-ec4fa704cbc5 | note | Add Photo
439903c6-c563-49ae-bf86-ad33186acd85 | checkpoint-no-value | GM Fire Sign Off
d1e657f8-239b-4ccc-b660-9cdc97a72008 | signoff | GM Fire Sign Off
4d9a3af6-346d-485c-a59e-afb4b18d5b3f | checkpoint-no-value | Principal Contractor Sign Off
f00732bb-7211-4c26-9fb5-c78d1ff01fdd | signoff | Principal Contractor Sign Off
eccefe1a-fa7f-421a-b64e-50afe78665ba | checkpoint-no-value | Consultant Sign Off
0ed7a4b2-7c5e-499c-b5e3-fc57b4526c23 | signoff | Consultant Sign Off
b225c4ca-4192-44b2-9a7d-ce4b375c0f4e | checklist | ITPS-205 Diesel Fire Pumpset Installation and Commissioning |  | ITPS-205 Diesel Fire Pumpset Installation and Commissioning
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
4ce8a016-716e-4119-a807-6438dd1d0d46 | checkpoint | 1. LOCATION
794d0e1b-427c-577c-872f-8289bab1e680 | note | CIBSE W5.2 State of the System
686ffbcc-ec7d-521c-9d27-25947de4b41d | note | AS2941.1-2013 – Section 11
2adb0d11-9d2a-5bb3-a1b6-58e23cf20fa6 | button | Is the Installation Pump installed in a position that is protected from falling debris, and vehicular and mechanical damage? | Yes, No
4df3f32b-0f87-5657-8c3f-a6e21ef8fd91 | note | Add Photo
54061128-a235-4f60-8a3c-d283d1335169 | checkpoint | 2. CLEARANCE
76d8b8c5-cbc0-5097-9f5f-9d5c3af94244 | note | CIBSE W5.2 State of the System
9aa700d0-ad24-51d3-8b46-183fff9d583a | note | AS2941.1-2013 – Section 11
f749bc67-c5a0-51df-bb01-c98506f32005 | note | Is there at least 1.0m of clearance around the perimeter of the complete pump setup; and/ or
aed13af4-22b7-5d02-b6e3-8233d7317ed2 | button | for multiple pumpset installations, there is a clearance of atleast 600mm between each of the installed pumps? | Yes, No
268f7072-6619-5644-9d73-d9ebb6a98ed8 | note | Add Photo
675e3953-b21a-4ad0-bf09-42567bd9b816 | checkpoint | 3. ELEVATIONS
f46cfa5f-0707-52d4-bfa1-53bfe364c43e | note | CIBSE W5.2 State of the System
9654eadf-0ceb-55c7-9d38-d23a5c197700 | note | AS2941.1-2013 – Section 11
0d73cca0-1903-554c-88b3-7386dc4fbd8a | note | Have pumpsets been installed with the centre-line of all suction pipes at the same elevation; and/ or
5b13ac35-221b-5169-a4a8-256dab2c2c08 | note | if the pumps have been installed at different elevations, the elevated pump is installed on a properly constructed mezzanine floor; and
acc4194b-766c-5831-9450-1adb4d845be1 | button | with head clearance of minimum 2.1 m to the underside on both levels? | Yes, No
14103439-dc2e-599c-87a0-30ce2ea3a6b1 | note | Add Photo
81e0f263-dad4-427a-af7f-d5efe6a0a6e6 | checkpoint | 4. PLINTH
48c97d13-0628-55c4-a52f-d329abe8128d | note | CIBSE W5.2 State of the System
9399cda3-de56-5783-91b3-83f0c37cf42b | note | AS2941.1-2013 – Section 11
cf3bf002-a5d5-5807-adb5-726e71f0a6aa | note | Have pumpset baseplates been mounted on concrete plinths with a height not less than 150 mm above the floor?
bd37f5fe-91c5-56e4-876e-e156a9557a0c | button | For fixing purposes, does the concrete plinth extend 150 mm past the edge of the baseplate on all four sides? | Yes, No
9ef51a25-72d5-5453-bfc3-8cb05384f310 | note | Add Photo
6caf1ba3-e213-4999-b4f8-613bcecfe6da | checkpoint | 5. PRECOMMISSIONING CHECKLIST - CHECK
a6288286-7f1b-5dd3-8394-fed057b7504c | note | CIBSE W5.5 Pre - Commissioning
7c21a387-f111-5938-ab94-1bbc614726e4 | note | CIBSE W5.6 System Checks
aa5e8242-9950-5086-b5c1-f9650df7fbd0 | note | AS2941.1-2013 – Section 12
f32c9d1d-f54b-5369-9845-f3365cfcbb2d | note | Have you checked;
a5704812-7296-5229-884f-d236462b83d8 | note | The cooling supply system; and
dea07c29-762e-5bb0-9847-c59584d87512 | note | Engine fuel supply; and
c0e16c39-1614-5b7b-aa6b-6d57480455a2 | note | The coupling alignment to ensure that the unit is aligned within the manufacturer’s specified tolerance; and
05b5ca73-41d5-56e1-a696-c1411eeb07f2 | note | The direction of rotation; and
886bfe0d-ab0c-5922-9615-190e1457d4ea | note | That the engine lubricating oil is at the correct level; and
8326b3b4-c592-5bc5-a0a3-d415f92a347c | note | The battery electrolyte level and the battery leads and connections; and
a8803385-4669-5ac2-9023-ac0c4c11030f | button | That the exhaust system is intact? | Yes, No
c4bd2397-874c-5123-9a93-cbbb52b84522 | note | Add Photo
c1b3d17c-5960-43ed-8533-9295e58bc863 | checkpoint | 6. PRECOMMISSIONING CHECKLIST - ENSURE
f2ac4c7d-e199-50a4-b4b4-8c4844d7e9b0 | note | CIBSE W5.5 Pre - Commissioning
4a83a057-c48c-5634-98c1-f4c45aa542a6 | note | CIBSE W5.4 System Filling and Venting
f87ba262-d673-5206-b659-06ff26e3fcfd | note | AS2941.1-2013 – Section 12
bce6df7b-8cb6-5f07-9ce2-97a6b9854ecb | note | Is the pump primed and lines are clear; and
487c4f22-37a3-5c82-bd46-14134ef14cf4 | note | valves are correctly set (open, closed or adjusted to required pressure); and
334d11fb-7b43-54d2-a998-55c4e5b7b1dc | button | is water available? | Yes, No
0afe26e6-6897-5565-b2bc-8c8d81e6d139 | note | Add Photo
fd9cf697-3927-4b7f-a1e6-9bb40344f444 | checkpoint | 7. PRECOMMISSIONING CHECKLIST - ISOLATE
b8b6c16d-c996-552d-8183-3f3e6f15a476 | note | CIBSE W5.3 Check before Filling
dde4fdbb-e2a1-5999-b41b-0b340fa4982d | note | CIBSE W5.6.2 Mechanical Checks: Automatic Control Valves
12da7dbe-a45c-5411-8b34-d9a5c1e5d39a | note | AS2941.1-2013 – Section 12
1c5ee796-e8e3-5c56-8941-4cd94160e178 | button | Have you isolated all other water supplies to the fire protection systems, such as the automatic pressure maintenance pump and any other compression-ignition engine driven pumps in the system? | Yes, No
0db53e62-ec9f-5916-85e0-f81f8d1c225c | note | Add Photo
06f8dd1c-e3c8-42f8-9a19-d633128cfd83 | checkpoint | 8. PRECOMMISSIONING CHECKLIST - REPORT
699335ec-c08c-5722-9640-015a90d537f7 | note | CIBSE W5.5 Pre - Commissioning
363c3ca4-2040-56db-a7da-dc6711e7aa84 | note | AS2941.1-2013 – Section 12
e7c265b9-237d-51cb-a3f1-628bdcc784ca | textbox | Pump plate details:
06b2ad24-c743-52d0-b6a7-3bb01b06b318 | note | Add Photo
9de6ad24-9873-4fc2-9d09-f6f8cad53eb6 | checkpoint | 9. COMMISSIONING CHECKLIST - RECORD
9fdc2da0-be2f-5776-80b0-a4ed8ca147f0 | note | CIBSE W7.10 Commissioning Certification
96adc920-fb98-5022-8aa2-935da569ad6a | note | CIBSE W7.2 W5.7 Static Completion Records
aa37baa3-6a77-5355-a2e0-e6febb1296d8 | note | AS2941.1-2013 – Section 12
3f97bb98-632e-54a6-bf5d-18ee0e1fe17c | textbox | What is the pressure in the system at which the pump starts automatically?
b9779469-c274-5f9b-9e38-f392f69f8bc1 | textbox | Engine oil pressure:
300590e9-f721-556a-83c8-0907c6ce3d1f | textbox | Pump shutoff pressure:
a583503a-f9bd-5f82-8c94-41dddfbdd7d4 | note | Is the Coolant flow correct; and
d8e2b1a1-4362-56fd-9da8-5640f14b14fc | button | Are the fan belts rotating and intact? | Yes, No
573cdf2e-49ca-5a1a-bbed-cc13747d61fa | note | Add Photo
b4f51475-6a2d-5885-becb-0aed1a830701 | checkpoint | 10. COMMISSIONING CHECKLIST - ISOLATE
34d928d4-b9bb-52f4-a207-87e55c84b6a8 | note | CIBSE W7.10 Commissioning Certification
05cf3260-4c6f-59f9-925c-051faf6d69b6 | note | AS2941.1-2013 – Section 12
ad2cd759-071a-5a3b-a267-98919468bc20 | note | ISOLATE the flow meter, partially open the test valve, and flush to remove any debris or foreign matter;
c86753cf-9de2-5f3c-976d-f6a4767887fb | textbox | open any meter-isolating valves, open the test valve, and record pump delivery gauge pressure when approximately full load flow is indicated on the flow meter:
2b90ec82-c5d2-5ac4-a1df-5db191cc2f60 | note | Add Photo
b9f052e6-e367-44ac-87dd-5dbb542e2b97 | checkpoint | 11. COMMISSIONING CHECKLIST - RUN AND RECORD
7c198f01-15d0-5179-aacf-7f6cc7dc3882 | note | CIBSE W7.10 Commissioning Certification
4e41ddad-fa1b-5d69-936f-5aa8ef9b07fa | note | CIBSE W5.7 Static Completion Records
216d48d3-f40f-50f2-b065-22746228af05 | note | AS2941.1-2013 – Section 12
3808afd6-096a-56d7-a966-afb08390b4f6 | note | RUN the pump for 30 min at maximum flow and record.
85c324eb-7978-5870-bb73-02dbf6d56af9 | textbox | Suction and delivery pressures:
3bc1a54b-e7fe-5c73-bbd2-6d5717580a12 | textbox | Engine running temperature:
bef05381-4376-5910-b711-7d32fe4b7cf4 | textbox | Engine oil pressure (within the engine manufacturer’s limits):
70583689-1e01-579f-8b2f-02786794a553 | textbox | Air temperature at pumpset:
93b0c498-f14f-5e40-8647-7f2dca4eacb5 | note | Hold the engine shutdown mechanism closed and simulating an automatic start signal until the engine has attempted to start for five automatic starting cycles.
3da5fb4b-c30e-5f25-96af-74186d4dc46e | button | On the sixth starting cycle, return the engine shutdown mechanism to its normal starting position. Does the engine start immediately? (Clause 9.3.6.2) | Yes, No
cf87689c-22b1-5db8-8800-84352c7e5d09 | note | Add Photo
89136ac2-e7da-4e71-a217-c350de26b0a3 | checkpoint | 12. COMMISSIONING CHECKLIST - RUN AND RECORD
ed60559c-6802-576a-9039-af992d446f15 | note | CIBSE W7.5 Preliminary Flow Rate Check
456c383e-a94c-5f72-8e5b-ccd49c1e7dad | note | CIBSE W7.2 Flow Rate Measurement Tolerances
af71fb18-5590-5fa9-980f-2cf72875722a | note | AS2941.1-2013 – Section 12
2e7a63fc-1937-516d-ac01-0fa327f5be11 | note | RUN the pump for 30 min at maximum flow; then
8ef4f6cf-6be2-59cd-8430-6734765f89b1 | textbox | Discharge pressure at three other flow rates between shut-off and maximum flow, one of which shall be at the duty flow rate:
9af852e3-223e-50b1-98ff-26acdc0d8e54 | note | Add Photo
dd3d2e6f-1737-484e-8668-9e581e9320c0 | checkpoint | 13. COMMISSIONING CHECKLIST - RUN AND RECORD
88b0c517-c4e7-5e0a-8f13-5dee0728761a | note | CIBSE W7.10 Commissioning Certification
f2889d4b-c540-5330-942c-8674032f367f | note | CIBSE W5.7 Static Completion Records
fdaf169d-ab25-5a8e-bc1b-e61eb216d6c9 | note | AS2941.1-2013 – Section 12
4b54d5f7-4419-5cca-b9db-53ade154d1d1 | note | DURING OPERATION:
2790d9fc-b6f4-5886-b46c-1378ee69ed15 | note | Have you checked the temperature of the bearings and stuffing box leakage and noted any abnormality?
479f48f8-b4c4-51ae-a5ac-635fbff14a3a | note | Have you checked that all alarms and indicators, both visual and aural, have been activated; and
31ac04f5-e82f-5839-b71d-3fc0bb732e21 | button | Alarms and indicators, both visual and aural, revert to normal stand-by status when pump is stopped? | Yes, No
89c5ba42-39f1-53a3-9f77-0fc68a5c5034 | note | Add Photo
562239d0-93ca-499d-a4dc-43537d65d5ae | checkpoint-no-value | GM Fire Sign Off
b70049f6-f23e-4b93-be4a-a692a143cb15 | signoff | GM Fire Sign Off
6ba80533-95e6-4bf9-b5c0-9c8640af64d0 | checkpoint-no-value | Principal Contractor Sign Off
e06386d2-67db-4b92-ae29-cf4a8bd4833f | signoff | Principal Contractor Sign Off
dbf9dc45-d8a2-44ab-b08d-e4a20e96abd5 | checkpoint-no-value | Consultant Sign Off
cc2d01a5-a24b-403d-91d2-cd072b39b6a1 | signoff | Consultant Sign Off
904e473e-47b7-4872-afdc-8976b4618274 | checklist | ITPS-206 Sprinkler Commissioning |  | ITPS-206 Sprinkler Commissioning
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
726ef3e4-bb25-435d-bfb6-48e6425cdbea | checkpoint | 1. CONFIRM WATER SUPPLY & PUMPS PREVIOUSLY COMMISSIONED
1c2d8973-ff1f-530c-b1e0-ccde3b3c310e | note | CIBSE W5.2 State of the System
87ee7588-f131-59a6-afe4-da03bc62f414 | note | AS2118.1-2017 - Section 14.9
806336c4-e32d-5d3f-9dda-44d6124fba63 | note | Water Supply & Booster Pumps have been commissioned
7b67508e-6add-58db-9b59-35e6dc89dded | button | Are all Valves in the correct position? | Yes, No
9640b4f2-e6c6-4ba4-8db1-e4aef1ae5560 | checkpoint | HOLD POINT
99c1a9b1-845e-5734-86f6-74d412d0e050 | note | There is a risk of damage to pumps if system is not ready for sprinkler commissioning . Refer ITPS-204 and ITPS-205.
b69d51d6-2955-4f25-8e67-bf4bd596a358 | signoff | GM Fire Sign Off
3e49aadc-59d4-4b89-9412-9443c2413b47 | checkpoint | 2. CONDUCT FLOW TESTING TO PROVE SYSTEM PERFORMANCE
107a7f34-b8d3-5e91-b2d2-0e4c939efa22 | note | CIBSE W7.5 Preliminary Flow Rate Check
6f4e43b6-34af-5fad-a41d-c9aa1938ec42 | note | AS2118.1-2017 - section 4.2.2.
3aecb1ac-ffc5-5c55-a20c-75bbadc7ac04 | note | Test
53725cfa-bb6b-53ab-bbe7-7be310546379 | note | 1) Confirm flow & pressure requirement
f7e9f690-fe51-514a-9bd5-9779f81fbf93 | note | 2) Secure flow meter to annubar test line
b99d16d3-f0ac-5125-8560-a65966a0224e | note | 3) Manually start booster pump 1
aef37d78-0b4c-5245-bc95-47310294a1b0 | note | 4) Incrementally open annubar test valve
d8a224bc-005b-5655-b1d0-e60314bc93a3 | textbox | 5) Record test flow & pressure at each stage:
3ee2d3d2-2e90-5482-9895-b2113941bd61 | textbox | 6) Record pump data at each stage:
3218e841-4aff-501c-b6a2-5eda0ea5e3ed | note | 7) Confirm system achieves pass result
d7dfe26b-d6b0-5814-bf42-dcce5017e6f2 | note | 8) Close annubar test valve
c392268b-f8da-517e-87b0-470e213b4d75 | note | 9) Stop pump
5033fd27-8c2d-5491-b402-bf6969db2eb6 | note
9c594ef3-096e-5041-8d55-b262afbf4bef | note | Has the Sprinkler Block Plan been completed?
9c4bedd4-0556-51da-a65b-e3ff1e6931f3 | button | Have you recorded this on the Pressure Gauge Schedule? | Yes, No
e5386685-0b5b-525b-82b3-12659fe2ab4f | note | Add Photos
8d2ec80d-37d9-4ab3-8759-fce2f6fe6a99 | checkpoint | 3. CHECK OPERATION OF DBA PRESSURE SWITCHES
470ec837-e7c9-5fc6-9b08-c2da0ec5fbc3 | note | CIBSE W5.6 System Checks
c8670e88-27f5-5543-b201-19b8d3f95a58 | note | AS2118.1-2017 - Appendix H4
f9723db4-9635-5685-a67b-b898ab4f0de4 | button | Does the pressure switch change state when system is activated (Rise in pressure switch)? | Yes, No
0b6d22db-a2bd-547c-896e-0c7a3e353775 | note | Add Photo
0506d7b4-1d2c-49d7-b918-0c1e8a891444 | checkpoint | 4. CHECK OPERATION OF PUMP START PRESSURE SWITCHES
a190d6a7-f767-5c25-8362-b15ba3b28052 | note | CIBSE W5.6 System Checks
1d624510-723d-55be-9109-779db15741ae | note | AS2118.1-2017 - Appendix H5.4
fa7947d8-e4d2-5d2b-b964-049764f8df68 | note | Are the pump start pressure switch settings in accordance with pressure gauge schedule?
b6ed5c2f-4938-54ed-9846-c22fd29201a5 | button | Have you checked the operation of All pressure switches individually? | Yes, No
c8910824-713d-5c70-8753-3142c3b408ba | note | Add Photo of Pressure Gauge Schedule
ed0af70b-9f67-4044-b29b-3b17a4683c0c | checkpoint | 5. CHECK OPERATION OF DRY FIRE INTERFACES
dd1f6178-85ed-52b5-a38f-79ec5d44fb90 | note | CIBSE W5.6 System Checks
84624320-92c2-58e1-9c43-b2b70e975a88 | note | AS2118.1-2017 - Appendix H6
2b47e2cb-ca76-5bc6-8c84-e880caafa477 | note | Activation of ancillary Pressure Switch (Rise in pressure switch) registers at FIP
aa64e749-ef61-5288-a93c-cf4d7a80a136 | note | Activation of flow switches register at FIP | Yes, No
cbed7106-9fd3-5160-95a7-9293ba774378 | note | Change in valve state/position register at FIP
0dab319c-e9c3-54a9-bac3-d92d8f5f780a | note | Attach the valve list
8be23b22-91f7-4239-be01-e0bf556a0403 | checkpoint | 6. COMPLETE FORM 71 & ALL TEST RECORDS
9fbda25e-96f1-5043-a8e6-0b8d37ccbdcb | note | W7.10 Commissioning Certification
612f9ad8-907b-53ed-adfe-45ce11bb92ff | note | NCC 2019, AS2118
208711d6-6c4d-5c88-802d-b8805d537ef6 | note | Flow test pass result on Form 71*
a5f6a9b9-f691-5971-859c-77d4b3d4fbb3 | note | Record the pump start pressure switch set points:
112ee4cb-f919-5c99-9042-e28252d77930 | button | Record the dry fire interface test results: | Yes, No
c2986637-da5f-5b1c-a517-90e3e427f8e8 | note | *Form 71 - Fire Hydrant and Sprinkler System Commissioning This form is to be used for the purposes of commissioning water based fire safety installations, as required by the Queensland Development Code – Mandatory Part (MP) 6.1, which is a building assessment provision under the Building Act 1975, section 30.
a86ddcc6-0123-5888-947d-794f7cc54142 | note | Add Photo
17235cab-9637-43be-9b80-49624941c9cf | checkpoint-no-value | GM Fire Sign Off
4d75dbe3-097c-4adc-8450-d45d39ca06c0 | signoff | GM Fire Sign Off
ea2c5a3b-d467-4f9c-a0a7-4ef86ad64afc | checkpoint-no-value | Principal Contractor Sign Off
fb7b303b-9369-4cb9-b855-9a8d42e5f3bb | signoff | Principal Contractor Sign Off
63e194ec-e4a5-4d07-8012-8639591b0550 | checkpoint-no-value | Consultant Sign Off
e1634f45-0155-42fe-913a-c7dc5e84f833 | signoff | Consultant Sign Off
11883ffe-c187-496c-a36c-1b8ffe4cf077 | checklist | ITPS-207 Hydrant Commissioning |  | ITPS-207 Hydrant Commissioning
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
384baf46-8ac5-44c5-9371-495d1461547d | checkpoint | 1. CONFIRM WATER SUPPLY AND PUMPS PREVIOUSLY COMMISSIONED
b8609c48-fcdb-5151-b1e3-6e606c9714ba | note | CIBSE W5.2 State of the System
3fb835ca-f219-5694-a8d1-a1545ad2cacc | note | AS2419.1-2005 - Section 4 - To comply with Part 4.2
e68546fa-d1e4-5031-b010-0ddc20b73244 | note | Have the Water Supply and Booster Pumps been commissioned?
4c82752a-91d0-5ce8-b17d-30cc5e04c442 | button | Are ALL Valves in the correct position? | Yes, No
859a0b14-b90f-41ca-b6e9-857dd5725699 | checkpoint | HOLD POINT
e90cc70d-3627-5112-bb19-8bda9901a5f4 | note | There is a risk of damage to pumps if system is not ready for sprinkler commissioning . Refer ITPS-204 and ITPS-205.
beb0451a-5895-4a15-91c4-c57fee1117d0 | signoff | GM Fire Sign Off
8411d399-bb8f-48ca-b2ff-2d7e5a20581c | checkpoint | 2. CONDUCT FLOW TESTING TO PROVE SYSTEM PERFORMANCE
36523e3c-7e98-575e-b665-e6f5bb17c1ac | note | CIBSE W5.2 W7.5 Preliminary Flow Rate Check
f5717354-bca8-51d2-ae96-d6e3443f73a0 | note | AS2419.1-2005 - Section 2
2add7594-2f7e-52c1-8192-969837fabe41 | note | 1) Confirm flow and pressure requirement
bd351425-ecd7-5def-8a72-868c593c7bc4 | note | 2) Secure micrometre and calibrated gauge to hydrant outlet
e2dbbaad-bf34-5a7e-bd5f-afadd6425db5 | note | 3) Manually start booster pump 1
cb19b323-fd2e-52fc-a246-7810fcf27198 | note | 4) Open hydrant valve to required flow rate
a78be6ed-3f62-563a-83a7-f1394453946c | textbox | 5) Record residual pressure at required flow rate:
52178ecf-3c0b-558d-9aa1-ced5cd5cc857 | textbox | 6) Record pump data:
3afc1643-6cf7-563d-8db9-dd54e6f18a3f | note | 7) Confirm system achieves pass result
8317a1a5-94b5-5252-9618-78325b216724 | note | 8) Close hydrant
b4411edd-12eb-5217-8346-734ad92c1250 | note | 9) Stop pump
faad2cc9-e5ba-57de-9272-880a09d5dcdd | note | Attach Hydrant Block Plan and Pressure Guage Schedule
2056767c-f1fa-4c71-a673-166059a94c71 | checkpoint | 3. CHECK OPERATION OF PUMP START PRESSURE SWITCHES
85a22966-cfb2-5610-8ab7-3223a6a7c3e1 | note | CIBSE W5.6 System Checks
71963d85-8bf7-5d23-be18-d55943de6e3f | note | AS2118.1-2017 – Appendix H5.4
030acb86-7db9-5134-a922-5261f8acf277 | note | Is the pump start pressure switch settings in accordance with pressure gauge schedule?
ced83c9d-1d1a-5cbc-b492-47e7e4503459 | button | Have you checked the operation of all switches individually? | Yes, No
ffee1ae9-c046-5c79-b118-243941a9c793 | note | Attach Pressure Guage Schedule
aca8cc56-8e48-4633-95d9-f477c8320dd1 | checkpoint | 4. CHECK OPERATION OF DRY FIRE INTERFACES
aa5ba526-0145-508c-bae0-ccd00f2f1675 | note | CIBSE W5.6 System Checks
241c7fe9-1568-527b-9a28-4940ad221eec | note | AS2118.1-2017 Appendix H6
6429ed67-d634-5698-bd56-448fa1c7ae56 | button | Change in valve state/position register at FIP | Yes, No
20bcb277-d0fd-57f5-8465-ad5bb950ba9d | note | Attach Valve List
84b7fdb9-dc7f-44c3-9557-66de9c296f05 | checkpoint | 5. COMPLETE FORM 71 & ALL TEST RECORDS
3254c634-d7d3-5bed-9b4c-294582c25cac | note | W7.10 Commissioning Certification
2f1ab442-cd99-575f-b17e-5758b15fbb21 | note | NCC 2019, AS2118
7d9cb622-1ea8-51cf-b8eb-51f2dfc31fed | note | Flow test pass result on Form 71*
df6f18d9-1130-5e33-b029-680151367100 | note | Record the pump start pressure switch set points:
549eb23a-d3d3-5198-a234-16d38e02fc13 | button | Record the dry fire interface test results: | Yes, No
8a2462f8-4cc7-525c-8f8e-1f25cd61b70b | note | *Form 71 - Fire Hydrant and Sprinkler System Commissioning This form is to be used for the purposes of commissioning water based fire safety installations, as required by the Queensland Development Code – Mandatory Part (MP) 6.1, which is a building assessment provision under the Building Act 1975, section 30.
02f67a4c-3858-5bea-b22e-7fc8d42432e9 | note | Add Photo
814deee1-d820-432e-a1b4-d720787e01ac | checkpoint-no-value | GM Fire Sign Off
687fd1d8-b44c-4010-8be3-96992bf383fc | signoff | GM Fire Sign Off
778bdea2-669d-446f-a225-67c83b067874 | checkpoint-no-value | Principal Contractor Sign Off
7d5553b8-8045-4a90-ac3a-325b94498f6d | signoff | Principal Contractor Sign Off
52e6bd86-e782-4ea6-97a0-c924a69f7607 | checkpoint-no-value | Consultant Sign Off
102d5af3-d6bb-4829-ae39-471ccd00bbdb | signoff | Consultant Sign Off
2211d7f7-ee52-4a2b-a094-eca4e22923e1 | checklist | ITPS-209 Deluge Commissioning |  | ITPS-209 Deluge Commissioning
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
eb373b4e-3ec5-436a-8638-24690320d47a | checkpoint | 1. AREAS PROTECTED
eff422ea-31c3-50d0-b9a0-03a38806d8d0 | note | CIBSE W5.2 State of the System
17e7b772-fe7b-5775-9c5e-184a638cc758 | note | AS2118.3
a640dab4-ec4d-5b79-bcbf-40cce29ec0b2 | button | Have you ensured areas protected do not exceed 300m/sq per valveset? | Yes, No
04d0a40d-3fe4-5746-a9a6-ca92e4519232 | note | Add Photo
9b1c1ff7-1dd6-4e87-a08a-776602a39869 | checkpoint | 2. HYDROSTATIC PRESSURE TEST
5c4141f8-2f04-512d-9f67-ce63974cbda2 | note | CIBSE W5.4.1 Pressure Testing
116f138e-7c4a-5169-940f-90aff24fe080 | note | AS2118.1
89113776-7a35-5a25-a90f-7acf03eeda85 | button | Have you completed a hydrostatic pressure test as per ITPS-203 for each deluge system? Note: Where open sprinklers are used ensure all heads are plugged prior to pressure testing. | Yes, No
f00a4c5b-1882-549f-9df6-1020a665c4de | note | Add Photo
06d2be04-1f12-44c2-a00d-ef301e75d49a | checkpoint | 3. EQUIPMENT TESTS - SYSTEM FLUSH
8e9d29bd-fa2e-54dc-8f55-2938291f2654 | note | CIBSE W5.5.2 Flushing Procedure
6c948c7c-69a9-53ba-96b9-bb083efd10df | note | AS2118.1
3b98bdf6-8e27-5c6b-b123-ac5745a8b819 | note | Complete the following PER valveset and open sprinkler head:
bbada224-14ee-5b6b-8865-3306c16dde80 | note | 1) Flushing of each open sprinkler head to ensure debris is removed.
ddb12192-bbf9-5276-b2ad-af295474742f | note | 2) Setup filtration mesh and water bin at each open head off each system (is there are a large number of heads then separate system by plugging each head).
925e05c9-9032-5467-ae53-3ee85a43f2f8 | note | 3) Let water flow through pipework onto filtration mesh
462457e5-f2f4-5dd3-b948-d78e204ad0a5 | note | 4) Once water is clear from debris shut off water and return system to normal.
eeea2c29-a420-5ce6-8bb6-2a695558ca20 | note | Take photo per deluge head and record deluge head/s location:
8d5ff72a-efb0-47dc-a871-a7cf69cafe95 | checkpoint | 4. RETURN TO NORMAL OPERATION
8aa49d3f-4e9e-54f0-a490-30dcb44f3a82 | note | CIBSE W5.6.2 Mechanical Checks: Automatic Control Valves
5002a83b-6716-5714-b58a-c92bf9fbb2ed | note | Are all open sprinkler heads re-installed where previously plugged?
857e114f-9cc5-59d5-85bc-fa5617bfd214 | note | Have system valvesets been returned to normal condition (or approved condition where construction still occurring)?
a9b85515-0c1d-583f-b7b2-629a2ff2d29d | button | Have water filled bins been emptied as per principle contractors requirements? | Yes, No
51563ee8-acdd-5c3d-b3b2-bc8fd17078a0 | note | Add Photo
a184c11f-3196-4bb2-b6d6-42cde9c904a3 | checkpoint-no-value | GM Fire Sign Off
b99c1026-4be5-4bbb-8f8f-e18ba6fa578b | signoff | GM Fire Sign Off
15511aaa-f952-4518-b3f1-952e26fceb1b | checkpoint-no-value | Principal Contractor Sign Off
cdaa1fef-1689-4c03-8199-6f23c46f5e23 | signoff | Principal Contractor Sign Off
ad63f4ff-cf8b-4d7a-bf3a-e9b20803be2a | checkpoint-no-value | Consultant Sign Off
cf865958-335a-4b73-a3c3-960adb18fdb7 | signoff | Consultant Sign Off
d6f31708-0c27-4027-a990-d90867dd3a45 | checklist | ITPS-302 QH Concept Design | itp | ITPS-302 QH Concept Design
d849d0bd-74ea-411a-a683-6dafb5bc6a13 | section | Details
f2fb8c41-7d26-4cfe-81c5-47b4bcc6980b | checkpoint | 1. Compliance
ad8a0214-4d91-557c-8b6a-59a711cddc50 | button | Does this design comply with the QH brief and CIR? | Yes, No
2bd89b82-04d8-514e-870b-d8c4469774f6 | note | List all codes and standards that you have complied with.
ad62bf16-a605-5663-9677-73d71a8afb91 | textbox | Australian Standards:
b7df0f52-3295-5cab-b659-cb35e38c6cf5 | textbox | National Construction Code (NCC):
13176a99-6fb0-5c88-be61-6f41fa68c64e | textbox | Site-specific factors and requirements:
8b377405-f547-536b-89d4-35790685f620 | note | Redundancy and reliability:
7ecd831d-fd7f-53be-925b-35e97de03adf | button | Is this in accordance with the AS and site requirements? | Yes, No
757e6150-a60f-5409-a477-a75d743b8637 | note | Future proofing:
ae6df7c7-c394-58c6-8942-db8afb66cde0 | button | Have you allowed for site expansion at major infrastructure (i.e. sprinkler manifolds, water storage tanks)? | Yes, No
ddb42761-344d-5d4b-9a0d-c8b5ad7ef4da | note | Disaster management:
32938e9b-09e8-5020-b701-f1dee373cb71 | button | Is this in accordance with AS, NCC and site-specific disaster management requirements? | Yes, No
028a6ffc-a889-5231-9f44-70fed43e3f6a | note | Performance & Maintainability:
6b66e7d7-d991-5519-af06-a1a42e31c149 | note | Is this in accordance with the AS and NCC requirements and;
0a5cc01c-d8bf-5460-9d85-c470707b1c6e | button | Have you assessed plant and riser spatial requirements for maintenance? | Yes, No
38d5a598-bbc1-435d-9734-825faa263613 | checkpoint | 2. Design process
c9de9656-9ee8-501a-a911-9688b884f2f1 | button | Have you completed a preliminary assessment and sizing of fire services infrastructure requirements, including tanks, pumps and major valve sets; and | Yes, No
4aa4620e-b6cd-5b28-a81a-2543cd734415 | button | the reticulation strategy to determine the quantity and location of risers; and | Yes, No
2c7fca45-2296-55f1-99d5-b1b3b9179bc1 | button | identified the required plant and riser areas for integration into the building’s spatial planning? | Yes, No
c14ed4e8-8204-4252-abf1-d63d632c4459 | checkpoint | 3. Cost estimates (in conjunction with QS for all phases)
d6110786-cf2b-5671-b1ce-30d7a8d36d54 | button | Did you coordinate with Quantity Surveyor (QS) for cost estimates based on preliminary plant requirements and outlet counts? | Yes, No
3c3fe8c1-e81d-4fe7-b460-f3e1c493662a | checkpoint | 4. General Coordination
ba2acf4c-c575-585e-a8b9-78896e753bd6 | note | Have you provided spatial requirements for plant rooms, risers, and access points; and
c8ee78b7-47ff-5a89-b32e-d9f953a6d123 | note | Liaised with key stakeholders; and
bf1c7ceb-0dfb-5e16-b9b3-a74428288451 | button | Provided input into the concept design report, including engineering baseline assessment for existing buildings? | Yes, No
88f668d5-9621-455b-b5fe-287f4b980050 | checkpoint | 5. Documentation and Reporting
ee6e6b9f-e2d3-5a52-b757-1dc35e3e1edd | note | Have you prepared design reports and documentation; and
dbac6845-03b5-5d80-993d-a5f9330cef26 | note | Reported any areas of non-compliance; and
f1a591c3-7c32-5a23-959a-b6c80afaae5c | button | Provided preliminary schematics to articulate requirements? | Yes, No
25335675-a655-5fa3-8b5b-7414c25f46b8 | note | Note all deviations must be raised via non-conformance submission.
8bb370d6-28e6-4bed-86b8-4ea5b2d36aaa | checkpoint-no-value | GM Fire Sign Off
67fa41f4-613a-4aa8-bd3e-f1074dfcae86 | signoff | GM Fire Sign Off
96a24b88-f65c-437a-aad3-2cd9b9661f3b | checkpoint-no-value | Principal Contractor Sign Off
d2382630-0623-402c-8532-3d7206217ef9 | signoff | Principal Contractor Sign Off
4dadd16b-2b24-4c97-a62c-1cc9d0800af5 | checkpoint-no-value | Consultant Sign Off
6d6c9a10-b7c7-4f88-bceb-4f18912f7834 | signoff | Consultant Sign Off
e6293711-ffd0-4808-a67e-7a03e57e1ea2 | checklist | ITPS-303 QH Schematic Design | itp | ITPS-303 QH Schematic Design
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
67404a03-0940-45d2-be75-5e052250a802 | checkpoint | 1. Compliance
ad6feb75-f172-512a-9a58-cfdf750c2a42 | button | Does this design comply with the QH brief and CIR? | Yes, No
1d8c601f-f39e-53f8-848e-6820ecd8ce7f | note | List all codes and standards that you have complied with.
9c6ee057-3d04-5357-a693-ef377dec7cc2 | textbox | Australian Standards:
6254fa70-c401-583c-ade7-edf7ed4a0af0 | textbox | National Construction Code (NCC):
b63ba54c-5fa6-5d94-9ce7-e8c447660b5d | textbox | Site-specific factors and requirements:
644ed55a-b0c3-5344-8ba8-20122a9082d9 | note | Redundancy and reliability:
bac9452d-fc9c-5cb4-9291-f04a880f0beb | note | Confirm strategy for site supply redundancy and reliability.
7f839fd9-8f9a-5934-9efd-1de259b29c8e | button | Have necessary details been included in schematic drawings to confirm reticulation redundancy and reliability strategies? | Yes, No
2bed11b4-65c0-5bf5-9a63-ab87acd61e9f | note | Future proofing:
767b5823-13b6-5d54-a02c-9c63601e64dd | button | Have you documented and aligned the strategy in the schematics and design reports? | Yes, No
ee4f2c2e-6040-5adb-a14b-70b61538f1a8 | note | Disaster management:
074ef4dc-07a5-542c-a2f7-d889e7f0ccd5 | button | Has design documentation been aligned with the disaster management strategy? | Yes, No
f40d0013-fb93-5d93-aa7f-e3094f2e4aa4 | note | Performance & Maintainability:
273d8c63-7a7b-51af-9924-4a7fb9d52172 | note | Have you confirmed performance is in accordance with the AS and NCC requirements and;
8a1842fd-7474-54b7-9f75-9dc49f90ec85 | note | Refined from concept design; and
ec737632-9728-54e4-b2a7-5f3e2cc1a861 | note | Confirm servicing access on SD drawings for plant areas; and
6a1e7ab4-8d50-5b67-8082-a6bee5e6682a | button | Provided a statement in the SD report that maintainability has been included? | Yes, No
94f846c0-878d-432d-93b8-8967a9f992f5 | checkpoint | 2. Design process
468a212b-98bf-5907-9624-7049d370dc61 | note | Have you refined major infrastructure requirements; and
0ddd2852-3199-5f28-8f27-14c245f85268 | note | Confirmed all points of connection to external infrastructure (e.g., water supplies); and
44a7a734-a411-5097-8a13-c3f33d5fb9d5 | button | Prepared fire services schematics and preliminary plant room drawings? | Yes, No
332658e2-75b4-43cb-b9ef-a5760abb1070 | checkpoint | 3. Cost estimates (in conjunction with QS for all phases)
237c7642-fe65-50c6-b12f-b38508e425fb | button | Have you confirmed cost estimates with QS based on any revised design parameters? | Yes, No
37e341a1-4647-4992-acbf-f574c91ba1b2 | checkpoint | 4. General Coordination
10d669ce-e668-58d5-9c2d-1c489411b4d8 | note | Have you provided spatial requirements for plant rooms, risers, and access points; and
b7abaf00-a539-5fbf-b4f3-7da2f260aa01 | note | Liaised with key stakeholders; and
d14a4e2d-21f0-593f-88a9-0ad97168ea6c | button | Provided input into safety in design? | Yes, No
662c7e67-df03-4331-9e13-277a3695d7b9 | checkpoint | 5. Documentation, Reporting and Drawings
f049358a-1549-5b3d-968b-b5f336554f32 | note | Have you provided input to the schematic design report; and
0922fcc5-3942-5285-8092-77a3ec711933 | note | Provide preliminary specifications if necessitated for the delivery model; and
f23716d7-7a35-5644-b40e-8ae03d5e1000 | button | Prepared schematics and preliminary plant layouts? | Yes, No
0de9f8d3-ef6a-47d9-85ca-3a45ac297a83 | checkpoint-no-value | GM Fire Sign Off
5a20cd90-f71c-45fc-9654-7bd3b9892c27 | signoff | GM Fire Sign Off
e668b9a3-be74-4f8c-8138-3a64157bae50 | checkpoint-no-value | Principal Contractor Sign Off
6dc776eb-8fee-40c3-a36e-5ffbe766e87f | signoff | Principal Contractor Sign Off
0769deee-d962-4e9b-b667-7d45d00347d8 | checkpoint-no-value | Consultant Sign Off
e3f3724b-a387-444f-ac68-2a0b239a1645 | signoff | Consultant Sign Off
ac79e6b6-fdfe-4554-8ed0-f5ff705f4a9d | checklist | ITPS-304 QH Detailed Design | itp | ITPS-304 QH Detailed Design
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
d3686b94-0e58-4e28-b119-c86250e9310a | checkpoint | 1. Compliance
8edbc314-c29e-5a3e-8c8a-290e58620260 | button | Does this design comply with the QH brief and CIR? | Yes, No
dfb38497-0a3e-5591-ba60-a6acefdd9685 | button | Have you provided a summary of applicable codes and standards in the design report, and detailed within draft specifications? | Yes, No
dc84f7d0-a877-5351-9d83-9697ee8c7085 | note | Redundancy and reliability:
b760fb25-1994-5dc8-b5eb-6ba75f6c86f0 | note | Reconfirm strategy and no material changes to site requirements.
4e835d7c-a652-53ba-9638-32e6a3a7dd4e | note | Future proofing:
a12f93d1-1466-5307-a69e-e85a752be6f8 | button | Has the strategy been documented in schematics, plans, design reports, and draft specifications? | Yes, No
03d2eeff-ae52-549c-a856-f9bbd8b58687 | note | Disaster management:
3c21e395-8c73-55c0-b2b4-3e6d727de4bf | button | Has design documentation been aligned with the disaster management strategy? | Yes, No
0311cbb0-1b77-55bc-baea-40a4f8d5a982 | note | Performance & Maintainability:
ec85fdf4-7502-538f-a3ba-f2a3f1500c0c | note | Have you confirmed performance is in accordance with the AS and NCC requirements and;
3466535b-040a-5506-a070-7feb6e84dca5 | note | Detailed design drawings to show maintenance provisions for plant areas; and
54f395fa-9a48-512d-88ac-17dbbf540753 | note | Ensured all valves will be accessible and not concealed in ceilings or enclosed; and
f81c6061-0c26-5631-91dc-65e3064831bd | button | Safety in design review? | Yes, No
359d0525-171c-5a1a-93e9-f7360ad557c6 | note | Commissioning testing and post-occupancy:
3fd83be9-e631-58af-b260-9fbe8aa32e34 | button | Have Preliminary requirements been included in draft specifications? | Yes, No
a67cc108-73b3-422e-a03a-ab94500842bb | checkpoint | 2. Design process
6c00227b-26f7-5834-8ac3-141734e87ae7 | note | Have you verified any department-specific fire services design requirements during the user group process; and
c254fedd-9c25-546a-8242-b2f2b191d772 | note | Ensured RDS capture final requirements for outlets and any other special provisions; and
79c27168-d98a-5c5f-9b84-63c2d2845643 | note | Updated documentation and progress fire services plan drawings; and
3b1bfe63-514a-5b7e-b5f3-c1fe19d524b6 | button | Provided confirmed plant room drawings? | Yes, No
4c9eb875-0175-41e8-8406-ae67aa6e14df | checkpoint | 3. Cost estimates (in conjunction with QS for all phases)
13f07fa8-1ee6-5399-94e0-fd05a035c561 | button | Have you confirmed cost estimates with QS based on device counts and/or SQM basis per department? | Yes, No
753ad2eb-2f97-4236-acbb-6bbf09229c2d | checkpoint | 4. General Coordination
f3ab6210-11d1-5bb4-abff-3c5dc3a8ba3b | note | Have you refined requirements via user group consultation; and
2ca67dfa-c610-5067-b0b9-4a6000f583e5 | note | Coordinated with architect for access and maintenance review; and
80d24c9a-4135-53c2-8081-3168ecf90b10 | button | Coordinated with other engineering services, particularly for points of interface (associated works)? | Yes, No
ce11cef7-1215-4077-9366-aab8f74ef162 | checkpoint | 5. Documentation, Reporting and Drawings
a1cf56b4-3f6a-5c9b-bbfb-1e3a750c6082 | note | Have you provided input to the detailed design report; and
124ee581-ebe5-5068-9860-be5a646d8ff5 | note | Provide preliminary specifications; and
7ae3f037-5882-5199-8d2f-ad2f11f4111b | button | Prepared technical schedules for major plant and equipment? | Yes, No
77e612dd-3785-51f0-b7b1-433268093b6a | note | Drawings:
efa47f45-6507-5a38-be2d-c6a0af18d25a | note | Has the Schematics been revised; and
14ee761c-31bc-53a5-9897-251f429b1379 | note | Have plan drawings been provided (plant areas, floor plans, reflected ceiling plans for typical rooms); and
105c0cbd-605f-528c-95fc-a80a9921c36e | button | Do they include maintenance requirements? | Yes, No
4e7d7b5c-7add-4b5c-811c-7cf81d708786 | checkpoint-no-value | GM Fire Sign Off
1758095b-4314-4498-9fd7-11febf8013c7 | signoff | GM Fire Sign Off
4f97a1ff-a7a0-4387-8f47-0a92a0cff5cf | checkpoint-no-value | Principal Contractor Sign Off
f4fe6e85-70a9-440a-ae81-6f267dd8c00b | signoff | Principal Contractor Sign Off
8f7c0b2c-bc7f-46b5-ab44-4438373dc83e | checkpoint-no-value | Consultant Sign Off
6ccba828-3094-4bac-9b80-662cb976b8b8 | signoff | Consultant Sign Off
63619b39-ba8b-4505-b6a5-01255ea7f925 | checklist | ITPS-305 QH Construction Documentation | itp | ITPS-305 QH Construction Documentation
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
e471a023-ca33-49fa-920b-7690a32ede7f | checkpoint | 1. Compliance
3a815aee-d54f-5356-945e-97da98bc5020 | note | Only deviations that have already been approved up to this point are assumed.
40f98e2e-9c29-510c-b49f-5cc1cc2e9797 | note | New design deviations should not occur in the CD phase since all scope has been approved during the Design Development (DD) phase.
5d854594-ce4f-5c6b-83a4-65db946b10f2 | note | Only deviations with detailed Construction Issue Resolution (CIR) specifications will be considered.
ed5656b5-4ddc-5631-af83-c4ea4700113d | note | All deviations must be raised through a non-conformance submission process.
776ea9ff-051f-5562-b2e0-90fa6feab51d | button | Has a listing of codes and standards been provided? | Yes, No
0a4662f7-a861-5496-83cf-3ee8163725b5 | note | Redundancy and reliability:
e5955ada-b4e0-5a5a-89c7-c46f5c451d34 | button | Do specifications and drawings incorporate redundancy and reliability requirements in accordance with the site strategy? | Yes, No
3560fc20-02c5-5f51-9501-79d54fff5092 | note | Future proofing:
2ab3f07d-977b-5d45-9a2e-8f8ed6c66660 | button | Do Specification and drawings include future proofing per approved strategy? | Yes, No
70e72af0-6d53-51f9-ac86-9281f58b2aea | note | Disaster management:
b3bf596e-db82-55cf-9ac1-f9a8af78f0e7 | button | Have you ensured design documentation captures extent of the required strategy? | Yes, No
752b7de4-d5ed-53ad-9b50-4080e7342aa8 | note | Performance & Maintainability:
1b1a273c-0e79-5b81-83f9-5be6b356f2c6 | note | Performance meets the requirements of Australian Standards and NCC; and
4ab8a29f-799d-57c4-b8cf-a9fb0615aeb0 | note | Maintainability for all plant areas, risers, serviceable equipment and valves is detailed in the documentation; and
8ccffa69-3ebe-523e-a788-abca8f5d80ff | button | Have you completed the safety in design review? | Yes, No
a075dee7-7dcc-5599-a55a-85c871415c73 | note | Commissioning testing and post-occupancy:
e516ed1f-b04d-5c1a-8a6d-8fe8521cdec3 | note | Have you ensured testing and handover requirements have been specified; and
6e3d3982-b01a-597e-b27e-de40bba3189b | button | O&M requirements are included within specification? | Yes, No
ca160dd2-95fe-4751-a29b-9b8b26be6356 | checkpoint | 2. Design process
bbf03df6-d336-5eeb-a8bc-3e81a6d7667a | note | Are specification and schedules ready; and
f7a4d3ad-8454-589d-ac04-01ae087f601c | button | Have final drawings (plans, schematics and all necessary details) been prepared? | Yes, No
0d0ac42f-6bce-4869-9f59-e17d1d4e46a1 | checkpoint | 3. Cost estimates (in conjunction with QS for all phases)
5dfdef8e-072f-5d1f-a0fa-1ee101b8f30f | button | Have QS confirmed cost estimates based on final design requirements that have been confirmed by the engineer? | Yes, No
f56920f2-f0f6-46de-bc44-2889dd7cdafc | checkpoint | 4. General Coordination
9912e0f3-7cc4-5a95-8148-cbd7062b2415 | note | Have you coordinated maintenance requirements for inclusion in specifications; and
3770bbb1-94df-540b-a4bb-c4a82eb27a33 | button | ‘work by others’ within specification documentation? | Yes, No
24a30eb1-27f8-452a-9d31-806988781940 | checkpoint | 5. Documentation, Reporting and Drawings
152be9d5-4c01-5ced-85d8-148f0d5e5302 | note | Have all detailed specifications, technical schedules and associated documentation for fire safety services been provided; and
594fe905-9c6f-5731-8d30-914f4d90a0d0 | button | Are all schematics plans and details finalised? | Yes, No
b4f26413-e17f-4434-8546-a8dff3fa5ba3 | checkpoint-no-value | GM Fire Sign Off
a6bee02b-4068-413c-964f-e1d3aac3c3eb | signoff | GM Fire Sign Off
838777dc-a42b-4f88-94ae-60ff3cbf8714 | checkpoint-no-value | Principal Contractor Sign Off
2d3e1a44-2898-404b-8491-07ddb354fa80 | signoff | Principal Contractor Sign Off
04b220f8-f916-4f22-8601-09ce6179cc43 | checkpoint-no-value | Consultant Sign Off
1df5bc15-a4a0-4011-b21e-d0bd8fb5ea29 | signoff | Consultant Sign Off
f61e3774-8e91-489c-8ee6-297f8273209a | checklist | ITPS-400 Temporary Fire Strategy |  | ITPS-400 Temporary Fire Strategy
3ac136ca-0982-4a95-856b-2e2ed0464cf2 | section | Details
fb56e710-19c6-471d-ac23-db3de0f2647d | checkpoint | 1. INSTALL AND CHECK PORTABLE FIRE EXITINGUISHERS INSTALLED AT FIRE EXITS
1150368a-e90f-4978-b3af-279e628fd981 | checkpoint | 2. INSTALL AND CHECK HYDRANT BOOSTER INSTALLED, BLOCK PLANS, LABELS
82cfe516-fd52-434f-9ae4-5a28241fcecd | checkpoint | 3. CHECK EXTERNAL ATTACK HYDRANT IS WITHIN 20M OF BOOSTER
a2261275-d199-4d42-93ed-6e5c10f9626e | checkpoint | 4. INSTALL AND CHECK SYSTEM IS PRIMED WITH WATER (TOWNS MAINS)
c8f9fa77-aabc-4c94-adf4-82b848362169 | checkpoint | 5. INSTALL AND CHECK HYDRANTS INSTALLED PRIOR TO JUMP
ee496441-53b6-411b-b4e6-f5651b795e72 | checkpoint | 6. CONDUCT WATER PRESSURE TEST OF HYDRANTS
24e28c15-3b6c-4e38-afa4-dcf7b60d640e | checkpoint | 7. HOLD POINT DETAILS
e97995a4-395b-5b97-af79-3fe3e485bd69 | button | Hold Point Required: | Yes, No
54b93c4f-e5d9-4c42-b0d1-18f62eb09f9c | checkpoint-no-value | GM Fire Sign Off
115049f8-d2dc-4e73-9845-ad6a72ec8f75 | signoff | GM Fire Sign Off
11a1655e-53c2-46e6-9df6-706fbb08aa67 | checkpoint-no-value | Principal Contractor Sign Off
fa007a02-e7c1-4643-9286-428df3ea36df | signoff | Principal Contractor Sign Off
0d7e12b9-a5fe-4d28-9400-fdc79bca6e5c | checkpoint-no-value | Consultant Sign Off
a19e064a-9ec5-4c7f-a8c6-25385d8e63b0 | signoff | Consultant Sign Off
b6c6771d-453f-4df7-8367-b17974c188d2 | checklist | ITPS-401 Site Temp Asset Lists Extinguishers |  | ITPS-401 Site Temp Asset Lists Extinguishers
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
9112d26b-cca6-411c-8b0a-b2a13c952d06 | checkpoint | 1. ASSETS 1 TO 10
60c72585-0579-50ed-8982-6fd782abf30c | note | Add Photos and Numbers Below:
52576060-a987-4f72-83e9-8197884d4753 | checkpoint | 2. ASSETS 11 TO 20
3300fdfa-9df4-5af3-a80b-ed531c10a6b3 | note | Add Photos and Numbers Below:
b686aa7a-5f06-4b48-aa08-9a970e441435 | checkpoint | 3. ASSETS 21 TO 30
193c7584-5256-5580-85c7-a14d57edba14 | note | Add Photos and Numbers Below:
82c673b1-86fc-49cf-9bc8-a6bde1150a70 | checkpoint | 4. ASSETS 31 TO 40
4cc6ae9e-2c6e-57ae-89e0-bbf57f778525 | note | Add Photos and Numbers Below:
6efb2511-db6e-4e3d-ab08-d9cc8fe42756 | checkpoint | 5. ASSETS 41 TO 50
d656d190-7beb-507b-9faf-fd30d54a9204 | note | Add Photos and Numbers Below:
ff2d6c2d-7aac-4fe2-b028-ed6fcdb42260 | checkpoint | 6. ASSETS 51 TO 60
b0cef9fb-f57b-5f7a-ac0e-1bf152fc812d | note | Add Photos and Numbers Below:
00a93cc5-f949-45fd-a8f9-e4fe5d536e6d | checkpoint-no-value | GM Fire Sign Off
35c07f7b-b59f-4c26-8f26-8f93bfde9e22 | signoff | GM Fire Sign Off
18e64411-3b9f-4e7b-974e-a53cf586350f | checkpoint-no-value | Principal Contractor Sign Off
b76124e8-1ee8-48d8-ad40-80fbc8f68912 | signoff | Principal Contractor Sign Off
b421b8f9-d7e7-41ac-8075-4aac0c132618 | checkpoint-no-value | Consultant Sign Off
35167768-107a-4dea-aca9-fa0542d44472 | signoff | Consultant Sign Off
1e70382a-cd84-5ae1-8862-c1c058edde43 | checklist | Lendlease Contractor Schedule H Checklist |  | Lendlease Contractor Schedule H Checklist
7a748d55-533f-527b-b0f9-60e8fa293f5f | section | Incident Reporting
6f2c97ae-ec7b-4ee9-b05a-57f02adc7949 | checkpoint | Incident Reporting
b5b35a37-7382-54ba-8bfb-811dbf4572bf | button | Any incidents were immediately verbally communicated to Lendlease | Yes,No
6801e20c-e2f1-5a7f-a0d5-fe47c4fd717b | button | A copy of Incident Notification Form was submitted within 4 hours | Yes,No
66e9a4c6-0421-5ef0-8732-cd78bca8e3a8 | note | Detail any incidents from the past month below and attach relevant forms below.
826609b4-fc54-5a39-ad75-e1293f234680 | section | Workers compensation first, progress and final medical certificates and Return to Work Plans
0c9492a0-811a-544b-b5bc-2fc846063034 | checkpoint | Injuries and Illnesses
e20f96b2-5ee3-56b2-b5c5-912388171f1b | note | The following have been provided;
5492c177-794d-5136-81c9-8f8430e1d1c8 | button | First Medical | Yes,No
823e0dc6-15b2-594f-962a-261c0a26bf92 | button | Progress Medical | Yes,No
09fd6dbb-22b0-55d9-bec1-c657d23b526c | button | Final Medical Certificate | Yes,No
d36edd68-abcb-576d-b8fc-6978886ed6b8 | button | Return to Work Plans | Yes,No
a20041b8-0ee5-5f04-a4e5-2f9b0b26598b | button | I have submitted any necessary Injuries and Illness forms within 2 hours. | Yes,No
b9e71c13-fb0c-5796-9a4d-1f3ce13a3ae0 | section | Reporting
e2cefbe1-7b4c-58cb-9296-52013acd2aff | checkpoint | A copy of any regulatory notices has been submitted to Lendlease via email immediately following receipt from regulator.
4094ba7a-5738-5658-93bd-78c5dff3acda | checkpoint | Daily Pre-Starts have been delivered to the office by 9am each morning.
4fb06383-4684-5418-9d3a-cc9f4daa39dd | checkpoint | I have submitted a copy of Toolbox Talks to Lendlease weekly, including records of attendance.
67b6449c-0fcb-586a-8ebf-2addf988ee69 | checkpoint | I have conducted a miniumum of 1 EHS inspection per day and a copy of EHS inspections for the month have been submitted.
2c6854ff-7dce-52fd-90e9-e611023a913b | checkpoint | Labour Statistics and Man Hours
c45fef96-b2bf-597b-b3ce-585cf62a4bdb | note | Contractor Labour Statistics:
3961a981-e885-5a9c-877f-050b8d38419c | button | Has been completed weekly? | Yes,No
2fcfc2ff-fc1b-5978-9631-1633f919466f | button | Has been submitted before the 26th day of each month? | Yes,No
506b1288-bedf-5659-a27b-52efdb96cd11 | button | Is attached below? | Yes,No
c5929b96-f03b-5652-94b3-156328f9754d | checkpoint | SWMS
1bfaab1b-8e49-53ee-9e9e-873030346dbc | button | Copies of updated SWMS have been submitted to Lendlease | Yes,No
e4104c40-5765-5a71-b723-f81d0bcfb590 | button | Contractor SWMS review register has been submitted to Lendlease | Yes,No
1adcbe56-3cdc-5f92-af30-4e947fc6e60f | button | Updated copies of signed SWMS have been submitted after onboarding each worker | Yes,No
d064d5c0-d0e0-5fe2-a4de-7727e0a3ff4a | checkpoint | Workers are trained and competent
973bcb55-6152-5f6d-a2b0-4d5902cff6f6 | button | Copy of current training register has been submitted | Yes,No
58d3b39a-17b8-56a7-9770-52ce522e2ef8 | button | Copies of licences, qualifications, training records for any courses attended during the month | Yes,No
3495576f-5639-59ab-a767-a607784a3cf2 | button | VOC (Lendlease Template) for concrete saw/angle grinders and Plant to be submitted for all workers before operation | Yes,No
aef74d7b-d587-5e34-9266-884de37191d4 | checkpoint | I have submitted copies of daily pre-start inspection records for the month
d77f5e32-8a3c-5a96-97b8-96e1ee4e803b | checkpoint | I have attached a copy of the up-to-date Plant & Equipment Register
863d56e4-a279-57b2-a68e-d4b15f9c5577 | checkpoint | Copy of current and up to date Electrical Register has been submitted ( 3 monthly unless new tools added)
1c11da09-d5b8-50be-807f-7a10f77c3645 | checkpoint | I have attached a copy of the Fall Prevention Register
f73063a9-6e9f-572b-981e-bc4461355341 | checkpoint | Lifting gear to be inspected, tested and tagged
e9a421ee-a73c-5e73-8691-a5ecb3c66c99 | button | I have submitted to Lendlease and attached below a copy of lifting equipment quaretly testing register | Yes,No
92bd2845-9677-5a10-9f62-2f292143cd1c | button | I have submitted annual inspection certificates to Lendlease | Yes,No
d8e7b937-09da-531f-a96c-18f76041589f | button | Monthly inspection register has been sent to Lendlease as per Lendlease Lifting and Slinging Guideline | Yes,No
ae92f7c6-9451-56f7-ae90-9960f5122f4b | checkpoint | I have attached copy of Hazardous Substances Register highlighting any chemicals brought on site this reporting period.
a02a0ab0-ff4d-53ee-8a92-1c3a98928fa7 | note | NOTE: Subcontractors are required to use Chemwatch to log all chemicals utilised
ba1f906f-1a0c-5a9f-a883-1abf31d17b82 | checkpoint | A copy of the Ladder register has been submitted this month
3d903859-b52d-52dd-aabf-1957c83c9f42 | checkpoint | I have attached a copy of Safety Data sheets for chemicals brought onto site within this reporting period (this month)
23484093-b5c0-5552-a60d-8d92e054fe12 | checkpoint | Temporary Works Design Register
75720ec4-cb43-5a56-a617-c22bb12e8de3 | note | NOTE Temporary Works Design Register must be submitted prior to mobilisation capturing of all Temporary works to be implemented by the trade
fcd4c867-242a-5081-80f1-6d415a64ea0b | button | I have attached the updated Temporary Works Design Register | Yes,No
5d21287a-0bce-5c38-a159-cd6673bf2998 | button | I have attached Evidence of Engineering Certification | Yes,No
d80834eb-8560-5715-b772-28441493f097 | button | I have attached Evidence of 3rd Party review of engineering | Yes,No
92ddcd9e-8e9b-5040-844d-c86a13562740 | signoff | Signatures
1f273173-0067-5218-b64d-d42df9bfeef4 | checklist | POLICY-005 Safe Work Procedure |  | POLICY-005 Safe Work Procedure
90e555f1-b7db-5342-8f6e-ab9bb0160482 | checkpoint | Task Details
11147022-6721-56f6-a341-42a8667feacd | note | Use this form to record your safe work procedure after analysing a particular task in your workplace.
3dcb34c4-4622-5088-9315-78cb15cddf61 | textbox | Work Area:
9c6b333a-b6ab-5b2b-a268-9a44d130f721 | textbox | Task:
a07d5aeb-3931-5bf4-b28b-b56f7df3c56d | textbox | Safety Risk: e.g. electricity, moving parts, noise
73bf96f4-9e1e-51a1-a557-4789936e6b2d | checkpoint | Personal Protective Equipment (PPE)
a319c4b2-bead-537f-874f-dabd819d84b1 | note | The following PPE must be worn, and precautions taken, when doing this task:
f838646f-2b74-5f7d-9c64-71b3158847df | tickbox | Work Gloves
8ec737f6-8ca8-551f-ae67-d046461bd280 | tickbox | Safety Glasses
3796683b-8e50-5b26-b0a2-b313a928a319 | tickbox | Steel Cap Boots
54c07798-b37d-586e-ac12-2b45b69df156 | tickbox | Ear Protection
7667fceb-3563-5c54-bcb0-0da4e36bbe38 | tickbox | High Visibility Vest
9c9b5140-0f92-54e2-bd6c-7774925392db | tickbox | Head Protection
eeaa94ff-b6fa-5971-8231-810933fbc339 | tickbox | Respiratory Mask
160ec2c1-8286-5856-bbb5-be6272c5026f | tickbox | Face Mask
92b6cca2-6bfc-51b1-aa9b-d9a6528df6d1 | tickbox | Protective Clothing
2839a8d2-a268-5fd6-bbb4-d52134b54727 | tickbox | Wash your Hands
cc546369-bca4-51b6-ab24-8e4406ba760e | checkpoint | Supervisor Signoff
4570fb2e-7310-5ac1-a58f-8ade9076d7c2 | signoff | BY SIGNING I CONFIRM I HAVE APPROVED THIS SAFE WORK PROCEDURE
3769d9ae-213b-5a91-94c1-062c3a51b036 | checklist | REPORT-002 Hazard |  | REPORT-002 Hazard
8111ace1-1386-5c1f-8290-3df28e3c8d3f | section | Details
7016619e-d9e9-575d-a598-04fc8176f882 | checkpoint | Hazard Report
9dfa438c-a6a0-58f7-a04e-74af131a650d | note | GM Fire employees shall complete a Hazard Report in the event they identify a hazard that may result in injury or incidents to person(s), property/plant, the public or the environment.
5fa49736-b36b-5338-89cc-b0c2e304a410 | note | The principal contractor will be informed immediately and provided with a copy of this report.
423d5ed9-def2-5985-8cad-6c2afa7e0d08 | checkpoint | Hazard
0ab9b796-c329-57c4-97a6-a378254b691c | textbox | What is the hazard?
e23dd611-f6df-5b35-a2ee-6c2f1af58ca8 | checkpoint | Contributing factor
495a5107-6085-52f1-842b-98b8d46ed834 | note | What are the contributing factors?
bfbb8ce9-9367-57c5-8b37-f1043661e9dd | tickbox | Environment such as noise, slip or trip
9d902241-0455-5bf0-8a45-9a3e271d090c | tickbox | Equipment/ materials i.e. wrong or inadequate
f30b96c3-2868-52c0-a677-906125de9f86 | tickbox | Work Systems i.e. inadequate training
89164cae-d255-560b-abb6-a3f30500b1b9 | tickbox | People i.e. production pressures, lack of communication, lack of procedures
0bcd8ba5-289c-5a20-a9e9-00a000866a68 | tickbox | Other
4d3ee642-573e-5e43-a4b1-18a8dff61014 | textbox | If 'Other' please specify:
5b8936dd-da50-5d1e-a2b4-e9a5b6b57cc3 | checkpoint | Corrective Action
2edb5515-0d62-5970-bf6f-9c5e3f8b1b89 | textbox | What are we going to do to fix the problem?
862da25a-c346-5e2b-a408-c21f132cbe42 | textbox | Who
accca31b-de0c-5d04-91d1-ad0c35e310d0 | textbox | When
09c0367c-9df2-5a1e-b57f-ce79d5be231a | checkpoint | Completed By
e8cad4f8-a779-54c4-8306-b65b38b7a52b | signoff | Signature
c8f83d37-ad60-5949-bb44-a66aca000fb1 | checklist | REPORT-003 Chemicals Review |  | REPORT-003 Chemicals Review
8111ace1-1386-5c1f-8290-3df28e3c8d3f | section | Details
9b472503-a221-4509-87b1-5097c7d20aad | checkpoint | Details
3cdd2383-24c8-55c7-bfac-edd7327dabcb | date | Date:
cff6026d-ea93-51af-89cb-f716e489f52c | textbox | Time:
eefd7d21-c3a8-5249-9155-dcea38b4b61b | checkpoint | Existing Register
0eeead6a-359a-5917-b6ea-6623882315a0 | date | Last Revised on (date):
5d3bb453-e9cd-57a0-a8c0-af548b64aea2 | note | Upload a photo of the "Register-006 Hazardous Chemicals" as it is on site today.
586de132-0677-5158-8fb0-c38150ef6201 | checkpoint | Chemicals on Site
99864ea8-7c01-5840-9f3d-2f215538f330 | textbox | Location where Chemicals are being stored:
a889dcc0-5345-51df-a02f-38fb69ebd9e3 | note | Upload a photo of each Chemical on site
8cbd2a0e-3c28-53bd-b9da-5a65540b2443 | checkpoint | SDS
c7fb5958-5380-57c9-a76f-9aae809e7f70 | button | Have any of the SDS sheets expired? | Yes, No
da6c4fe4-f7cb-588c-8a76-7c95476e2fff | note | If 'yes', cease use of Chemical and contact GM Fire Management immediately.
d1c99c34-3923-5138-8d73-bce227637e15 | note | Upload a photo of ALL Safety Data Sheets (SDS) on site.
58bfb4fd-b3d4-5f94-a67a-e067a225bcd0 | checkpoint | Declaration
27ce2233-485b-574f-a842-2d66969a0bf9 | button | All Chemicals on site have been approved for use by the Principal Contractor | Yes, No
f8c4ba68-2411-579c-ae4f-072cd46d22b3 | button | All Chemicals are stored securely | Yes, No
6ad6b62a-f02e-5599-bff0-bd3a4591509f | button | Any Chemicals that are no longer required on site have been removed and or disposed of as per WHSE guidelines | Yes, No
0da0ee29-0ac0-5051-ad4a-3e439a9e4b19 | signoff | BY SIGNING I CONFIRM I AM THE REPSONSIBLE PERSON FOR HAZARDOUS CHEMICALS ON THIS SITE, AND THAT ALL INFORMATION I HAVE PROVIDED IN THIS REPORT IS CURRENT AND TRUE.
42c7df9a-ccb8-5d7f-9abf-a956b1f84163 | checklist | REPORT-006 Incident Investigation |  | REPORT-006 Incident Investigation
8111ace1-1386-5c1f-8290-3df28e3c8d3f | section | Details
6412ac75-35b3-555b-a89e-87d89553cfa8 | checkpoint-no-value | Incident Investigation Report
26c7a877-82ff-5d4d-9964-4e831bec896a | note | GM Fire shall complete an Incident Investigation Report in the event of any injury involving medical attention or off site treatment or in the event of any incidents involving a near miss, property/plant damage or injury to the public or the environment.
c7009061-5139-5526-a062-83adc69dbabf | note | The principal contractor will be informed immediately in the event of the above. Following discussions with the principal contractor, a decision will be made as to who will conduct the incident investigation. The principal contractor will be provided with a copy of the completed Incident Investigation Report.
0bb42031-c4a8-5bcf-80ff-6fc5304ee4f4 | checkpoint | Class of Incident
319b1c6b-9f44-55ea-b16c-b1a07631b0a3 | tickbox | Injury
0adde8bb-4f35-5400-993c-c7d0180c2af2 | tickbox | Property/Plant Damage
621668cf-7542-5404-a731-45e940e7d4ee | tickbox | Near Miss
95d75d3d-669b-5354-b3b0-96b4a129a1c0 | tickbox | Environmental
67776edd-303c-58ed-b6a4-4c93c3ad56de | tickbox | Other
c5515547-5acf-5223-adaf-ff810432bbba | textbox | If Other - Please explain
e433ee97-85b5-52fa-97a9-25ca60ea13bc | button | Reported to Princpal Contractor | Yes,No
857bb4fc-18cf-5306-a76e-802c247b752f | textbox | Details:
e1d07f73-ecd2-514f-8842-5a2e0effd57f | button | Further Action Required | Report to Authorities,Other
820f14d5-50a0-5c15-96c5-71e6e32d06c6 | textbox | If Other - Please explain
bc36afa9-00da-5f53-99b5-0b99d61a7935 | checkpoint | Details of Incident
92284681-efd2-53d4-8e0b-d46de0d7e437 | date | Date of Incident
673f8d24-ff72-5e07-b453-93880d52a9f4 | textbox | Time of Incident
325ed646-43a2-5fc3-9425-0bef6e03fe7f | button | am/pm | am,pm
4b70799d-acc0-5966-a907-0ef28ba3f126 | textbox | Witness Name
541505a5-4428-5a09-a1c7-efa380a6cf43 | textbox | Witness Contact
fdfff4a4-8f76-588d-97bd-e1944521b0f4 | textbox | Nature of Incident
725a55af-18c7-57c8-afe2-bfa092de1b6a | textbox | Location of Incident
3f3be10a-9abd-53e3-82f0-2667d7e71aa8 | textbox | Description of Incident
b482344c-2e6d-577b-9ddb-70e3d053f88b | textbox | Details of damage to equipment/property?
5acc9a29-5ef8-55dc-93ab-9320efe0254e | checkpoint | Injured Person/s (if applicable)
24e6a102-3cb8-5740-9562-2f6fcc5871ca | textbox | Name
c68b8d90-60e8-5111-8e35-d7857559c628 | textbox | Address
e678a59a-6b1f-5756-b6cf-2d17da084cb1 | date | Date of Birth
66d64f8b-744b-59a5-8649-41a77a1b3902 | textbox | Occupation
f3631539-86a5-543a-ad2e-dad8be5e4b52 | textbox | Employer
df6586a3-039d-5599-8263-333b90fa2c9b | textbox | Referred/transferred to
2653d5b4-f6f4-5d10-b061-5710923ec319 | section | What factors contributed to the incident?
673b3686-24cc-52e8-a200-da491c74d4d4 | checkpoint | Environment:
5bebb027-96f0-5460-890a-132a143a47e3 | tickbox | Noise
5e04e3c6-c511-54d9-855b-61b79ba33d83 | tickbox | Layout / design
be7367f6-b65c-5e31-9806-b57e064484b1 | tickbox | Lighting
b344a257-3875-58bf-9242-ae1b70d9c52a | tickbox | Dust / fume
c1b98094-8764-57ae-8d8f-23524f9f5e83 | tickbox | Vibration
c6079cb7-cfed-539d-a3de-4ffe5242c1a5 | tickbox | Slip / trip hazard
85c76db0-7b13-5e0b-b320-9a0f6543aa2d | tickbox | Damaged / unstable floor
1e95cef6-f5ed-5510-89c5-ba7214c48c16 | tickbox | Other
7af769cf-fdc6-5763-a34f-36b7668432b1 | textbox | Other (if applicable):
da263eea-7753-5dda-9253-36aae5136ab1 | checkpoint | Equipment/materials:
fe1e78dd-509e-5b53-8078-3c13e8d0020a | tickbox | Wrong equipment for the job
48449b5b-94f5-56fd-aa68-28179f2a1234 | tickbox | Equipment failure
34dbaa91-66eb-5b35-86e6-12b7080c0add | tickbox | Inadequate maintenance
340c7cf0-23ea-5aaf-be3e-08341656325a | tickbox | Material / equipment too heavy / awkward
d44177e4-2535-597e-9309-931a3a8d12ee | tickbox | Inadequate guarding
3d7d49b4-0c2b-5d53-bfdc-aa67787549d7 | tickbox | Inadequate training provided
000690e7-a449-5a80-a869-a79c71c27c48 | tickbox | Other
e2a3d872-b06f-56d7-868a-7dfc157a60c7 | textbox | Other (if applicable):
29bb93fe-1a56-5a6a-a4d8-caafbdc08848 | checkpoint | Work systems:
5dd9bf85-df05-50a5-9d39-ba8c92524aee | tickbox | Hazard not identified
2fbf68fc-22c1-530f-9cb2-b87b25344ca7 | tickbox | No / inadequate risk assessment conducted
0387a054-0cba-5d62-97d1-4479ebe8b41d | tickbox | No / inadequate safe work procedure
d37a698b-994a-54ae-81f2-b04aa7a1df63 | tickbox | No / inadequate controls implemented
c6ba7810-1a06-5766-8b22-30f4fdc6cfd1 | tickbox | Hazard not reported
8f15171b-ea63-518f-a1d3-40a0cdb8bb86 | tickbox | Inadequate training / supervision
22ddaef3-e684-5031-82f2-eabc39055e20 | tickbox | Other
df7a8e40-28bc-528b-b28a-0b6efe49c3d3 | textbox | Other (if applicable):
13eb0e36-06f7-5153-ba71-5b36d7104644 | checkpoint | People:
68c29607-73a8-59a9-918a-e8a1a7758f3b | tickbox | Procedure not followed / no procedure exists
f49a9eb6-f469-5486-a041-424512d20bb0 | tickbox | Drugs / alcohol
315224a4-528b-59d0-b752-048abb08d4dc | tickbox | Fatigue
2ed0f27c-86d8-5e84-a4f2-361debecd863 | tickbox | Time / production pressures
1cf8af67-af67-5409-bca2-d1a6cdab08ea | tickbox | Change of routine
91dc8070-c2b8-5f0c-bd24-be694c6f87a7 | tickbox | Distraction / personal issues / stress
06712e9c-8051-58f7-8676-16be7955cabe | tickbox | Lack of communication
feefc030-bfe5-5354-a12e-104f9508da2b | tickbox | Other
c3685b47-7234-5973-bc9c-d337e162b8f6 | textbox | Other (if applicable):
1c21ef12-b1aa-5192-a53b-a50ba28212cd | section | Corrective actions:
e23dd611-f6df-5b35-a2ee-6c2f1af58ca8 | checkpoint | Contributing factor
34fb92e3-cc81-5b39-9cc4-3570d31ea806 | textbox | (from above list)
73874509-bac9-555d-8853-d738436ac006 | textbox | What are we going to do to fix the problem?
da26fb44-6d60-52fb-870e-90b8c5ffd716 | textbox | Who
f5d8b083-01e8-5841-aea1-53e16258b921 | textbox | When
585d5a57-d317-5a2c-8c86-399f10c406d3 | date | Completion date
09c0367c-9df2-5a1e-b57f-ce79d5be231a | checkpoint | Completed By
11f31f0b-4a44-5a8b-8133-2e07b430d536 | textbox | Name
9346513a-1500-5fae-b25b-d6e769dd31d7 | textbox | Position
40b6d092-dcdd-58fd-840d-c4a54e7f5c2d | date | Date
e8cad4f8-a779-54c4-8306-b65b38b7a52b | signoff | Signature
9b5ba583-05dc-5180-af78-f80a73b4a3b9 | checklist | REPORT-010 Request Corrective Action |  | REPORT-010 Request Corrective Action
8111ace1-1386-5c1f-8290-3df28e3c8d3f | checkpoint | Details
b3f79cef-26af-5621-a651-c23a0a72b9a0 | date | Date:
78d0eeda-4657-54ac-90db-75ab1e2ad22c | textbox | Time:
94eb6c20-0725-5d9d-a965-dae1c8b22a56 | textbox | Location:
be57c9f6-9a0b-51be-9cc3-9d4ec8b20a01 | textbox | Supervisor Name:
d5aaa5eb-093f-5332-af20-a8b65033877e | checkpoint | Corrective Action Report
8ba6567e-d8ee-50f3-a245-87becadd26f7 | textbox | Principal Investigator
faf22afb-f5db-55a2-9add-59b26e1ec56c | note | Non-Conformance is:
72587bce-48cf-5ce5-becf-e3f37a4ee637 | tickbox | Minor
db4f6a5c-56ef-53c3-aa3e-93a5fb0fd8da | tickbox | Major
f47a8bf7-76e0-5ad1-ae79-03d0b72856e3 | tickbox | Critical
20347967-523f-5e9c-b424-bc75c105227d | textbox | Details of Non-Conformity Identified
be6476b3-e89f-5683-aaa1-cfc9a60805a6 | button | What is the likelihood of Fatality? | Very likely, Likely, Unlikely, Highly Unlikely
a7f4be5a-6690-5562-8b35-21cca5645009 | button | What is the likelihood of Major Injuries? | Very likely, Likely, Unlikely, Highly Unlikely
6cc88732-fcca-5425-81dd-e8190bb25dfb | button | What is the likelihood of Minor Injuries? | Very likely, Likely, Unlikely, Highly Unlikely
f99c34a4-7c62-5099-b2f6-e17cb7afb9d5 | button | What is the likelihood of Negligble Injuries? | Very likely, Likely, Unlikely, Highly Unlikely
167f470a-4eca-5d5c-800f-10fd32059b87 | note | Add photo evidence if applicable.
5d294295-86ae-51e1-92b2-e35eee764d2a | checkpoint | Corrective Action Plan
399240b2-6f5d-5b11-83ae-d2b6eaee99e3 | textbox | Describe corrective action
7905cbb3-a6f9-5c73-8363-90bc6ed2675e | textbox | Is this plan permanent or temporary? | Pernament, Temporary
2db69516-fa06-5ebf-91e9-b77b8ed7ccb0 | date | What is the proposed completion date?
42c21dbd-9bff-5051-bd1f-f936237b2320 | checkpoint | Signoff
2923664c-ab55-5c48-87d4-1901f7c5ef27 | signoff | BY SIGNING I CONFIRM I HAVE COMPLETED THIS REPORT TO THE BEST OF MY KNOWLEDGE
bb4ab48c-d4ce-5ac0-8069-c58ccfa71d0c | checklist | SYS - ASSESS-004 Plant Risk |  | ASSESS-004 Plant Risk
8111ace1-1386-5c1f-8290-3df28e3c8d3f | section | Details
5011c755-395d-598c-bc65-ea69efabb143 | checkpoint | 1. Competent Peron(s)
2b55821f-6b88-5c3a-b5d5-d9d3f82fd37f | note | This familiarisation checklist should be completed by a Site Supervisor or Site Foreman to verify that the workers involved in the operation of Plant Equipment/ Mobile Elevated Work Platforms (MEWP) can demonstrate their ability to understand and operate the MEWP functions in accordance with the manufacturers operating manual. This familiarisation checklist must be verified by a competent person who holds the equivalent licence/ ticket required for the type of Plant Equipment/ MEWP to be operated (e.g. Boom lift/ Scissor lift)
53157e79-f882-521b-9f6e-7f47e6114202 | textbox | Your Name:
ad8bb218-875f-521c-8815-e5e20e419b9a | note | Your Licences / Tickets:
307d4c9d-09ad-5247-b649-397ed25f84de | tickbox | WP High Risk
f45c4e63-765c-5f62-89f0-7fe543db8f4f | tickbox | Boom Lift
894b6192-c805-590d-910b-3489537d3b45 | tickbox | Scissor Lift
e5031a76-2d00-560f-897e-124fef2d0e0d | tickbox | Vertical Lift
2ba6e153-65f7-5a17-bdbc-2a4357f88228 | tickbox | Other
8b905508-63e7-53a2-9c6f-e04b789fd42f | textbox | If 'Other" please specify:
c06fe721-a6e8-585c-ad93-6752e11d8265 | checkpoint | 2. Plant/ MEWP Details
0a7d6b15-e23a-56f9-98be-25e98e392dd6 | textbox | Make and Model:
a2c3be77-953a-5274-b0b7-6e95098724b2 | textbox | Type (e.g. BL>11m, BL<11m, SL, VL):
6b0e5610-cf37-5886-aa78-b8bc2aea3ba0 | checkpoint | 3. Employee Competency
3d3d4b83-23d0-543c-8fc4-7ca914948de1 | textbox | Name:
77d8c00c-ef60-5f5a-b71c-8d8a812d96cc | note | Role:
c85b51f0-ade7-594b-a9e0-d3200c6c6cda | tickbox | Operator
0ac29beb-ac4a-5723-845d-a02a09373a16 | tickbox | Spotter
83a8e82c-86b3-5a07-95aa-3e3e655a1338 | note | Licences/Tickets Held:
fd0e6240-4050-50b1-bd40-eb63f3c07997 | tickbox | WP High Risk
912ef621-b311-5c38-b5a2-3496bc7c3b45 | tickbox | Boom Lift
236303f8-4905-5cf5-908c-3b6676e7c864 | tickbox | Scissor Lift
c6f5475d-3689-5ebc-8d57-de885bb4cbc1 | tickbox | Vertical Lift
06ebc66d-119e-58a4-8c6d-3668b83861ad | checkpoint | 4. Employee Competency
70fe390c-bf94-504e-a1f2-94eb9f458898 | textbox | Name:
814c2b7f-742b-5deb-b247-cc1e676d4ea3 | note | Role:
4f7278e9-0c1c-5a2a-bfee-019abe2b4d71 | tickbox | Operator
86648e43-f143-5d1e-9594-afa33b6f79e3 | tickbox | Spotter
d12bed5d-50d2-598b-a2b8-069e2c6430ac | note | Licences/Tickets Held:
3d1562f8-d84a-5083-ae80-02b3595a50a0 | tickbox | WP High Risk
70722709-3493-51d6-ad90-7a6c2e402a4e | tickbox | Boom Lift
ac522710-5f5c-5555-b776-215c73dbe06a | tickbox | Scissor Lift
ce7d3c69-5e1c-53a0-a73d-88c0842f3d78 | tickbox | Vertical Lift
3ef8e758-7384-5d13-8fa3-292a5f04a9d8 | checkpoint | 5. Employee Competency
c8f2048d-f9ca-55d3-98be-fe0b7abfa06e | textbox | Name:
a3f61bec-c909-54b4-be69-8e44fd85bb2a | note | Role:
5ba35dcb-ffc1-5a79-85e8-ac1ba2aa24b2 | tickbox | Operator
778cd0b4-6a1a-5208-9604-d51d8e49f9f7 | tickbox | Spotter
dc4e7913-25b5-5c3f-906a-d9d02286b1db | note | Licences/Tickets Held:
eb150c55-b3f5-5de7-a5c5-aa628364441a | tickbox | WP High Risk
3b883298-8e77-5ee0-926d-c1e8b3853685 | tickbox | Boom Lift
7ebbd69a-fd4a-5d6b-b11d-365234cc09eb | tickbox | Scissor Lift
fc81307b-cfae-5aed-81e0-279357e30e48 | tickbox | Vertical Lift
0db35e59-5266-54bd-bc6b-7ababdb43cef | checkpoint | 6. Declaration (to be completed by competent peron(s) noted in Section 1.
5d244105-8188-52f5-bdd2-6ba550ee1ade | button | All 'Operators' hold the appropriate licence/ ticket for Plant/ MEWP | Yes, No
caed7594-fe47-5a6d-8fac-07fb289cacc5 | button | All 'Operators' understand the operational controls and emergency functions | Yes, No
1aec6383-16de-5ba8-9dae-61cf2958e67f | button | All 'Operators' are aware of the logbook and pre-start requirements | Yes, No
402e7045-85dd-5d4e-a34c-db2016776789 | button | All Ground Support understand the emergency functions | Yes, No
c3cbebab-a46a-5ef4-9071-8ebe474b8a1d | button | All GM Fire employees on site have participated in an emergency drill | Yes, No
6823091b-1043-5128-b7fd-bbed62caec4d | button | All GM Fire employees have signed onto applicable SWMS | Yes, No
9899d9ec-b306-5aed-bbc5-b1347ea6537c | signoff | BY SIGNING I CONFIRM I HAVE ALL PERSON(S) LISTED ARE COMPETENT TO OPERATE THE LISTED PLANT/ MEWP ON THIS SITE.
bb61ac93-b8dc-50ca-a15e-597c83587356 | checklist | SYS - REPORT-003 Chemicals Review |  | REPORT-003 Chemicals Review
8111ace1-1386-5c1f-8290-3df28e3c8d3f | section | Details
7b60f568-7566-40fe-9109-643751056982 | checkpoint | Details
7b5b24bb-03b7-5a3d-86e1-d430a8767da3 | date | Date:
b3fb7472-3895-5fe6-a664-0ba07777ee11 | textbox | Time:
eefd7d21-c3a8-5249-9155-dcea38b4b61b | checkpoint | Existing Register
87833c0d-601e-56c1-9c55-3c2585d45cea | date | Last Revised on (date):
0d12fd67-bcc7-5a2d-8083-a746ffe97d71 | note | Upload a photo of the "Register-006 Hazardous Chemicals" as it is on site today.
586de132-0677-5158-8fb0-c38150ef6201 | checkpoint | Chemicals on Site
1607c03b-70c6-5ab0-9b82-99811f48640e | textbox | Location where Chemicals are being stored:
8e0bcecc-6715-5e2e-bfa2-5e2c98a2d0a0 | note | Upload a photo of each Chemical on site
8cbd2a0e-3c28-53bd-b9da-5a65540b2443 | checkpoint | SDS
83912bc1-9904-5442-a5c7-9526c3c9f807 | button | Have any of the SDS sheets expired? | Yes, No
dc7fec34-6d7f-5977-8ac0-4c0207dd87fb | note | If 'yes', cease use of Chemical and contact GM Fire Management immediately.
b33ed948-57df-574c-8ebc-ceb70dc2063e | note | Upload a photo of ALL Safety Data Sheets (SDS) on site.
58bfb4fd-b3d4-5f94-a67a-e067a225bcd0 | checkpoint | Declaration
b5c5721a-757c-563c-8524-a2b72d0deb62 | button | All Chemicals on site have been approved for use by the Principal Contractor | Yes, No
de6801c9-5807-5bb9-bf75-75a642a9fe2e | button | All Chemicals are stored securely | Yes, No
ad3bb911-e14d-5745-8cc9-13b8f2b72c0f | button | Any Chemicals that are no longer required on site have been removed and or disposed of as per WHSE guidelines | Yes, No
0da0ee29-0ac0-5051-ad4a-3e439a9e4b19 | signoff | BY SIGNING I CONFIRM I AM THE REPSONSIBLE PERSON FOR HAZARDOUS CHEMICALS ON THIS SITE, AND THAT ALL INFORMATION I HAVE PROVIDED IN THIS REPORT IS CURRENT AND TRUE.