## Master List Templates
Id | Type | Name | Values | Prompting Name
87dbf723-3c96-462d-bf66-e455fedf5f06 | checklist | ITPS-209 Deluge Commissioning |  | ITPS-209 Deluge Commissioning
8eea13d2-6902-4b58-986a-3c9ed55875f7 | section | Details
7817e386-1f03-4300-b563-044adf24669d | checkpoint | 1. AREAS PROTECTED
0f26962a-7b53-515d-b6b3-22f5c1ae0bbc | note | CIBSE W5.2 State of the System
f6c8df84-0587-588f-a3c6-5fb3d4f3a162 | note | AS2118.3
579b67c5-1d15-5b2f-bfaa-4893198ed8bd | button | Have you ensured areas protected do not exceed 300m/sq per valveset? | Yes, No
69a0a452-eee7-5400-b4c3-1d18d8f626f5 | note | Add Photo
e13b2f41-965d-47fe-b293-b669ac827608 | checkpoint | 2. PRESSURE TEST
b77b8a3d-9734-5cad-b586-4c6c8f11065c | note | CIBSE W5.4.1 Pressure Testing
b5dd3634-0e61-5e2b-a53d-78f9fd902b38 | note | AS2118.1
088ba1e8-65f5-5bab-b519-e8d61450a0f6 | button | Have you completed a pressure test as per ITPS-203 for each deluge system? Note: Where open sprinklers are used ensure all heads are plugged prior to pressure testing. | Yes, No
b4e01887-62fb-5ccb-9378-5e7c57b095e0 | note | Add Photo
1ae11dd8-82e8-4a6a-9c03-a5c7b3ce35dc | checkpoint | 3. EQUIPMENT TESTS - SYSTEM FLUSH
728f2aca-b05d-5e3e-89ac-d818871303ea | note | CIBSE W5.5.2 Flushing Procedure
0851b159-f1c6-5973-977a-cb3586eb9363 | note | AS2118.1
543b63ae-49e1-55ad-b2ff-593c4e0fb7af | note | Complete the following PER valveset and open sprinkler head:
ec26301e-47b5-50d4-972e-b4d24505bd78 | note | 1) Flushing of each open sprinkler head to ensure debris is removed.
9c12745e-e70d-59ce-abb7-ac762de00e99 | note | 2) Setup filtration mesh and water bin at each open head off each system (is there are a large number of heads then separate system by plugging each head).
1903c679-9e94-5e4a-8788-0686e90ca55f | note | 3) Let water flow through pipework onto filtration mesh
29b7d2ca-0540-5357-b85d-d2214726c8f2 | note | 4) Once water is clear from debris shut off water and return system to normal.
79de03cd-4a66-53e9-a70f-2b83859bb91b | note | Take photo per deluge head and record deluge head/s location:
c62db6fb-5360-49e9-b201-c73c7170ea52 | checkpoint | 4. TRANSIT TIME TESTING
c61592c5-2057-5eaf-873e-fdc3c8791cd9 | note | CIBSE W5.6.2 Mechanical Checks: Automatic Control Valves
655f698f-f7f9-5633-8f34-22bd130f6610 | note | AS2118.3 Cl 2.9.1
dca9d2ad-e275-576e-b1fe-5f22044bf59a | note | Complete transit time testing
24da5ecf-6c2c-59bf-886c-e935fd082ba3 | note | Test of the deluge valve to ensure the transit time does not exceed 30s from the valveset to the remote deluge head.
ca7a5928-1b84-55d6-9e89-7a1559ca7660 | note | Add photo of results of transit time.
3a04b841-ac9a-4574-b21d-5e715db680a8 | checkpoint | 5. RETURN TO NORMAL OPERATION
0a93862e-2b51-5279-931c-3b3f60087f9c | note | CIBSE W5.6.2 Mechanical Checks: Automatic Control Valves
83d068c2-f166-5a5a-950f-7dba0ba9b53f | note | Are all open sprinkler heads re-installed where previously plugged?
eb006e7b-ed6a-56f8-8e5a-e7b3b4e19414 | note | Have system valvesets been returned to normal condition (or approved condition where construction still occurring)?
b0c22b87-45d6-5de6-a6c7-d46ea7ff4bc3 | button | Have water filled bins been emptied as per principle contractors requirements? | Yes, No
e3e5c507-051b-5c83-9f98-b95a7e82ef8d | note | Add Photo
f4e4ad9b-dd6e-4b4c-9955-2e35567b6483 | checkpoint-no-value | GM Fire Sign Off
8b042243-f6a4-4082-8826-804c333eb1ce | signoff | GM Fire Sign Off
44ef14c4-0907-4701-b770-28081a0f23f3 | checkpoint-no-value | Principal Contractor Sign Off
85d7a163-ece4-4347-b7b8-2cd6e059e22b | signoff | Principal Contractor Sign Off
287159ad-2b09-44b6-9445-76962cf3474e | checkpoint-no-value | Consultant Sign Off
0531c335-d3e4-4752-a6dc-20e7e02a75ed | signoff | Consultant Sign Off

## Project Checklist Templates
Id | Type | Name | Values | Prompting Name
c5dc7d7c-df99-5ec2-a589-b436df406a75 | checklist | 010SAF_08 SWMS |  | 010SAF_08 SWMS
a1c9d02b-1fdf-5e00-bcb7-56aeec761826 | checkpoint | 1. INDUCTION - Attach your signature to confirm you have completed the Principle Contractor's Induction.
d39621b2-57eb-545c-b19b-913b988ebada | signoff | By signing I confirm I have completed the Principal Contractors induction.
93e7a6a9-2417-5a63-a628-5bbbe7c40d86 | checkpoint | 2. ALL STAFF
cbaa5304-d926-5145-abea-643403fc7075 | note | 003G Using Platform Ladders
4c0dcfe7-d8a0-5008-bd8b-d7bc54f1ac2a | note | 004G Inhalation of Respirable Crystalline Silica
1117a6d0-9a4c-5b98-b403-d22a7b5ad3a6 | note | 005G Working at Heights
68979298-f5d8-548e-baec-8741d208ed87 | note | 006G Working at Heights Rescue Plan
1e1b9f0c-d012-59f5-9748-6f1fbc413551 | signoff | By signing I confirm I have read and understood ALL the SWMS documents listed above. I have reviewed these documents onsite with my supervisor and I have signed the hard copy.
d3e29984-ceb2-515c-9230-7a6de1161462 | checkpoint | 3. WET FIRE TECHNICIANS
b4e0d11c-383a-5193-a4d8-06886c652d7b | note | 019T Pressure Testing of Pipework
543f3f86-57b8-5b16-b786-9b1a07dba3bc | note | 020T Sprinkler System and Associated Pump Test
e8307916-4807-52bf-87e5-102669e43c3f | note | 021T Hydrostatic and Flow Testing of Pipework
b9ed5514-0cad-5767-9bc2-787d09c4b91b | note | 022T Fire Rating
3eda0a35-e17c-5ffa-8f13-550cbe45fa28 | note | 023T Fire Alarm and Emergency Warning Systems Testing
6a966737-d7b0-592b-adaf-4fd6c5c1ce28 | note | 024T Commissioning and Testing of Hydrant System and Booster Area
ec96f917-5f59-57b4-b51e-789fed1bc3e7 | signoff | BY SIGNING I CONFIRM I HAVE READ AND UNDERSTOOD ALL THE SWMS DOCUMENTS LISTED ABOVE. I HAVE REVIEWED THESE DOCUMENTS ONSITE WITH MY SUPERVISOR AND I HAVE SIGNED THE HARD COPY.
cb6326be-0982-5008-a0f6-df63d2b7f5a8 | checkpoint | 4. SWMS - DRY FIRE TECHNICIANS
5d11d398-a985-5a6c-aeb6-18ee293dc7c2 | note | 008I Removal of Existing Fire Alarm Systems and Devices
92d6eeb4-8277-5022-83a0-fc89644f8bed | note | 009I Removal of Pipework Fittings
52103321-2daf-5ff5-83c8-2ade86fd2490 | note | 010I Fire Alarm and Warning System Rough-in
8205c84e-07ea-575b-bae8-d3015acb0b02 | note | 011I Fire Alarm and Warning System Fit-off and Installation
884a1c0d-249f-5a69-b8f2-2e03f9760652 | note | 012I Installation of Fire Alarm and Warning System Cabling
61c0ba51-1491-512b-936c-ac2c0f143740 | note | 013I Installation of Pipework and Fittings
c29e79e2-249c-55ba-b869-187073053c35 | note | 014I Installation of Fire Control Panel & Emergency Warning Systems
12c89be3-5c80-51bc-be0f-9f94b3c520b4 | signoff | BY SIGNING I CONFIRM I HAVE READ AND UNDERSTOOD ALL THE SWMS DOCUMENTS LISTED ABOVE. I HAVE REVIEWED THESE DOCUMENTS ONSITE WITH MY SUPERVISOR AND I HAVE SIGNED THE HARD COPY.
8b3b509a-75aa-5bb4-bf99-8e6b8d8e597b | checklist | 010SAF_08 SWMS - AIDP Ripley |  | 010SAF_08 SWMS - AIDP Ripley
8111ace1-1386-5c1f-8290-3df28e3c8d3f | section | Details
a1c9d02b-1fdf-5e00-bcb7-56aeec761826 | checkpoint | 1. INDUCTION - Attach your signature to confirm you have completed the Principle Contractor's Induction.
d39621b2-57eb-545c-b19b-913b988ebada | signoff | By signing I confirm I have completed the Principal Contractors induction.
93e7a6a9-2417-5a63-a628-5bbbe7c40d86 | checkpoint | 2. ALL STAFF
e10de068-098a-54e4-9ca5-367664a0021d | note | GM FIRE 001 Working with Elevated Work Platforms
15671497-ad54-5d32-afa4-04d3f3c4b7b8 | note | GM FIRE 007 Manual Handling
520f9407-d01a-5995-b868-f3de1b60147e | note | GM FIRE 008 Working at Heights
fd6856ce-5fcf-5581-a5f9-83f42ae44906 | note | GM FIRE 051 Using Platform Ladders
98e081c0-c0f2-5647-a6e5-e314220d57ab | note | GM FIRE 060 Inhalation of Respirable Crystalline Silica
1e1b9f0c-d012-59f5-9748-6f1fbc413551 | signoff | By signing I confirm I have read and understood ALL the SWMS documents listed above. I have reviewed these documents onsite with my supervisor and I have signed the hard copy.
d3e29984-ceb2-515c-9230-7a6de1161462 | checkpoint | 3. WET FIRE TECHNICIANS
12aa4e47-69ce-583a-99b5-9ec6063e0430 | note | GM FIRE 009 Pressure Testing of Pipework
68ec500e-a59b-5b0b-b97e-769b3dde3619 | note | GM FIRE 031 Sprinkler System and Associated Pump Test
f9b74e32-e4b3-583e-91f9-e7b3e7f28716 | note | GM FIRE 032 Hydrostatic and Flow Testing of Pipework
ec96f917-5f59-57b4-b51e-789fed1bc3e7 | signoff | BY SIGNING I CONFIRM I HAVE READ AND UNDERSTOOD ALL THE SWMS DOCUMENTS LISTED ABOVE. I HAVE REVIEWED THESE DOCUMENTS ONSITE WITH MY SUPERVISOR AND I HAVE SIGNED THE HARD COPY.
cb6326be-0982-5008-a0f6-df63d2b7f5a8 | checkpoint | 4. SWMS - DRY FIRE TECHNICIANS
96e187af-4508-5796-814d-edf71d430753 | note | GM FIRE 002 Wiring Rough In Minor
edf53965-a075-57b6-9e59-ee1f53c5eea8 | note | GM FIRE 003 Fit Off Fire Alarm System
6d09c463-be7a-5e4e-bf48-f312657a39db | note | GM FIRE 006 Installation of Pipe and Fittings
12c89be3-5c80-51bc-be0f-9f94b3c520b4 | signoff | BY SIGNING I CONFIRM I HAVE READ AND UNDERSTOOD ALL THE SWMS DOCUMENTS LISTED ABOVE. I HAVE REVIEWED THESE DOCUMENTS ONSITE WITH MY SUPERVISOR AND I HAVE SIGNED THE HARD COPY.
9e0279ff-7609-525d-9686-c77d8964a06d | checklist | 010SAF_08 SWMS - ODYSSEY |  | 010SAF_08 SWMS - ODYSSEY
8111ace1-1386-5c1f-8290-3df28e3c8d3f | section | Details
a1c9d02b-1fdf-5e00-bcb7-56aeec761826 | checkpoint | 1. INDUCTION - Attach your signature to confirm you have completed the Principle Contractor's Induction.
d39621b2-57eb-545c-b19b-913b988ebada | signoff | By signing I confirm I have completed the Principal Contractors induction.
93e7a6a9-2417-5a63-a628-5bbbe7c40d86 | checkpoint | 2. ALL STAFF
92bb9af3-0b3c-58d5-af01-dcaa3f0b56f9 | note | GM FIRE 001 Working with Elevated Work Platforms
16ddb0bd-0fc5-58c9-8947-d15f08b642d0 | note | GM FIRE 007 Manual Handling
5ed13011-b997-5fb6-859a-409c9dfd8397 | note | GM FIRE 008 Working at Heights
f233adc5-9ce8-5fa1-ae06-8bb9ae69b156 | note | GM FIRE 049 Working At Heights Rescue Plan
aa74eefc-fb81-571a-bef1-13ae5835d8a4 | note | GM FIRE 051 Using Platform Ladders
5194bef9-5c15-5d9f-861a-2f5c3e600e75 | note | GM FIRE 060 Inhalation of Respirable Crystalline Silica
1e1b9f0c-d012-59f5-9748-6f1fbc413551 | signoff | By signing I confirm I have read and understood ALL the SWMS documents listed above. I have reviewed these documents onsite with my supervisor and I have signed the hard copy.
d3e29984-ceb2-515c-9230-7a6de1161462 | checkpoint | 3. WET FIRE TECHNICIANS
c78fac4a-5239-5f18-9a7a-73a9ec3e70e6 | note | GM FIRE 009 Pressure Testing of Pipework
9f860354-0af2-5f62-ad21-86c78c194f74 | note | GM FIRE 031 Sprinkler System and Associated Pump Test
4fc9cf05-94c2-5778-94c6-e190eb249ca1 | note | GM FIRE 032 Hydrostatic and Flow Testing of Pipework
ec96f917-5f59-57b4-b51e-789fed1bc3e7 | signoff | BY SIGNING I CONFIRM I HAVE READ AND UNDERSTOOD ALL THE SWMS DOCUMENTS LISTED ABOVE. I HAVE REVIEWED THESE DOCUMENTS ONSITE WITH MY SUPERVISOR AND I HAVE SIGNED THE HARD COPY.
cb6326be-0982-5008-a0f6-df63d2b7f5a8 | checkpoint | 4. SWMS - DRY FIRE TECHNICIANS
de972ceb-44c7-57f4-b5da-0399766270af | note | GM FIRE 002 Wiring Rough In Minor
d9228552-ac2e-5900-8cc2-e99ea5a3530a | note | GM FIRE 003 Fit Off Fire Alarm System
9ba02a88-ad12-53e3-98b8-aa4b8159636c | note | GM FIRE 006 Installation of Pipe and Fittings
12c89be3-5c80-51bc-be0f-9f94b3c520b4 | signoff | BY SIGNING I CONFIRM I HAVE READ AND UNDERSTOOD ALL THE SWMS DOCUMENTS LISTED ABOVE. I HAVE REVIEWED THESE DOCUMENTS ONSITE WITH MY SUPERVISOR AND I HAVE SIGNED THE HARD COPY.
02820854-2b26-5b84-8a78-37944efc42b3 | checklist | 010SAF_08 SWMS - Wacol |  | 010SAF_08 SWMS - Wacol
8111ace1-1386-5c1f-8290-3df28e3c8d3f | section | Details
a1c9d02b-1fdf-5e00-bcb7-56aeec761826 | checkpoint | 1. INDUCTION - Attach your signature to confirm you have completed the Principle Contractor's Induction.
d39621b2-57eb-545c-b19b-913b988ebada | signoff | By signing I confirm I have completed the Principal Contractors induction.
93e7a6a9-2417-5a63-a628-5bbbe7c40d86 | checkpoint | 2. ALL STAFF
e5f4983c-79f9-5d2c-aa86-19628d97bca4 | note | GM FIRE 001 Working with Elevated Work Platforms
cb97e826-81ed-5498-a1ce-8026ccaa34ad | note | GM FIRE 007 Manual Handling
3b53ae2d-a214-5919-8837-5ff53a686f11 | note | GM FIRE 008 Working at Heights
ad6ae2e0-0d48-5ac4-ab38-827dbaaad25f | note | GM FIRE 049 Working at Heights Rescue Plan
addf5555-e97e-5e0f-a3ae-e0bdc7cb00d5 | note | GM FIRE 051 Using Platform Ladders
29dc9e88-4534-5045-931b-379ccf48318e | note | GM FIRE 060 Inhalation of Respirable Crystalline Silica
1e1b9f0c-d012-59f5-9748-6f1fbc413551 | signoff | By signing I confirm I have read and understood ALL the SWMS documents listed above. I have reviewed these documents onsite with my supervisor and I have signed the hard copy.
d3e29984-ceb2-515c-9230-7a6de1161462 | checkpoint | 3. WET FIRE TECHNICIANS
f1b0bb87-0310-5266-aeba-e3557c2bc226 | note | GM FIRE 009 Pressure Testing of Pipework
aeb50cbd-b592-59f9-889d-b43dcaf721bd | note | GM FIRE 031 Sprinkler System and Associated Pump Test
afab2c86-7bc8-5186-b3b3-7364105642c4 | note | GM FIRE 032 Hydrostatic and Flow Testing of Pipework
ec96f917-5f59-57b4-b51e-789fed1bc3e7 | signoff | BY SIGNING I CONFIRM I HAVE READ AND UNDERSTOOD ALL THE SWMS DOCUMENTS LISTED ABOVE. I HAVE REVIEWED THESE DOCUMENTS ONSITE WITH MY SUPERVISOR AND I HAVE SIGNED THE HARD COPY.
cb6326be-0982-5008-a0f6-df63d2b7f5a8 | checkpoint | 4. SWMS - DRY FIRE TECHNICIANS
c22eb604-a543-55e8-a9bc-009aa41cad12 | note | GM FIRE 002 Wiring Rough In Minor
f0a3092c-62a3-588f-ae43-2a09e0cbbfe5 | note | GM FIRE 003 Fit Off Fire Alarm System
666707d9-d1a3-5bb1-800c-46a33c145d82 | note | GM FIRE 006 Installation of Pipe and Fittings
12c89be3-5c80-51bc-be0f-9f94b3c520b4 | signoff | BY SIGNING I CONFIRM I HAVE READ AND UNDERSTOOD ALL THE SWMS DOCUMENTS LISTED ABOVE. I HAVE REVIEWED THESE DOCUMENTS ONSITE WITH MY SUPERVISOR AND I HAVE SIGNED THE HARD COPY.
b2707511-d95d-5bd8-9fe5-d7b1aeb787fc | checklist | ASSESS-001 Risk |  | ASSESS-001 Risk
8111ace1-1386-5c1f-8290-3df28e3c8d3f | section | Details
1c657631-910b-56b0-9af0-2d9a539b2537 | checkpoint | Assessment Details
2737dda7-0da8-5350-a990-3c75e95a2887 | note | Use this form to document the risk management process for a single generic hazard.
289128ce-f3c7-536a-8723-4c70cd69bfce | textbox | Work Area:
ae1c42b6-c657-5e4d-9209-2bad75870138 | date | Date of Assessment:
8a53b641-9f68-5989-8d44-4cf1ba1926bb | textbox | Name of Assessor(s):
caa8797b-e08d-52e2-8736-115154cf3705 | textbox | Position(s):
f6ba4789-5bd0-5594-9b1c-010bc61db611 | textbox | Incident Ref. No:
270f8fc3-f5f3-5606-80eb-fc2c80ae4f95 | checkpoint | Hazard Identification
68274c54-05ce-5ce6-86e9-ca232bb22a04 | textbox | Describe the Hazard:
bfd5195d-87aa-5c40-ac91-f0b3a6ea86bc | checkpoint | Risk Assessment
8a96e579-e757-52cd-aac7-c2595bbe497f | textbox | What harm could the hazard cause?
403ab9f6-98ce-5c66-868e-2679ce633da0 | textbox | What is the likelihood of this happening?
5bd4779e-96af-50dd-9f6a-99a1d0cdff0d | textbox | Persons at risk:
e51e81a4-bb38-5350-a32e-178abbc64320 | textbox | Existing control measure:
711cba2d-b126-5349-aaf1-f13b90a0bfe9 | textbox | Consequence:
df1c1362-d4be-51c7-97a0-196760254788 | textbox | Likelihood:
43c9bc56-3d31-5b6b-88d9-be99de6d3ef5 | textbox | Outcome:
32563b01-0feb-5e94-999f-2bc4f92e2c20 | checkpoint | Control Measures
26bc5138-30eb-58e0-9a12-54885a1212d4 | textbox | Elimination:
dc594457-3299-539f-8a27-727188b7aaf7 | textbox | Substitution:
809c790a-705f-5659-94a9-63c4e630e13d | textbox | Isolation:
a9c2b50c-045f-5fd6-bab9-52e76acc984a | textbox | Engineering:
fb6bc54d-9c0a-5f84-8964-f0f46bfd349a | textbox | Administrative or PPE:
e4d91219-de55-500e-ae36-937ccddb4ff0 | textbox | Preferred control option:
71245745-e635-5d28-b0f1-51a28405fcc8 | checkpoint | Implementation
ad41fa7a-48fb-500a-9607-b49a60e29f86 | textbox | Associated activities:
4534f779-9710-5858-94f9-d6ce7fef84be | textbox | Resources Required:
9ea6d005-499c-56f7-974b-aa0ef858cb30 | textbox | Person(s) Responsible:
52b2f865-6543-582a-bf9f-e8a527fb4846 | date | Scheduled Review Date:
7717528b-ba68-53aa-a357-393c48e0a282 | signoff | Signature
367c214b-499a-50a2-88bd-3efe1f2b2b50 | checklist | ASSESS-002 Manual Tasks Risk |  | ASSESS-002 Manual Tasks Risk
8111ace1-1386-5c1f-8290-3df28e3c8d3f | section | Details
1c657631-910b-56b0-9af0-2d9a539b2537 | checkpoint | Assessment Details
490c172b-529e-535d-95e8-e5ad2fb72267 | note | This assessment identifies how to manage the risks associated with hazardous manual tasks and control the risks of workers being affected by musculoskeletal disorders as per the code of practice under section 274 of the Work Health and Safety Act 2011 (the WHS Act). Use this form to help identify and manage risks of hazardous manual tasks.
ab900e56-77e5-5805-9997-0d1dfe555ee7 | date | Date of Assessment:
2aec5e0b-8872-5011-9421-48854f44e051 | textbox | Name of Assessor(s):
5e55219b-583f-56f3-bfdd-5dea292dd57c | textbox | Position(s):
e9a03c42-ce41-510c-81f9-6726eabba5a7 | textbox | Incident Ref. No:
58267725-2c6f-55fe-83b6-0579eb36ea4e | checkpoint | STEP 1 What is the Manual Task?
d8a88177-159b-582e-9b31-2a129c8d8287 | textbox | Relevant worker(s) to consult:
e232891b-c7c3-5c4f-8710-9e25a80167ba | textbox | Name of task or activity:
037244fe-8b0c-5516-b956-b112323b670e | textbox | Location where task occurs:
7ad89bb6-a5b4-5328-a0e3-bc256710943c | textbox | Who performs the task:
d3180965-d2b6-5838-8138-4fd1533da7f7 | textbox | General Description:
bf2b5766-0a58-58a5-9304-cb818f3230f5 | checkpoint | STEP 2 Is the Manual Task hazardous?
aab5e53a-b884-5772-9678-39989f5669f7 | note | Hazardous manual tasks can result in musculoskeletal disorders (MSDs) such as sprains or strains. Work through the following to determine which postures, movements and forces of the task pose a risk.
aea3be1b-890b-5d5c-a299-8bddf9f945cf | note | 1. Does the task involve any of the following risk factors?
2f77bbb9-7a7b-580a-810e-83fa27e840a9 | button | Repetitive movement | Yes, No
74ead498-3c45-5e04-ad4b-502bba13a14c | button | Sustained or awkward postures | Yes, No
fb28a310-8cb2-561e-bf72-d57a019c6402 | button | Repetitive or sustained forces | Yes, No
34214a95-3841-51a1-bf4e-63eb1481bc91 | note | 2. Does the task occur over a long time?
6c8da810-d8ee-5e6c-b376-44d52748c8ed | button | More than a total of two hours over a whole shift? | Yes, No
82340f3d-6d46-59a9-861a-14429e99d1e2 | button | Continuously for more than 30 mins? | Yes, No
9c3dad32-e3f8-5cd9-b455-e6d7311e5e10 | button | 3. Does the task occur over a long time? | Yes, No
a7af4a9a-52ff-5f1e-8dfd-0ce660580656 | button | 4. Does the task involve vibration? | Yes, No
125544aa-735e-506b-a178-319eeb48e499 | note | 5. Is there a Risk? The task involves a risk of MSDs (e.g. sprain and strain) if you answered ‘yes’ to either:
b5eda523-6c02-5219-b69a-213dd43893f0 | tickbox | Question 1 and 2 (above)
1b6414b1-311c-5add-b3eb-36ffeffa0a86 | tickbox | Question 3 (above)
56e36077-34d7-5a5e-aed9-15ce5695b159 | tickbox | Question 4 (above)
0cd16434-4ea6-590f-a9d8-22c8120046dc | note | If you ticked anything in question in Question 5, continue to Step 3.
08ad31b6-03ac-561f-942e-c8e3166bd958 | note | Additionally, if you answered ‘Yes’ to Question 4 the task may be a risk and will require further investigation.
43bb97fe-9131-5be9-be82-2660ffb39a19 | checkpoint | STEP 3 - What is the source of the risk?
8d1e9cf7-f475-53a5-90ab-16d167860176 | note | These are the things that are causing the risk and may be changed to eliminate or minimise the risk.
b73be6fb-033a-5d07-b7fe-3c85624d7282 | tickbox | Work area design and layout: workspace available; design of workstation, furniture and equipment.
33e5a4bb-1125-5f9c-9b67-c0ca918b214f | tickbox | The nature, size, weight or number of things handled in performing the manual task.
4b2e8d21-43fb-5539-8e97-b79a576d9999 | tickbox | Systems of work (e.g. pace and flow of work; resources available; maintenance).
68abb300-f394-5a9a-9ce0-557ece1da760 | tickbox | The environment in which the manual task is performed (e.g. flooring; obstructions; lighting; hot/cold/humid environments).
75306ffa-8cad-5fb5-8c60-4770efcfbc4e | checkpoint | STEP 4 - How do I control the risk?
398a9051-c14e-516e-9e62-3cf13abe5e71 | button | Can the task be eliminated? | Yes, No
368f597c-006e-5a4c-9622-48d5c1e579a3 | button | Can you change what is causing the risk (the source)? (e.g. change the work area; alter the size of loads; use mechanical aids; manage environmental conditions; use adjustable equipment; implement preventative maintenance program). | Yes, No
9bffc518-e600-563f-83ee-b46609ceeb6f | textbox | If 'Yes', provide detail:
c4d0d777-07a6-5a79-8614-ff5925bd7cd2 | button | Is training needed to support the control measures? (Training needs to be task specific, noting that training in lifting techniques is not effective as a sole or primary means to control the risk of MSDs.) | Yes, No
6a5b0a4b-fa33-5a1b-a349-4b1922bd8324 | textbox | If 'Yes', provide detail:
249717bf-db57-5fb4-b61b-9f7678983512 | checkpoint | Implementing Controls
2af5e740-8b0e-52a2-a6b3-9e5ba22dcc64 | textbox | Name of Responsible Person:
5fa58af3-1606-5f22-bd13-ee000d4bac34 | button | Responsible for: | Approving, Implementing
e1b9ffd7-6efd-5f3c-9c53-1acc8e453440 | textbox | Name of Responsible Person:
59827434-9895-5505-8e76-8e811858ed18 | button | Responsible for: | Approving, Implementing
9cd466bd-5a1e-5a06-acf9-a0f373c775d6 | textbox | Name of Responsible Person:
c475ab63-1681-519d-b90f-20724591aaa6 | button | Responsible for: | Approving, Implementing
6052a159-cbde-544d-979f-ab6b78557e36 | textbox | Name of Responsible Person:
60efcd64-d526-5420-aed2-141bb0678c2a | button | Responsible for: | Approving, Implementing
89334ebf-57ec-5f05-8b4e-750b91a0dc81 | signoff | BY SIGNING I CONFIRM I AM AWARE OF MY RESPONSIBILITIES AS OUTLINED IN THIS RISK ASSESSMENT
1ac85fbd-c1e0-52f8-a16f-a7d8e29a8854 | checkpoint | STEP 5 - Review the Controls
05cc12f9-13ba-5a46-851b-3ffa3889999b | date | Evaluated on(date):
aa933b5d-a414-56fb-9593-349817c6cb58 | textbox | Name of Assessor(s):
de2d6041-2451-56c8-a1b0-8123bb1f5ec2 | button | Consultation undertaken with relevant workers and others? | Yes, No
09a25e1d-447b-5703-a1a7-cf4cb0ccdd3f | button | Have any other risks been created by the controls? | Yes, No
62630e4b-1b37-507c-a268-7018937bb888 | button | Have the controls implemented reduced the risks? | Yes, No
8363f20e-bbe2-58a1-bdf2-6d6ec2000b64 | button | Can further controls be implemented to minimise the risk? | Yes, No
a80bd9a1-e2eb-5c96-ab03-28f50004f41c | checklist | ASSESS-003 Hazardous Chemical/ Dangerous Goods Risk Assessment |  | ASSESS-003 Hazardous Chemical/ Dangerous Goods Risk Assessment
8111ace1-1386-5c1f-8290-3df28e3c8d3f | checkpoint | Details
d64f9e12-a8d1-572d-b52d-a264f7fe2c21 | textbox | Hazardous Chemical (product name):
61131b33-b900-5454-a839-bacf04fddc09 | textbox | Hazardous Chemical Reg Item No:
fa30c358-8185-53ab-a3e5-7a89d93b620c | textbox | Use:
eec44df0-883b-5db0-a668-e111f5465eb4 | checkpoint | Nature of Hazard:
c3865074-534e-5e92-8183-abb02d5e0f45 | tickbox | Toxic (Poisonous)
73380fb3-2daa-58dd-a27c-fd92c28cc19e | button | Route of Exposure: | Eyes, Skin, Inhalation, Ingestion
1a4cca2b-c7c6-582e-8872-a69b23f4f996 | tickbox | Carcinogenic (Cancerous)
8448ff25-8567-56c9-bc8d-c65b7be067c3 | button | Route of Exposure: | Eyes, Skin, Inhalation, Ingestion
fbc7d650-c863-5438-88c0-b6801548cf7f | tickbox | Teratogen (Harmful substance that could affect abnormal prenatal development)
0a973027-0604-5fd1-8e33-1f6843068a0d | button | Route of Exposure: | Eyes, Skin, Inhalation, Ingestion
0c23b16f-1a98-579a-a5cd-b10341a3c93e | tickbox | Sensitiser (Reaction to an antigen, such as pollen)
26e95726-3d59-5326-a5cf-7952dba23427 | button | Route of Exposure: | Eyes, Skin, Inhalation, Ingestion
42fedfa0-4abe-5559-9a9d-3293d48b513b | tickbox | Mutagenic (Capable of mutating DNA, such as radiation)
6b6b9d2f-ae5d-51b8-a33a-bc4e0582efd9 | button | Route of Exposure: | Eyes, Skin, Inhalation, Ingestion
72b4fd57-ee4c-528b-9346-3cc09a71a26c | tickbox | Irritant (Inflammation of the skin, eye or respiratory system)
65ff1186-86dc-5bc0-9441-f7cda9142a6b | button | Route of Exposure: | Eyes, Skin, Inhalation, Ingestion
1488ffce-4246-526d-8862-2701ca976c59 | tickbox | Flammability (The ease of which a substance will ignite, causing fire or combustion)
fb8d25c9-0361-5fc2-992a-c8ac54018ced | button | Route of Exposure: | Eyes, Skin, Inhalation, Ingestion
c5299fc2-0138-5c3e-9df0-fdb6f6a23c55 | checkpoint | Risk of Injury
d5a297e5-61f4-58ff-b1b1-c8ca2eadf8ba | button | Risk of Acute (Short term) Injury: | High, Medium, Low
39a06ae2-da96-5801-a080-9de8bb9bd02a | button | Risk of Chronic (long term) Injury: | High, Medium, Low
6adca422-e108-5631-9168-8f36735799d3 | checkpoint | Controls and Requirements
dff33aea-d864-5296-85a7-3c3d89a4dbd8 | textbox | Control Measures to reduce exposure i.e. change to a safer product, ventilate area, (P.P.E.):
89612ad9-31eb-5b1b-b34f-25be2eacadf9 | textbox | First Aid Requirements and Storage Requirements:
42c21dbd-9bff-5051-bd1f-f936237b2320 | checkpoint | Signoff
f6e6ad58-755a-5ec6-ac1a-b3db6c24bfc3 | signoff | The persons listed below have been consulted in this risk assessment, understand the hazards associated and agree to use the control measures identified above to carry out the works safely and in a manner which protects themselves, others and the environment.
7a2e19d4-a232-5ccb-9e9b-f9c2132fc0a5 | checkpoint | Assessor Signoff
d0aabc79-7a66-528f-976e-31f5a7db0456 | signoff | BY SINGING I CONFIRM I WAS RESPONSIBLE FOR CONDUCTING THIS ASSESSMENT
2ea687ee-acea-5b17-843b-86fee551733b | checklist | ASSESS-004 Plant Risk |  | ASSESS-004 Plant Risk
8111ace1-1386-5c1f-8290-3df28e3c8d3f | section | Details
5011c755-395d-598c-bc65-ea69efabb143 | checkpoint | 1. Competent Peron(s)
9a9b3958-e0c2-5268-aaf5-3e077666511d | note | This familiarisation checklist should be completed by a Site Supervisor or Site Foreman to verify that the workers involved in the operation of Plant Equipment/ Mobile Elevated Work Platforms (MEWP) can demonstrate their ability to understand and operate the MEWP functions in accordance with the manufacturers operating manual. This familiarisation checklist must be verified by a competent person who holds the equivalent licence/ ticket required for the type of Plant Equipment/ MEWP to be operated (e.g. Boom lift/ Scissor lift)
421913a6-005a-5bfe-b708-440417ab5d27 | textbox | Your Name:
3d439d05-c639-5ad1-ab00-1ba3920a9817 | note | Your Licences / Tickets:
11d866e9-f084-5b26-843b-254282a6c100 | tickbox | WP High Risk
5e54de38-508f-50a3-ab0e-e0c8679f8a1a | tickbox | Boom Lift
ea68eb1f-321e-5e02-a622-a3508facf2c4 | tickbox | Scissor Lift
f33fdee4-d517-591b-8e36-9e836bd3d6e1 | tickbox | Vertical Lift
81a98fa0-20d0-5274-9330-e937fa7e313e | tickbox | Other
c7f781a4-a73b-5d49-9565-093b617aba7c | textbox | If 'Other" please specify:
c06fe721-a6e8-585c-ad93-6752e11d8265 | checkpoint | 2. Plant/ MEWP Details
90819d9c-8041-58fa-925f-ff4173355404 | textbox | Make and Model:
72d506d5-4e56-5ec5-8c93-b3f7d99536ce | textbox | Type (e.g. BL>11m, BL<11m, SL, VL):
6b0e5610-cf37-5886-aa78-b8bc2aea3ba0 | checkpoint | 3. Employee Competency
283fe821-9465-5997-884a-e53b824195ee | textbox | Name:
fe2792fe-88fa-5cc7-822e-859e2506a067 | note | Role:
0cae945b-d039-5202-9dc1-c1f31d837e92 | tickbox | Operator
6e501ba1-23dc-5885-a740-dcb403ba9400 | tickbox | Spotter
ab7d246c-0564-52d1-8da5-f8432c1bffa9 | note | Licences/Tickets Held:
51471574-24e5-57a8-9d87-1ad1fd20269c | tickbox | WP High Risk
c8680c7b-abeb-52c1-b43d-450b4de8fcf8 | tickbox | Boom Lift
fe824038-2fe3-59bc-8a08-d3570fef7ac3 | tickbox | Scissor Lift
52a4e5af-5299-5c5e-a60e-0e296500ce88 | tickbox | Vertical Lift
06ebc66d-119e-58a4-8c6d-3668b83861ad | checkpoint | 4. Employee Competency
73351cee-c380-5c96-b1c7-82c4bdc7793a | textbox | Name:
47b977ce-db23-5091-9181-d12522014aeb | note | Role:
4115b285-0dab-509b-b78c-6b3fe3068366 | tickbox | Operator
af2cc185-f772-5a03-969d-bf46bb86577a | tickbox | Spotter
ffc930ab-59a8-5e18-afb0-da251ac3661c | note | Licences/Tickets Held:
eee9b880-b7b4-5f05-9f45-44bc188ceb0a | tickbox | WP High Risk
32033229-269f-5e26-9a26-6024c4bced51 | tickbox | Boom Lift
8f37f26d-6637-5101-b032-1e34a248d86d | tickbox | Scissor Lift
47dfed81-5cfe-5cd8-84b7-d113b35adc16 | tickbox | Vertical Lift
3ef8e758-7384-5d13-8fa3-292a5f04a9d8 | checkpoint | 5. Employee Competency
70f78733-b0b1-5c22-a6ee-c84eb8cd5382 | textbox | Name:
e47caed1-7c4a-5091-84e9-87591d2a2fb9 | note | Role:
c84eba4f-6301-5058-96b5-2fdca6bc206c | tickbox | Operator
7f109594-56af-5ef1-b67b-b1e88673aa41 | tickbox | Spotter
5f1cc387-8b6d-5d5f-a08a-fb01a2b0d557 | note | Licences/Tickets Held:
b4dc56cf-627f-5e84-92e2-81be2c729e0f | tickbox | WP High Risk
ad5efe5c-cc66-52e7-9f33-9be813518ded | tickbox | Boom Lift
f3db69b0-11a3-5ff7-ae41-5bea8ceb8ed8 | tickbox | Scissor Lift
22049df2-afa1-534d-82b8-767d6e6e2636 | tickbox | Vertical Lift
0db35e59-5266-54bd-bc6b-7ababdb43cef | checkpoint | 6. Declaration (to be completed by competent peron(s) noted in Section 1.
f2766483-04cb-5da7-890e-dcc4e17777bd | button | All 'Operators' hold the appropriate licence/ ticket for Plant/ MEWP | Yes, No
5031b2eb-1c9c-55f6-a5cc-e63e9cfc76b5 | button | All 'Operators' understand the operational controls and emergency functions | Yes, No
12f920b1-81aa-59e1-a68c-e7269492885e | button | All 'Operators' are aware of the logbook and pre-start requirements | Yes, No
e2c18959-6e5b-562c-b9a5-4dac9408d32a | button | All Ground Support understand the emergency functions | Yes, No
925a0673-c38f-5fb4-b952-0246d6d57ff0 | button | All GM Fire employees on site have participated in an emergency drill | Yes, No
58559eb2-25f7-513c-9294-7fac027dbbb9 | button | All GM Fire employees have signed onto applicable SWMS | Yes, No
9899d9ec-b306-5aed-bbc5-b1347ea6537c | signoff | BY SIGNING I CONFIRM I HAVE ALL PERSON(S) LISTED ARE COMPETENT TO OPERATE THE LISTED PLANT/ MEWP ON THIS SITE.
298a1679-3b4d-50ad-97f7-8d79b298e664 | checklist | ASSESS-005 Confined Spaces Risk |  | ASSESS-005 Confined Spaces Risk
8111ace1-1386-5c1f-8290-3df28e3c8d3f | checkpoint | Details
130a7940-3935-5253-8ae5-82b1055dfd14 | note | Use this form to document the risk management process for a Confined Space.
5ca532df-2d29-581b-82a2-afa02f372b39 | date | Date of Assessment:
efa51e91-77f1-5628-a232-99f3c48b4020 | textbox | Name of Assessor(s):
faca6a3e-c6b2-569d-a658-055a4b1164db | textbox | Position(s):
270f8fc3-f5f3-5606-80eb-fc2c80ae4f95 | checkpoint | Hazard Identification
fad4c4f5-7e3d-5c24-add3-b36005494c89 | textbox | What Hazard/ Risk is associated with the task?
3caf8aa5-c5e5-5180-abaa-0a9a28dd8bda | textbox | Planned control measure to remove/ minimize hazards/ risks
80dd6f73-8abb-5f6e-b96d-a003c0862604 | textbox | What Hazard/ Risk is associated with the task?
d9d61964-0aa1-59dd-b417-a00130fda9f1 | textbox | Planned control measure to remove/ minimize hazards/ risks
2d8973bd-68de-5078-a649-d84eb5324735 | textbox | What Hazard/ Risk is associated with the task?
ad6a71eb-3672-50d8-bb44-58040405bb6f | textbox | Planned control measure to remove/ minimize hazards/ risks
beed0557-db27-53c9-b4fc-4106fb1a89e1 | textbox | What Hazard/ Risk is associated with the task?
e51d3210-35ea-5cdb-87eb-76a364960c2e | textbox | Planned control measure to remove/ minimize hazards/ risks
d291aadf-b45c-58c8-9abb-102b9ccd401c | textbox | What Hazard/ Risk is associated with the task?
9dcad28e-a5ed-5bcf-8b09-877284ed48f2 | textbox | Planned control measure to remove/ minimize hazards/ risks
520f3973-2a3e-554c-9da3-fcd0d6905a7f | checkpoint | Review
a5bad4ff-4c84-55b4-979f-864d1d649e12 | button | Does the Risk Assessment Identify that confined space work is involved? | Yes, No
ba7cd854-f374-50a0-bfdb-ccbcc4196d6d | note | If YES the Confined Space Work Permit MUST be completed
6cec88c8-2282-5790-9d56-16331bfb102c | note | NOTE: EMERGENCY & RESCUE PROCEDURE: Where an accident occurs which requires that an emergency rescue be attempted, the standby/ rescue person is to immediately contact EMERGENCY SERVICES on 000 for assistance.
7a2e19d4-a232-5ccb-9e9b-f9c2132fc0a5 | checkpoint | Assessor Signoff
a9d78622-1c5c-5ef7-96e7-636ddd7d9229 | date | Scheduled review date:
946f9c2d-1950-57b6-981a-43e43c738227 | signoff | BY SINGING I CONFIRM I WAS RESPONSIBLE FOR CONDUCTING THIS ASSESSMENT.
2e9f4f5f-73ce-5181-a4d3-ab809667db17 | checklist | ASSESS-006 Job Safety |  | ASSESS-006 Job Safety
5e25be48-4354-51fa-a917-1881487cb8a0 | checkpoint | Client Details
bf83fa46-22f9-52ba-80ce-a37529230034 | textbox | Client: i.e. Principal Contractor
589f8e09-feec-5403-88ff-194eb59adbe6 | textbox | Client Contact Name: Responsible Person(s)
eaeb3e60-e653-5a94-92f4-d3b629923fc7 | textbox | Client Contact Phone:
a7aa3b37-be9e-5945-8920-278208dee51a | textbox | Client Contact Email:
bad8a559-d874-55eb-a218-4243f23c1f05 | checkpoint | Job Safety Analysis Details
e0472b52-555b-578f-9b0d-10ca185460a1 | textbox | Work Activity:
7755fbc5-1db4-5c6a-9eb9-1a50b1b4f39b | textbox | Location:
9c4ccf3a-dc0f-5789-a749-3b3c139a461c | textbox | Who is involved in the activity?
3ff18e9a-8a0b-505d-a5ad-334bf588fe4f | textbox | Plant and Equipment used:
8fc90058-6ecc-5824-be76-439a2920b450 | textbox | Maintenance checks required:
503c2e9e-0cf2-5780-83bb-17e8b8e8cd20 | textbox | Tools used:
b474c44b-9350-5cb0-88c6-309a83224ea6 | textbox | Materials used:
3a661dd6-8651-5a9a-abd9-54ae562e3b84 | textbox | PPE used:
62d2facf-fd51-5926-9608-32ef95c4748f | textbox | Certificates, permits and/approvals required:
538da0a8-b2aa-517d-b88c-85e029139a90 | textbox | Relevant legislation, codes, standard MSDs etc. applicable to this activity
f948400d-3b6d-5037-a27e-a1da8d06232a | signoff | This JSA has been authorized by:
df68f526-1e94-59d2-832e-1b4bc4eb113c | checkpoint | Job Safety Assessment
ab741e71-0e49-5969-b5c0-f1c3f4db8a43 | note | Refer to the attached Risk Ratings table to complete the following..
3e4c920e-6e44-5089-aebe-027b3d41e2f5 | textbox | Job Step Details:
76039bd0-3c61-57c9-8744-263d7e249743 | textbox | Potential Hazards:
ff90c12e-9264-5ec9-bcfb-3809ecc00f80 | textbox | Name of Person(s) Responsible for work:
079e5ac5-4175-5234-8d36-7fe10d966313 | button | Risk Rating: | Low, Moderate, High, Critical, Catastrophic
f64d3e6b-5e0f-5c3b-a0b3-1c3a80d8b0fe | button | How to Control Risks: | Eliminate, Substitute, Engineering, Administrative, PPE
c8538ff2-0ff0-578b-aeef-883e852d2656 | textbox | Job Step Details:
6fa25bbc-560c-5b99-a629-cdc256177219 | textbox | Potential Hazards:
305af7ce-90b2-53c3-ac23-31c07c5e76a9 | textbox | Name of Person(s) Responsible for work:
f921fa6f-7fcd-5f5e-97a3-4c987bd12dff | button | Risk Rating: | Low, Moderate, High, Critical, Catastrophic
278e01f2-0559-54a4-8c20-ae06c6fb8a94 | button | How to Control Risks: | Eliminate, Substitute, Engineering, Administrative, PPE
8c34d454-01a5-5eca-9ee8-bfbf2fc6de79 | textbox | Job Step Details:
7bf50a7e-e54a-51b1-a340-1e56e1576981 | textbox | Potential Hazards:
e422d336-150e-51a7-94cd-4ab59a8286a4 | textbox | Name of Person(s) Responsible for work:
e2e1fd0c-62ed-50c9-b80d-fd9141eae82f | button | Risk Rating: | Low, Moderate, High, Critical, Catastrophic
bfcca39f-b561-5f72-9ea8-3ee3779e362a | button | How to Control Risks: | Eliminate, Substitute, Engineering, Administrative, PPE
42c21dbd-9bff-5051-bd1f-f936237b2320 | checkpoint | Signoff
9c249912-b3c0-5116-b8ec-aba0ea058e1e | signoff | This job safety analysis has been developed through consultation with our employees and has been read, understood and signed by all employees undertaking the works:
930a3e43-5647-50d1-87f2-966cce2343da | checklist | CHECK-002 Site Inspection |  | CHECK-002 Site Inspection
7604d349-3c9d-59ec-8769-a0cfe4110d87 | section | 1. Administrative, training and risk management requirements
b646b6a2-68d2-5b04-925e-0e13a9bb914a | checkpoint | 1.1 - So far as reasonably practicable, all workers carrying out construction work on the project have been made aware of the content of the WHS management plan, including any updates, and their right to inspect the plan.
6ba63d7d-3b3f-5c31-9434-f4939b574a87 | checkpoint | 1.2 - All workers carrying out construction work have received the general construction induction training.
b9691151-2ecd-5ee2-8ec8-b533204f2fd9 | checkpoint | 1.3 - Workers have been informed of the site-specific health and safety rules.
60ac4aca-7460-564d-ba14-2d3d98bfd234 | checkpoint | 1.4 - Suitable and adequate information, training, and instruction has been provided to workers in relation to work they are carrying out.
66bab419-a393-57f6-9c97-758d79271510 | checkpoint | 1.5 - Personal protective equipment (PPE) is being worn in accordance with the projects requirements.
2ab82d7a-cc3c-56a0-a89c-ba9e4252acc3 | section | 2. Safe work method statements
c145e282-9bf0-58ac-8a85-4500302a4c6e | checkpoint | 2.1 - A safe work method statement (SWMS) has been prepared for each high risk construction work activity that is underway or about to commence.
fe929405-eae8-5ca8-8783-fd58e2de54ac | checkpoint | 2.2 - Workers have reviewed and signed off on the relevant SWMS
7934e80d-dec5-5f41-be0b-42bbfcdd01e2 | checkpoint | 2.3 - High risk construction work activities are being carried out in accordance with the relevant SWMS.
8f0ef03e-318f-5cf3-b827-93b54c1df497 | section | 3. The work environment
e6018bbf-c8f1-5f07-b149-1bf83ae3ef97 | checkpoint | 3.1 - The work environment has been maintained such that it is clean and in a safe condition.
79bdc24c-1c00-5acf-983d-ebaa5ce5fad4 | checkpoint | 3.2 - Work areas are clearly identified and separated as necessary so that work can be undertaken safely.
1825c9fa-24bb-50ad-8b3b-a1e424e13ba5 | checkpoint | 3.3 - Lighting at the workplace is sufficient to allow:
f8272eb3-01c5-5337-a307-f72286a48c32 | note | ○ Each worker to carry out work without risk to health and safety.
1be19c4f-a82e-522b-98e5-e5aa656efb60 | note | ○ People to move within the workplace without risk to health and safety.
aef67d61-2c29-5ed8-9db6-bcf3ceacb0db | note | ○ Safe evacuation in an emergency.
e6860137-88a0-51f5-bab0-d6de14d63cb6 | checkpoint | 3.4 - The workplace has sufficient ventilation to enable workers to carry out work without risk to health and safety.
4ff74d5f-cec6-5c19-bd25-e6838e8f1c56 | checkpoint | 3.5 - The entries, exits, and access ways in the workplace are kept clean and clear of materials and waste.
48066b16-7c21-5768-945d-e4a5cf766b0b | checkpoint | 3.6 - A safe system has been implemented for the collection, storage, and disposal of excess or waste materials.
0b615730-4ffb-51cd-bfb3-02fcfc4435d7 | checkpoint | 3.7 - Sufficient area has been allocated to safely store materials or plant for the construction work.
8dca0770-d2f9-575c-9e8a-bc6b57a4f871 | checkpoint | 3.8 - Protruding objects that are a hazard have been made safe (e.g. exposed nails, vertical reinforcing steel).
b201c421-5b2c-5c48-9704-05cf6113c44a | checkpoint | 3.9 - Adequate facilities have been provided for workers, including toilets, drinking water, washing facilities, and eating facilities.
c51929b0-8776-5f5d-9a2c-3ebcffee0dad | checkpoint | 3.10 - First aid equipment has been provided for the workplace and is accessible to each worker.
18a4e767-8b1d-5672-a5a5-274690a036b4 | section | 4. Confined spaces
2825d9b2-da10-596a-9ce0-b40fcc56a1cc | checkpoint | 4.1 - For each hazard associated with a confined space, a competent person completed ASSES-05 Confined Spaces Risk.
0a584ab9-a5b3-52a1-b882-f4b9709cc8db | checkpoint | 4.2 - Prior to commencing the works, FORM-003 Entry Permit Confined Spaces has been completed and approved.
89309c03-7f35-5362-a583-36791c1dba8a | checkpoint | 4.3 - Appropriate signage has been erected for all confined spaces.
d0a6d31c-65a4-5bf4-bc31-672ba9175665 | checkpoint | 4.4 - First aid procedures and rescue procedures to be followed in accordance with POLICY-006 Confined Spaces Rescue in the event of an emergency in a confined space have been developed and practiced to ensure they are efficient and effective.
ded5ed0a-e444-5b8a-bb7f-fdbe7f8fb660 | checkpoint | 4.5 - Workers required to work in or around a confined space have been provided with information, instruction, and training in relation to the:
bed85791-cdf2-5734-99e5-42eabe40f212 | note | ○ Nature of all hazards relating to a confined space
be7ccc94-3134-5b95-8b20-72fefb415b43 | note | ○ Need for, and the appropriate use of, control measures associated with those hazards
b110c5ef-6275-5bf5-a856-5a63e44d03ea | note | ○ Selection, fit, use, wearing, testing, storage, and maintenance of any personal protective equipment
1a99ce71-7f11-5eeb-a21b-b350ded8d8c3 | note | ○ Contents of any confined space entry permits that may be issued
b0c02c77-ff62-5a00-8a01-e40663b3102c | note | ○ Emergency procedures.
e81da6f2-b7fb-5d0c-920d-ac0985916342 | section | 5. Working at heights
e2a6047c-3469-57d7-a1ee-63a6d2ce1e6a | checkpoint | 5.1 - A SWMS is available for all high risk construction work that involves a risk of a person falling more than 2m that has commenced or is about to commence.
c2fb3d08-8253-53dc-a912-7762ad36b3c3 | checkpoint | 5.2 - Where a risk of fall of less than 2m exists:
15a0bb70-25a2-55ce-8391-f9705261ae79 | note | ○ Each hazard that may result in a fall or cause death or injury if a person were to fall has been identified
098e60b1-4049-5b81-9802-dc44b50477cb | note | ○ The risk of death or injury that may result because of the hazard has been assessed
d8e17ce6-5b0d-5d71-adcb-c9012baa2fa9 | note | ○ Any control measures necessary to prevent, or minimise the level of, exposure to the risk is used.
98b57a94-c6a8-50d7-bb1c-2783d46d3990 | checkpoint | 5.3 - Where a risk of fall of at least 2m exists, control measures have been used which:
df712649-e072-54fe-b908-fe63884b915b | note | ○ Prevent a person falling any distance
28993959-da47-509e-a241-bb45845a83ee | note | ○ If prevention is not practicable:
55b684af-87ab-5194-82b6-3e644dbb1a7b | note | – arrest a person’s fall
7575aa24-7d52-5200-8719-e639552c447b | note | – prevent or minimise the risk of death or injury to a person when the fall is arrested.
6a7044d6-a81e-5157-bf4a-f5cbc210f31d | checkpoint | 5.4 - Ladders are not used to support a weight greater than that for which they have been designed.
d81daed7-0057-50a6-9fe9-8aece2cab495 | checkpoint | 5.5 - Ladders are used where the:
d8458251-f7d1-554a-bcc3-372ab76e7d8a | note | ○ Bottom of the ladder is on a stable surface
c8fdd838-d4e2-5652-83e9-9bc5b3b6145b | note | ○ Rungs of the ladder are approximately level.
3f3316e4-f01d-5a03-a2af-4637d940f52b | checkpoint | 5.6 - Scaffolding has been erected by appropriately licensed workers.
e8760cac-e387-5620-9ab6-470830ad9fb6 | checkpoint | 5.7 - Scaffolding is or has been erected and/or dismantled so as to eliminate or minimise the risk of falling at least 2m to people carrying out the work, in accordance with the regulations
faed25a7-0d74-5c49-bf12-7d35d9c1c221 | checkpoint | 5.8 - Safe access to and egress from scaffold has been provided during erection, use, and dismantling.
06596e0e-a7d6-5ec1-ae87-b458bc352bec | checkpoint | 5.9 - Written confirmation from a competent person stating that the construction of a particular scaffold has been completed, has been obtained prior to the use of that particular scaffold.
a1cf7634-7b7a-503b-98b6-a44b1401c2de | checkpoint | 5.10 - REGISTER-007 Plant and Equipment is up to date and includes all mobile plant in use.
92665bac-aa8b-572e-82c0-08a5392f0bfe | checkpoint | 5.11 - CHECK-004 Pre-Start Plant and Equipment has been completed for all mobile plant in use on delivery to site.
3dd77402-8a87-529b-8183-9c072abbce8a | checkpoint | 5.12 - CHECK-005 Regular Plant and Equipment has been completed for all mobile plant prior to commencing operation of the plant that day.
26a08f78-359d-5909-8059-66675eee2c23 | checkpoint | 5.13 - Mobile plant operators hold the appropriate high risk work licence.
23b709bb-1735-5ef2-90a2-edf28c5eaf62 | checkpoint | 5.14 - Where there is a possibility of powered mobile plant colliding with pedestrians or other powered mobile plant, a warning device has been fitted.
a556791d-1316-51ef-8b5c-74f5158d5808 | section | 6. Electrical
b2dcd8ef-695d-5a07-a1c9-d7a4c42cb637 | checkpoint | 6.1 - Electrical leads are arranged to avoid damage.
d2a5d551-016e-5c24-aaed-9a6546efb65d | checkpoint | 6.2 - Electrical equipment has been inspected, testing, and tagged in accordance with AS/NZS 3012 Electrical installations – Construction and demolition sites.
a3dea501-b49e-52a0-b686-be4f3b199e32 | section | 7. Hazardous substances and dangerous goods
28f006f5-6133-536c-83c5-e5fd046e9474 | checkpoint | 7.1 - All hazardous chemicals that are used, handled, or stored at the workplace are correctly labelled.
d9654d68-e223-5e2a-a924-23ef86d304da | checkpoint | 7.2 - A safety data sheet (SDS) exists and is available for inspection for each hazardous chemical used, handled, or stored at the workplace.
569fad8c-3f02-54bb-9e8d-8a513e63a228 | checkpoint | 7.3 - A register of hazardous chemicals used, handled, or stored at the workplace has been prepared in accordance with the regulations and is kept at the workplace.
73d14d34-271c-5e50-a0cd-036c9275e063 | checkpoint | 7.4 - A spill containment system has been implemented in each part of the workplace where there is a risk from a spill or leak of a hazardous chemical.
a5f93861-409f-57a4-9892-aad365d82b0e | section | 8. Corrective actions
a3895f4e-c7f0-509b-ac43-872a6873bc7e | checkpoint | Corrective actions
fefdfa68-8ae7-5784-8f52-ff31386b2624 | section | 9. Inspection sign off
19075f73-f3d6-5581-b9a9-39135e1c7056 | checkpoint | This workplace inspection checklist has been completed by;
4b32712d-5eb5-5f21-8318-9f10d9fee1e3 | textbox | Name:
8f6f1e26-c9d1-5d5c-beb5-fb775c1e28a2 | date | Date:
75e3ab6c-26b3-5c04-9c56-ec536230e4ac | signoff | Signature
690502ea-7da5-5119-ba91-b2aa394089de | checkpoint | I hereby certify that all corrective actions as identified in the above checklist have been completed;
be7ee8f6-2fdf-5e61-aee6-adf9bbb71704 | textbox | Name:
f58dc23b-c6d5-59c2-9d2a-57694b8eff87 | date | Date:
3e494399-cc9e-5e9f-964d-deff12bc6678 | signoff | Signature
7bd28543-904f-5683-acd7-cdd9184635f4 | checklist | CHECK-003 Site Establishment |  | CHECK-003 Site Establishment
8111ace1-1386-5c1f-8290-3df28e3c8d3f | section | Details
0b4ad232-5674-51d3-9408-aef0b58a609d | checkpoint-no-value | Details:
a9f0eb07-3912-523a-be5f-a802d6ff641b | textbox | Project Number:
be704f51-8345-5d07-82ad-4691b8d46bd7 | textbox | Project Name:
55438198-cfca-5417-84b8-414b08417475 | textbox | Project Manager (PM):
cecfc96f-5250-5907-bbf1-e0562cea155d | textbox | Project Address:
71a86034-b956-5203-b873-8d6f798b33ad | textbox | QA Platforms used:
d76c3f2b-8320-5708-a9da-38fbd066c69d | checkpoint | In house, FER & Specification Numbers
62d9c92d-c1ab-5446-89b1-bf80cbc0d1a4 | date | DATE:
087bf1f2-2a91-5ac0-811b-92888709522d | checkpoint | Site visit & survey
9d598589-23f2-5739-abd1-38084d2be5a8 | date | DATE:
f40bf70e-7c03-562e-9e73-8fbcd929c861 | checkpoint | Review Drawings & print for site
767f52ec-aec3-5775-a064-7229f459323b | date | DATE:
86a71627-b83a-5fe5-827a-1173c7cec5b0 | checkpoint | Review Fire Engineering Report
0d7909f1-54e9-5c90-92e6-074eee42c7aa | date | DATE:
eb035cf3-e47b-505b-b522-f71e191c12e9 | checkpoint | Allocate labour
0a895642-a262-5e46-a17d-2bd265707331 | date | DATE:
dae330e6-ef9c-57c6-9197-103abfd54f8e | checkpoint | Review Principle Contractors (PC) proposed baseline program
1692f978-f249-5f30-958a-396ff70c258b | date | DATE:
a55f05f2-ebad-534b-8cbf-1758e22f0184 | checkpoint | Create Fire Services Proposed Programme
07f60850-c8ec-5c07-8cb3-4760f7a199c5 | date | DATE:
7a356f7b-71e1-5c53-87a9-49ac25d117b8 | checkpoint | Upload to ALL necessary QA platforms
b5b18c80-8662-5430-9ca2-81c6feb62800 | date | DATE:
e81b739e-4825-5367-841f-3db753c333bf | checkpoint | Save softcopy in GM Dropbox
c65d94ba-f3ef-5124-bde6-1efbcc2ca74a | date | DATE:
c2e6bd69-c405-5afe-b004-c8b107fec18d | checkpoint | All employees have attended Induction
f2578d06-522d-52c8-91f5-609e406fe43b | date | DATE:
2630ff26-4768-5012-85c8-d89b8e40b4dc | checkpoint | All SWMS soft copies signed & hard copy printed & filed in the ‘on site’ paper folder
ccf4434e-fcc7-5408-8a54-c9b9b3f5816e | date | DATE:
5674c7a7-848b-557d-a867-52fce0b2bfd9 | checkpoint | PM Signature:
1ec883e5-6967-525b-ae22-80125604b1fd | date | DATE:
c87607a0-8578-5433-aab2-734b6f931e89 | signoff | PM Signature
a9f3dae5-2089-56f0-a2a7-1e8117f00339 | checklist | CHECK-004 Prestart Plant and Equipment |  | CHECK-004 Prestart Plant and Equipment
8111ace1-1386-5c1f-8290-3df28e3c8d3f | checkpoint | Details
0e841671-e894-5ff8-8c03-82b5d38ebca8 | date | Date:
c1d0f4b3-7c9a-5132-9202-97a201ea48ef | textbox | Time:
bb60eefc-fad6-507f-945f-d1ad16fbf517 | textbox | Location:
24067169-41ae-5b98-ad46-2642b05d62e7 | textbox | Supervisor Name:
0b454d7c-2ee3-5e46-a2c9-e543b923b322 | checkpoint | Plant or Equipment
f5a882c2-e981-51c1-b81b-ea1e16eb70bc | textbox | What Plant/ Equipment is being used?
f2431a16-e799-5a6c-80c2-763dddad7637 | textbox | Person operating today:
dd154f8d-3d7b-5f2c-88c3-251fe510498d | button | Is this person competent and licenced (if required)? | Yes, No
70fb33c4-1f70-5ac0-942b-6a10ea85acdb | button | Is the operator under the influence of alcohol or drugs? (If 'Yes' please explain in comments and find an alternative operator) | Yes, No
cc81ce2f-8bc8-5749-80fd-06fb563d3672 | button | Is the operator tired? (If 'Yes' please explain in comments and find an alternative operator) | Yes, No
63617e94-873e-5e03-9f60-862196254f6a | button | Have you added this to REGISTER-007 Plant and Equipment (located in Dropbox) for this project? | Yes, No
a7d9973d-01b6-5c61-bcc7-8234615b507b | button | Have all relevant SWMS been completed? | Yes, No
f9910de1-77f1-541c-876c-35b08d530ef7 | checkpoint | Plant and Equipment Checks
e3c467e9-a510-5e56-beed-49a3f8877e1a | note | As per WHS Regulations 2011, s206 the person with management or control of plant must ensure the plant is used only for the purpose it was designed and ensure that all safety features and warning devices are used in accordance with instruction. Please check the following:
546a8afd-7693-55a2-914a-54e7c90d72ae | tickbox | Electrical switches, traffic indicators, front and rear lights are working
e5b78bd6-d41e-528e-9746-0c62c2c527e7 | tickbox | Guarding is of solid construction, unable to be bypassed or disabled, is appropriately fixed and operates correctly (check latches/ locks and interlocks if fitted)
8b9ff6ad-23d7-57de-9e48-14a9253d2139 | tickbox | Engine, fuel and lubricating systems are as per manufacturers specifications
5806d6c3-2813-50a0-a427-7fa9935957a4 | tickbox | Tyre pressure is as per manufacturers recommendations
d39fe1f4-ba21-5239-8ecc-7f4573210e83 | tickbox | There is no risk to the plant colliding with any person or thing (i.e. workers, other vehicles or plant, energised powerlines)
54704e4f-9089-5ee6-ae7f-46a0727eac60 | tickbox | There are no mechanical or other failures (e.g. hydraulic failures, release of hazardous substances)
f6e7258f-adb6-541d-b22a-ed50132853e8 | tickbox | Seatbelts are available
5d47353b-22df-563b-a9ca-2faccbdb89e6 | tickbox | There is no damage to switch gear and controls and that controls can be locked off
58c4f0bd-8df6-524c-a238-af2983501734 | tickbox | Emergency stop controls are marked, accessible and coloured red
3ad0b909-d61c-507a-a372-2aec69aa39af | tickbox | Warning devices are positioned to work effectively
4ccae013-80b5-5161-9761-e7028e449e0c | tickbox | There are no hazards to the operator (e.g. things that could fall on the operator)
f7a4206a-0f8f-5a90-863e-6dc75e30731c | tickbox | There is no hazard or risk that could caused the plant to overturn
cf1206a0-2d7e-5f3f-be6c-0f9e888638ec | tickbox | Maintenance and inspections have been carried out
2bcc0a89-8c1f-5fe5-958d-a1f1ba7233a4 | checkpoint | General Notes
d7295a42-11dc-51c1-80d1-cf9ed24c9857 | checkpoint | Operator Signoff
c685b88b-9455-5eaa-8271-b512fa65c130 | signoff | By signing I confirm I have participated in this prestart and understand my duties. I know what PPE I am required to wear whilst operating, the load limits and I am aware that it is my responsibility to leave plant not in use in a state that does not pose risk to others.
cc546369-bca4-51b6-ab24-8e4406ba760e | checkpoint | Supervisor Signoff
411f2708-55c2-5469-af77-82675a4393a8 | signoff | By signing I confirm I have conducted this prestart with the operator (above).
9532b837-f860-5b1d-ab12-067a44cade17 | checklist | CHECK-005 Site EOD |  | CHECK-005 Site EOD
8111ace1-1386-5c1f-8290-3df28e3c8d3f | section | Details
e7f3c29e-5e50-58c0-b5bc-209b95434737 | checkpoint | KPIs
ef28294d-80e7-5a97-9797-47eab0412edd | textbox | What area did you work on today? Specify level(s)
8bac133b-8e7b-54d3-bd45-213c754c0666 | tickbox | Detection - In Slab Conduits
df315065-d10d-5309-a137-f96b6957f3ca | tickbox | Detection - Rough In
79d811d4-f9b3-5356-8c5c-282608faae28 | tickbox | Detection - Fit Off
bd243762-5500-5cc3-863e-a5089b537b11 | tickbox | Sprinkler - Rough In
b32b2f5d-1593-5094-8ac0-574540448662 | tickbox | Sprinkler - Fit Off
b6b03401-f74a-555d-a276-7baec04d7748 | tickbox | Wet Weather Stand down (List names and duration of stand down per person in comments below)
702632f3-f07d-55dd-b02a-798d0cd2c2bb | tickbox | Safety Stand Down (List names and duration of stand down per person in comments below)
ad3f731b-7995-5c43-9ca1-66fcc39f907a | tickbox | Industrial Action/ Techs chose to leave site (List names and what time they left in comments below)
d6aa768d-18cb-5397-9287-98d25f058d4d | checkpoint | Productivity
935439a4-16d9-54f5-94c7-76368fef5f00 | textbox | In terms of production, did the team meet the site goals today? | Yes, No, Partially
5eb767e9-2d9b-5650-9148-f8d6eacb88e9 | button | If 'No', what hindered the progress? | Time management, Lack of training, Fatigue, Equipment issues, Other
e94f5534-5646-540d-aa79-e9ebca99d6ea | textbox | If 'Other' provide detail:
0da64418-8a08-5008-a58c-e5368b811be6 | checkpoint | Clean Up
ff4b227b-9ed7-503b-a008-a24d64c82a30 | button | Is your work area tidy? | Yes, No
2685c8cb-e50d-53b0-81fc-2140a66dc922 | button | Have Chemicals used today been returned to secure storage? | Yes, No
63aa0fac-8064-5883-8936-a62b7a9bec47 | button | Have all tools been returned to toolbox? | Yes, No
ec167b87-5679-50a0-88b1-36f8dbca244d | button | Are all tools (including site iPads) charged and ready for tomorrow? | Yes, No
95ffe66b-b5ad-53bb-9648-f5d931f2f4c0 | button | Have you completed all necessary QA paperwork for today? | Yes, No
bb4bba5b-d0e8-5fdb-a13b-dbc423aaee5a | button | Are all employees aware of where they are working tomorrow? | Yes, No
db72225a-9b45-5d2c-9afa-e9dfb88f7dd0 | note | If 'No' contact management now
a11f6f9a-2853-505a-b6fc-46a0fac484e1 | button | Were there any incidents, injuries or near misses on site today? | Yes, No
2b76a127-74df-54eb-92bd-c06e1d1e92d7 | note | If 'Yes' complete the necessary reports
42c21dbd-9bff-5051-bd1f-f936237b2320 | checkpoint | Signoff and CLOCK OUT
5d29489d-1335-55db-945d-fe7621bce49f | signoff | This EOD has been completed in consultation with our employees and has been read, understood and signed by all employees on site at the EOD today.
47a05a8f-01d6-5308-b319-09c8bfef63a9 | checklist | CHECK-006 Daily Prestart |  | CHECK-006 Daily Prestart
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
af98ba3f-7105-4c3e-be07-e2ab6454306d | checkpoint | CLOCK IN
c58e65ab-a72b-4fed-85ca-080ec1fa3336 | signoff | Sign here to CLOCK IN to your shift
0b4ad232-5674-51d3-9408-aef0b58a609d | checkpoint | Details:
c67a5ad6-470a-5e2f-997a-f5f60b5e37f6 | date | DATE:
be60c24b-9584-50b3-85e7-c97aac850d9f | textbox | TIME:
5309490c-3518-5494-8898-6b41003721aa | textbox | SUPERVISOR NAME:
694414d8-1e1b-5f09-a0ec-7b8d590ad762 | checkpoint | Issues
29d3d625-f08c-54b1-bf3c-b22dfa3fbd75 | button | Are there any issues arriving from yesterday? If YES, detail in comments below. | Yes,No
88bc1641-daee-577f-b7e3-efc84c9a3236 | note | NOTE: If this requires a change to the SWMS then please ensure this is captured and relevant personnel inducted.
0662f670-ac3d-5439-af86-c1336a2b3861 | checkpoint | PLANNED WORK ACTIVITIES / TASKS
89e3b170-750e-51d8-a682-a426806358d3 | textbox | ACTIVITY / TASK
63009163-b71f-5d74-88ab-182d0339fbec | note | SWMS that relate to today's task/s
3217cd42-d7b4-5c06-8925-f508bd3b2eb4 | tickbox | 001 – Working with elevated work platforms
4e6ff252-595a-527a-99b7-8b0d317de7fb | tickbox | 002 – Wiring Rough In Minor
cd7e73e3-d703-52b7-9d32-c59cb15791e0 | tickbox | 003 – Fit off fire alarm system
b8ad95df-8b35-52b0-9faa-5efb930c096d | tickbox | 006 – Installation of pipe and fittings
2fc333ec-8649-5094-9bac-e7db22722260 | tickbox | 007 – Manual handling
793477a1-ebab-528d-ac0f-4cf5e41a28fa | tickbox | 009 – Pressure testing of pipework
abf682f7-668c-584c-add3-69603f01ffe9 | tickbox | 051 – Using platform ladders
aab532fe-44ab-58ce-84b2-320c641c1eca | tickbox | 060 – Inhalation of Respirable Crystalline Silica
55efd7fe-fc29-5217-af4c-3858f7a3124e | tickbox | 061 – Working in Major Area of Concern
774a66c3-3fea-5200-a769-32e4e0d72e01 | tickbox | Task-specific Safe Work Procedure
23c8da75-1795-5395-a9d2-b738a880bbe9 | checkpoint | Is a SWMS in place for ALL high-risk construction work and work procedures in place for all other works?
018251a3-fdc4-5187-821b-085ee9060fc3 | note | IF NO, STOP AND DEVELOP!
ebf4ce4a-0774-58f0-a144-522ec96b5a15 | checkpoint | Are you subcontracting out any works today and will you be interacting with other trades?
95fe8c17-73e5-5a12-84ab-0e88db6ce7aa | textbox | If YES, please list
279dbae7-8c1f-5553-98d3-d60918e8eade | checkpoint | Permits
ccbee4d0-b0fc-50f9-aba7-187627b00d3a | button | Isolation Permit | Yes, No
e9e5dd68-707a-5644-8f38-af984c59f3e6 | button | Have conditions changed since permit approval? If YES, please note changes below. | Yes, No
498988e2-fa90-543d-abe2-62bbc0b59d3d | button | Hot Works | Yes,No
49f83c80-5eec-5445-acf1-c5c9e01af072 | button | Permit to cut or drill | Yes,No
26129dde-acee-57f3-b54c-c083077e591c | button | MAC Permit | Yes,No
1d20b088-7c9c-5436-8f27-c1ecd33f79fd | note | Please list Permit numbers with description below, and upload photo/ attach file if available.
cae12b06-72bd-55e9-a701-9b47a7fdd5d7 | checkpoint | Environmental Risk
d043a4ae-8752-53fc-bcd7-920e72521388 | note | What controls are in place to manage environmental risk on site, specific for today; e.g. Wash out areas, maintenance of sediment fences and drains, monitoring of dust?
be468b16-df19-537b-854e-46bbd3df7b89 | tickbox | Clean up the general area
03b3f67c-e939-50e1-8cb2-87e19dbe9fd7 | tickbox | M-Class vacuum
054df62a-5657-559a-8159-5ed36c7947b6 | tickbox | Fit test and appropriate fit mask
3640b7ac-10ad-5ec3-ab6e-ae1284393ae1 | tickbox | Spill kit onsite
9bbc93b8-7fb5-5515-8c51-902ff1a50612 | tickbox | Other - detail below
903e1008-c734-5d92-8e65-be1215f53964 | checkpoint | Checklist for Activities
f1e2b79e-aefd-53e7-bcd3-7868bdf06e49 | number | Number of people in your Work Group
57c8c5eb-69d5-5928-bcc8-b3fe0690aa3a | button | Daily Risk Assessment Completed | Yes,No
d198e689-340f-595d-aa6c-5796b9e55eea | button | Qualifications/training of staff adequate for work activities | Yes,No
a89c730d-f0a5-5583-9141-f6861600debc | button | Plant and Equipment on/off site | Yes,No
c2abc099-5048-5862-be7e-69276e515d47 | button | Equipment safe to use | Yes,No
c35b1cc8-2353-5462-9376-b66fbffbe2eb | button | Work area inspected and safe for staff to enter and work in today | Yes,No
446e2139-b3e3-5032-b3b7-4b2ecf6682f2 | button | Appropriate and adequate PPE supplied to work teams (SWMS/SDS) | Yes,No
1297b9fc-83fc-5f03-8c96-a7ef0df8cad5 | button | Weather conditions for work to be conducted assessed | Yes,No
50775e4c-331c-5bcf-9d61-90de79b49eb6 | number | How many workers have been allocated for today’s clean up?
31b028e3-39b4-5b10-96c0-301d4210e7d4 | button | Pre-start communicated to all work teams including all trades & subcontractors | Yes,No
00d26647-1805-5512-8e68-9d14a06237f7 | button | I acknowledge that all Plans on my Dropbox shared file are up to date and I have confirmed this with management | Yes,No
f21451ba-8bea-5c8f-a381-24f716ce840c | checkpoint | Builders Briefing Notes
96ad1a92-eed7-5574-b446-3263c628aa29 | note | Attach a photo of the builders brief
2bcc0a89-8c1f-5fe5-958d-a1f1ba7233a4 | checkpoint | General Notes
79c2dc13-619c-4cd7-80ac-60aa3e45c613 | checkpoint | Mental Health Check-in
cd31bf4e-e2d5-5d58-b35c-fd75f58de3c1 | note | Prior to commencing work, ask your fellow workers: Are You OK?
0c6ae895-4776-5618-ae00-20be5d041a11 | note | Mates in Construction 1300 642 111
bd2c90e5-3cd6-5a5f-aefc-f4f34c1caf48 | note | Beyond Blue 1300 22 4636
3ecf9d4d-a367-5b79-a67e-d473daee966d | note | Gambling Help 1800 858 858
065e825a-d2be-5f52-accd-f30095264611 | note | Drinkwise 1300 858 584
462a3bfd-f982-5f3f-95bf-2a3e5632bbde | note | GM Fire Management 07 3519 7573
42c21dbd-9bff-5051-bd1f-f936237b2320 | checkpoint | Signoff
ad0d0126-8a7e-5cc0-84b3-32f1ee14e2ef | note | Remember to clock in and out of your shift.
2c27aaf3-a648-56ea-92c9-e1e22f200a26 | signoff | By signing I confirm I have have partipicated in this Prestart and I understand my roles and responsibilities today.
83cd8a70-2c48-4704-ae9f-aa06805bcd49 | checklist | Communication (empty) |  | Communication (empty)
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
d4c25ea0-808c-4521-a9b7-2f9c58da8b7e | checkpoint | Communication
0c2c099e-edf9-5390-b182-f1f1989ed33f | note
5450b772-d997-57fe-895d-71ad5cc37336 | checklist | FORM-001 Tool Box Talks |  | FORM-001 Tool Box Talks
0e50f726-5e25-5b32-be5e-0af50c2a4fbb | checkpoint | Tool Box Talk
e3272aff-5ad7-5584-9f05-601db13efeff | note | Project: Odyssey
c4982672-0b0f-5087-ad36-2079a30053d4 | textbox | Tool Box conducted by:
b862c72d-bb88-5890-9585-9eb1d66d73f3 | date | Date:
201ee0d5-9875-55e5-a6b4-cf9a175f45ee | textbox | Attendees:
272ef767-b0f9-5d40-860f-37667165b540 | checkpoint | Electrical tools Tagged & Tested
de358699-2ee1-5f01-a52d-02e78a8f5dcb | note | ACCEPTANCE CRITERIA: Completed Onsite
9031bd57-1d4e-547c-b0ec-b6fb0b1da5db | date | DATE:
605677f5-661a-5bc3-a836-02384d30df5c | checkpoint | Tools checked for wear & tear
d34b0a75-d62c-564d-93ac-a1912bd32f6b | note | ACCEPTANCE CRITERIA: Completed Onsite
8aa8c1f1-8235-59cf-9f29-b950ab07c005 | date | DATE:
acfc8acb-9e64-5733-af2a-b8ca4ea1ea81 | textbox | Items for Discussion:
eabcda0d-be6f-512a-b32a-8bddf5fcbc83 | textbox | Items for Review and discuss at next meeting:
95cb37b4-7a6f-5ffc-99b0-5d11fbc535e8 | signoff | Signatures
67624c30-0631-53f9-aa45-6f94413e7795 | checklist | FORM-002 Tool Box Talk Platform Ladders |  | FORM-002 Tool Box Talk Platform Ladders
106e79f1-1888-598d-99d2-b5a1def7ffd3 | checkpoint | Tool Box Talk - Platform Ladders
887bab57-3216-58e7-9dd5-6974b3a623f9 | note | DO NOT use platform ladder unless you are familiar in its safe use and operation.
ac68153f-7547-5f9f-b14c-f8801309e330 | note | Always complete as much work as possible at ground level before using the ladder.
3271903a-2c15-5d14-ac31-800aa151f93c | note | Make sure the platform ladder is stable before climbing.
5c4a49ee-d931-5509-bdad-bc64c1ca1617 | note | Project: Odyssey
00a320e9-986f-593f-bfe8-d25f2931da45 | textbox | Tool Box conducted by:
d0208122-f03a-5610-bde4-6bcb1a760f97 | textbox | Attendees:
da9865ac-d3b6-579f-bb6b-472d8b97b3d7 | date | Date:
fe834967-5fae-5142-ad41-d9de6147f88c | checkpoint | Potential Hazards
3674f2b7-e39a-58bf-b062-1209a407d5a0 | note | The folllowing potential safety hazards and risks have been explained to attendees:
5ea57c24-c9ef-5ac2-aae7-14b6543b15e5 | tickbox | Falls from height
e35ecb4b-a22f-5bcd-833f-fe852d10554a | tickbox | Falling objects
a3d70cbf-4729-5583-aee4-bcf73f29102e | tickbox | Awkward posture
016ab889-7fd8-5c55-95e3-1cf5f8ca44c5 | tickbox | Duration of task
674a0483-b78e-5388-ad6a-db7ac2554b1c | tickbox | Repetition of movement
3f4946f8-8fdd-526a-bb60-7b0d27db4098 | tickbox | Sprains/strains
a6af3874-9657-5afa-ac7b-5c30211f6885 | tickbox | Over-balancing
75d35ab2-1c77-568c-80f3-d9d45ae93ef3 | tickbox | Slip/trip/fall
4a7ce000-11b4-5942-9d59-57beec09de90 | tickbox | Electrical hazards
70790ef5-6074-57a2-b56e-987747b11967 | tickbox | Climbing with loads
1bd92719-b7cf-583c-a096-9b04e390c7ae | checkpoint | Pre-Operational Safety Checks
6ffbd377-bf17-5fba-98aa-8caef52856d1 | note | 1. Familiarise yourself with the safety instructions on the ladder.
a2ea6641-1eb7-56a0-a6e1-7e49d7e16115 | note | 2. Wear slip-resistant footwear. Never wear sandals, high heels or flip-flops. Wear appropriate clothing (e.g. no loose or flapping clothing, or clothing that restricts movement when climbing
aaf65bc0-57d6-5a03-b04a-8610a6416a50 | note | 3. Do not use if affected by a medical condition or medication.
2ba95fdc-b818-55eb-8e98-76f82b92f60b | note | 4. Keep ladder clear of live wires, electrical hazards and ceiling fans.
2c22d256-80a1-5046-8b5e-69ef43b328e9 | note | 5. When transporting your ladder check for overhead power lines, live wires, service cabling or electrical hazards.
93412ad9-195b-58ad-a5cc-688db75dd770 | note | 6. Carefully inspect your ladder to ensure there are no worn parts or damage before climbing:
ffc562ba-2d4e-5c0c-923b-aee111b51e69 | note | • joints between steps and side rails tight, all fittings secure, moving parts operate freely
639c69e6-a3c5-5051-a7d0-e2ca755bc18b | note | • rungs and platform are free of paint splatter, grit, oil and grease, welds are intact, and
5dc33034-ebb6-5e46-8386-62410b6d7321 | note | • all components of ladder intact including side rails, rungs, platform, feet, hand grip.
c1ec81fc-3779-5bbb-99e7-d74bdce4d420 | note | If any component is found to be worn or damaged, rectify any faults before use.
b6eb527a-c4c7-5a69-bb85-a66da835bc7d | checkpoint | Operational Safety Checks
df307b10-6066-5dfe-b2be-ccdabe4b711c | note | 1. Complete as much of the task at ground level as possible.
50ceb36d-3a89-51e0-a79d-8e7534c96b76 | note | 2. Ensure the ladder is placed on dry, firm, level ground/floor. Uneven footing may cause the ladder to rock. If this occurs re-position the ladder until all feet have firm contact with the floor. Always check there is no rocking movement before climbing the ladder.
2b10f449-9e31-58fa-8e70-0fe01b8c3789 | note | 3. If castors are fitted to the ladder, ensure rubber feet have firm contact with the floor when the springs are depressed.
37b91bc5-cb01-56fc-9108-0102c7c4058a | note | 4. Ensure the ladder is fully opened and the spreader bar is locked into position. Check for overhead obstructions before climbing.
7cac46ae-5fc7-5ee4-994f-75dd2980ea6f | note | 5. Only light work is to be undertaken on the ladder. Always face towards the ladder when climbing, and always maintain three points of contact with the ladder. Use a tool bag or tool belt to help to keep hands free.
64f23374-768a-5597-b8a4-9427fc451328 | note | 6. Only one person is permitted on the ladder at any time. A second person may stand alongside the ladder and help to steady it, or pass materials/tools up if required. Do not lift heavy weights that unbalance the ladder.
cea9f832-60c9-5a6a-8373-7c2c02db8309 | note | 7. Never stand or sit on the top cap or use the rails around the top as a step. It is not designed to be used as a tread/seat or step. Always stand in the centre of the platform.
c5338561-5326-55d2-8865-025c5fc7aa76 | note | 8. Do not over reach whilst using the ladder. Maintain the majority of your body weight inside the perimeter of the platform.
6a5bcd9f-5002-5193-afd2-5687e1f860a2 | note | 9. Do not ‘walk’ the ladder while on it. Always get off to shift position.
19c1d6b4-49ea-5f94-9658-6f1b832f0141 | note | 10. Before moving a ladder, take care to ensure that all tools and other items have been removed.
2d257990-358a-561e-bc89-f01924822341 | note | 11. Be mindful of your concentration and fatigue level. Avoid becoming overconfident when using ladders during repetitive tasks.
9d5b0bf0-53b6-5af8-a766-a7d78d594580 | checkpoint | Housekeeping
b7b52c7c-7b6c-5b22-8666-70b57f43c8ee | textbox | Items for Discussion
5c711e95-86eb-5f70-9f58-45404bea1e34 | textbox | Items for Review and discuss at next meeting:
0d24abf6-09a7-54db-913a-af58fcfdb176 | note | All attendees have been made aware they should:
fdb2ffa5-48c5-5b86-a475-b5e212b244b3 | tickbox | Return ladders to secure storage in a clean and in safe working order
ac8f4780-7d87-5234-98fe-0fee60585788 | tickbox | Regularly check ladder feet for excessive wear.
61838543-8502-5082-8baf-f0fa703ab465 | tickbox | Enter any maintenance in an equipment maintenance record
3015ae9e-0d1b-58a3-bfcd-57a87f411d9a | signoff | By signing I confirm I atteneded this ToolBox Talk.
c752d65b-6785-47bd-80b4-4db433ff37e7 | checklist | ITPS-100 Cast In and Penetration Installations |  | ITPS-100 Cast In and Penetration Installations
4b9a4425-672b-419c-ad78-55db79229cb2 | section | Details
a39df76d-8c78-46da-86cb-056c0cc69770 | checkpoint | 1. LOCATION - ENSURE
5ef154c1-5dab-5877-a6d0-8cd9392a9700 | note | CIBSE C5.2.2 Set Points
09e630bc-2f7c-5ceb-92ea-87e3ee6290e0 | button | Is the device setout correct and accurate as per RCP and installation plans? | Yes, No
b9f0f1bc-71b9-5d78-8be5-e3f0fe549ad7 | note | Add Photo
53188b4a-5da5-45a4-8ba2-711278c14676 | checkpoint | 2. CONDUIT INSTALLATION - CHECK
a6054f7d-45d8-5ac9-b577-581b40e7cbc2 | note | AS1670.1, AS1668.1, AS1670.4 and AS3000
32e4b4b3-cb41-5ff4-bb37-716b5702b600 | textbox | Drawing Reference and Revision Number:
fb239f69-ae94-594e-a503-558d9eb860be | note | CIBSE C5.2.2 Set Points
381a59a7-6d52-599a-8ac6-68c3e5b5b8a3 | note | Are Conduits routes are correct as per IFC Drawings?
a7884800-a0f5-54a6-a2f3-4c16b7a8d9f9 | note | Are Conduits are joined correctly and glued using approved PVC piping and glue?
acf8b286-9f7e-53d2-b490-16fd717af536 | button | Are Conduits are tied in properly to prevent movement and damage? | Yes, No
1a02436a-3a6b-5922-ae95-39bf0eea934e | note | Add Photo
9823d6e9-7bfd-42eb-a780-64da61a737a7 | checkpoint | 3. SLEEVES AND PENETRATIONS - CHECK
074bfaeb-f4ef-5254-9216-349c272d5dfc | textbox | Drawing Reference and Revision Number:
dcb21f86-156b-57a5-81bc-476237ce484e | note | CIBSE C5.2.2 Set Points
4218bfb1-16b5-5fd7-9869-e9b95b5f0d20 | note | Are sleeves the correct type, size and quantity as per penetration drawing?
ac04b737-d305-5203-9602-669e73121600 | note | Are sleeves routes correct as per IFC Drawings?
a5eb33d6-5035-5495-98f3-8b8d59a43047 | note | Are conduits joined correctly and glued using approved PVC piping and glue?
a728ca65-dfb3-5066-8599-5b06c4eaa1a7 | button | Have sleeves been tied in properly to prevent movement and damage? | Yes, No
837eaacc-0bab-5798-bd74-eaa6d6f24769 | note | Add Photo
1342def9-41c8-4883-860d-8c6d39dad8d4 | checkpoint | 4. PRINCIPLE CONTRACTOR - CONFIRM
5b2d5933-aff6-5060-8ab0-164d913c9c36 | note | CIBSE C5.2.2 Set Points
453ba0b8-74da-5b8f-ae27-757c848cc6c4 | button | Is the Principle contractor's sign off required prior to pour? | Yes, No
629e51ea-960e-5631-a1cb-e2bbabaf2035 | note | Add Photo
ad3be74f-233e-4099-82bc-382e20da9739 | checkpoint-no-value | GM Fire Sign Off
ab5f7a81-742d-41db-9dbe-5f405ac17f06 | signoff | GM Fire Sign Off
f9de37fc-1cec-4e42-b65c-de36e6f3dd81 | checkpoint-no-value | Principal Contractor Sign Off
3763b074-3b02-4a4e-b972-909e6605db09 | signoff | Principal Contractor Sign Off
b268ee7a-871f-4d26-960e-10bbe47520c3 | checkpoint-no-value | Consultant Sign Off
6e27d9e7-4e51-4ca5-b594-e33b14a9bac4 | signoff | Consultant Sign Off
fef270dd-c9dc-4e05-9099-e3d8f7a48d88 | checklist | ITPS-101 Fire Alarm and EWIS Rough In |  | ITPS-101 Fire Alarm and EWIS Rough In
6d1c95ec-d3be-4a6b-89df-e9e882af277f | section | Details
cf574374-e703-4440-a005-5e0dd64bff6c | checkpoint | 1. CABLE - CHECK
6b2dce9a-96b1-5ea8-b5a6-c2c62bc92870 | note | CIBSE C5.4.0 Wiring
ce7d9049-64e6-5fe0-b4d1-1b6090904ca1 | note | AS1670.1, AS3000
e68486bc-2006-5b04-b235-a8c57b49ba96 | note | Is cable installed the correct size and type?
dc028c52-d50b-5130-9484-e27005ea312a | button | Is cable secured at regular intervals? | Yes, No
64488453-d50f-5552-a388-dfcaa98293e8 | note | Add Photo
714b6da0-5968-57dc-9473-c0aa542fa5d4 | button | Have you attached a photo of cable markings for Green Star Compliance? | Yes, No
664cedec-6604-52cf-92ab-46b04305ccc5 | note | If no, stop and attach now
cba37353-5c3b-46ab-bbc5-c6e51aad89e4 | checkpoint | 2. FIRE RATED CABLE - CHECK
8643553a-467c-5ff9-bb67-85c02a0eba25 | note | CIBSE C5.4.0 Wiring
8fb005b0-42de-54c0-9762-098d6e445ae8 | note | AS3000, AS1760.1, AS3013, AS/CA S009
d916763d-a9d5-5c25-bcbd-2a2908ab884c | note | Have fire rated cables been secured with fire rated fixings at a minimum of every 1200mm?
98ad43e7-7945-5411-907d-1ef9bb7e7f42 | note | Have compliant fire rated cable and fixings have been used for required circuits?
5c013aea-4bae-5b7c-866a-e05aedec036b | button | Are fire rated cables installed as the highest circuit? | Yes, No
da09e15e-baa1-5355-aecc-a6c5770e226b | note | Add Photo
a701edb0-a1f1-47a7-b1da-00b8bc99f91f | checkpoint | 3. CONCEALED SPACE DEVICES - CHECK
50ae80e5-12bb-58e9-9ad5-0a39dddd678f | note | CIBSE C5.6.0 Sensors/Detectors
cf6350db-b359-521c-a43b-3fc399751d98 | textbox | Drawing Reference and Revision Number:
99694dc9-fe8f-5c77-978b-7f275b76e715 | note | Have all concealed space devices been fit off?
14b2c9aa-eda1-5e3c-b9e7-91e2f0570e0d | button | Has remote indicator cable been left with adequate length? | Yes, No
727a8db5-9f01-519b-a6cc-556b2109ff55 | note | Add Photo
df7725d2-33a9-4cf4-8f2d-212b79c9c57f | checkpoint | 4. ROUGH IN - CHECK
748e2b33-68fc-5cde-8f1d-eced5105defd | note | CIBSE C5.2.5 Control Loops
62eccab1-b067-5a38-92bc-3f2c66f294e4 | textbox | Drawing Reference and Revision Number:
408efa09-48c9-583e-9aa9-d56c3a90797d | note | Have all devices been roughed in?
d3cffd7f-75a2-5df9-be67-8c0dccc22f87 | note | Is there adequate length left for fit off?
a72a0e23-27fe-5b93-a942-77cf8132a5d1 | note | Are device locations accurate as per the latest RCP?
931dab71-9cbc-576b-bb0b-c20d544426ae | button | Have circuits been metered for continuity? | Yes, No
8f0901a2-475a-57a7-82f5-2c2b066dbb38 | note | Add Photo
c57b1d47-f2a1-45b7-887e-c4e9398bf223 | checkpoint | 5. MAG DOOR HOLDERS - CHECK
81760bee-404b-5c75-8490-19db4653e29c | note | C5.2.2 Set Points
378da007-5fca-509c-bf52-8bd2aaff17ed | note | Have wall noggins have been installed?
5511e34f-2b8b-5ce1-8850-da258c9c8692 | button | Are cables roughed in to the correct location in wall? | Yes, No
4df9b5ab-36f7-41a5-8c61-96b1dc2ef778 | checkpoint | 6. SEGREGATION - CHECK
9a5ea305-e4da-5d6b-a435-cfa11d25a819 | note | C5.2.2 Set Points
2a09a2fb-7021-5776-8601-14a1fd5d63a0 | note | AS3000
e3b317d9-6196-59c5-8eac-fec5fee389be | note | Is there a Minimum of 25mm from water & gas pipes?
ff245dda-4b97-579f-9da4-cd62e61322bf | button | Is there a Minimum 50mm between ELV & LV installation or a physical barrier? | Yes, No
f01b7f74-2034-4f60-8bbc-8964e295c251 | checkpoint | 7. AS WIRED DRAWINGS - ENSURE
ccb58587-2140-54f7-ab91-2b13aad73752 | note | C5.4.0 Wiring
8c6ac1f0-4fec-5b38-a1a2-ec082d697746 | textbox | Drawing Reference and Revision Number:
04987c1f-c17b-53e8-b11f-8320c2227bde | note | Are As-wired drawings complete and accurate?
104dfed6-405c-523c-8602-0ab20c9860df | button | Have photos been uploaded to Dropbox? (as well as below) | Yes, No
8a4031a5-a2e6-5e61-92f2-35c6e8309273 | note | Add Photo
39163b50-167b-44f2-b863-49341bb39d36 | checkpoint-no-value | GM Fire Sign Off
66dee818-0084-4bef-84e7-fb1df866851e | signoff | GM Fire Sign Off
dbd062ae-9375-41e6-b1eb-32b729504d06 | checkpoint-no-value | Principal Contractor Sign Off
084a69da-8884-4ac0-a6ff-588b28102e85 | signoff | Principal Contractor Sign Off
bc1b286f-f0cf-401e-b29c-f82954182e4c | checkpoint-no-value | Consultant Sign Off
03648807-9825-4686-90d2-049145c7494a | signoff | Consultant Sign Off
926b0aeb-71aa-4454-8808-82282f63ce8a | checklist | ITPS-102 Fire Alarm Fit Off AS1670.1 |  | ITPS-102 Fire Alarm Fit Off AS1670.1
7c056c18-777b-4719-8c42-b8c26de2a952 | section | Details
4a10caf2-3b43-4970-adfa-b047114eaf29 | checkpoint | 1. DETECTOR TYPE AND LOCATIONS ARE AS PER THE LATEST RCP
f4dd4903-b3f7-5f5d-b6de-f63ea9d0ed8b | note | CIBSE C5.6.0 Sensors/Detectors
b54035f1-b250-5af0-8f90-3fb206b0e970 | textbox | Drawing Reference and Revision Number:
a28144ea-8e91-570e-8e3a-aaff56458f37 | note | Add Photo
db60d0d5-e4d9-4ddd-b053-e02edb2d82c0 | checkpoint | 2. DETECTOR ADDRESSES ARE MARKED ON AS BUILT DRAWINGS
6ea3a9b4-d6d8-58fb-81fd-21962a1e64fc | note | CIBSE C5.2.2 Set Points
6bf3d543-c044-56c7-9342-1d3522da26f1 | textbox | Drawing Reference and Revision Number:
8ea1c4dc-e110-56c8-9d51-7fe0dc03c91b | note | Add Photo
d3f9d90f-4b54-4f7f-93fa-3f731e342816 | checkpoint | 3. DETECTORS MAINTAIN MINIMUM CLEARANCES FROM WALLS, PARTITIONS & AIR SUPPLY OPENINGS
4297478b-45f3-5c29-98f0-6644e17e28e7 | note | CIBSE C5.6.0 Sensors/Detectors
99d0eea9-c087-5e22-86b6-a7ae55f9affb | note | As per AS 1670.1 - 2018 - 5.1.4 & 4.1.4;
41403934-2388-529a-ad3e-0d580beff83f | note | Is there a minimum of 300mm from walls & partitions?
7c81482c-e787-5d04-84d5-15fcf0578be5 | button | Is there a minimum of 900mm from air supply openings for smoke detectors & 450mm for heat detectors? | Yes, No
f805b1c2-49ca-5aee-9d7a-7f6cb439a2b2 | note | Add Photo
be483340-a5bb-4c9d-a8db-f279753991fe | checkpoint | 4. DETECTORS MAINTAIN CLEAR SPACE AROUND SAMPLING POINT
624183a2-970c-54fc-a164-577f9b95e9b8 | note | CIBSE C5.6.0 Sensors/Detectors
b1cb2ca0-6e8c-5e7b-8c66-b120a6e1a796 | note | As per AS1670.1 - 2018 - 3.27.1;
7b9b2d7a-2102-552b-952a-73a1e946d1b0 | button | Has a clear space of at least a 300mm radius and 600mm depth been maintained from the sampling point? | Yes, No
fa6ca6f1-1d8d-53f1-a949-c4b7dc4a0612 | note | Add Photo
fbff2246-f270-4220-bb3b-3c3cbf58fa73 | checkpoint | 5. PROTECTIVE CAPS ARE INSTALLED ON ALL DETECTORS
3a7e05b5-4d49-5088-8b4d-7f0a15c0066f | note | CIBSE C5.6.0 Sensors/Detectors
37effdb3-f4a7-5cea-8780-f2392eaffb95 | button | Have dust caps have been installed on detectors to prevent contamination from construction work? | Yes, No
844de038-179a-53fa-bfff-40ada7b65a6e | note | To be removed once dusty works are complete, or at commissioning.
dc3d9223-a318-54ea-872c-45339e885079 | note | Add Photo
2fe4c73b-017c-4255-bd69-027ea80db604 | checkpoint | 6. MANUAL CALL POINTS INSTALLED AS PER LATEST IFC DRAWING.
8b364f16-0809-5d58-8ef5-c7f59a6a734b | note | CIBSE C5.10.0 Manual Call Points
f30f1775-1b7e-588e-aeb1-67d9ffe85991 | note | Have MCPs been mounted between 750mm & 1200mm above floor level?
1bbfcde0-a516-59dc-bc75-0bc7d185ca1d | note | Is there a clear space of 300mmm on both sides?
89a8aa98-798e-5af7-a9b0-b35803508be1 | button | Is there a 600mm arc directly in front of the MCP? | Yes, No
f3edfd9f-ad05-515e-8951-dfbd52475e79 | note | Add Photo
5fc60959-8e72-4acd-a959-e5319ed0b88b | checkpoint | 7. MANUAL CALL POINTS SPECIFIC LOCATIONS
9ae9aea3-27f8-59aa-82ab-922a185a7afb | note | CIBSE C5.10.0 Manual Call Points
db428802-0fa3-5b3b-9e50-3b3ab8a1fac9 | note | As per AS 1670.1 - 2018 - 3.14.2;
7ff3deb9-6d67-5139-9bad-b880223fd003 | button | Is at least one MCP installed in a clear and readily accessible location in the circulation space of the main entrance of the building? | Yes, No
afe4a77b-78d0-5d5d-967f-a41d3e7b5015 | note | As per the NCC2022 - S20C4;
ef4dc476-d217-5f8c-bf99-a43f10184e19 | button | If in a Class 9a building, have you ensure MCPs are located in evacuation routes so that no point on the floor is more than 30m from an MCP? | Yes, No, N/A
d5797b48-96ff-5b65-970e-94cda253741e | note | Add Photo
1102022d-c2b4-4140-8698-fb69bb393935 | checkpoint | 8. FTRS
7f32026d-1f1d-587e-ad05-758a06698c22 | note | CIBSE C5.8.0 Modules Input/Output
e1b2ed07-fedd-50df-bacc-009bd686631b | note | Have all FTRs been installed in correct locations as per latest drawing?
f9b59859-635c-5af1-bddc-a862697736c8 | button | Have the right quantities been installed to ensure correct operation as per the fire & mechanical matrix? | Yes, No
24225d5a-8960-51a6-bca9-ef48a402a47f | note | Add Photo
c082ec51-59d6-4233-ab0c-89226494cfee | checkpoint | 9. MAGS
9fb93b3b-097f-5a99-91b7-2a6022d0f4b6 | note | CIBSE C5.8.0 Modules Input/Output
7b7c4292-1a7b-5113-845f-a2e75678692b | note | Have the mag door holders been secured properly to withstand the weight of the door?
02fff620-dfc1-52b4-b3b8-54cd2125e23c | note | Have they been installed at a uniform height on each door leaf?
c80c1e15-3330-5992-aa0c-6289a67a3d02 | button | Has a release switch been installed? | Yes, No
d6efccbb-ab1c-5a08-b30c-a65b6a11d1ac | note | Add Photo
8b20e485-1198-43ae-a32c-b23de2e086fe | checkpoint | 10. MASDS
1a78019a-1ccf-502a-82d1-6ee800ad8e73 | note | CIBSE C5.6.0 Sensors/Detectors
558f4273-de6c-5bcd-ab01-85b10ab0d5d9 | note | Has all pipework been installed in line with the Aspire calculation & design?
3e7dda1e-296f-56e7-99cb-b62cc5246f0a | note | Has all pipework been glued?
bc5e9584-99c5-541f-8b45-be6c744a5145 | button | Is the head end unit installed in an appropriate location? | Yes, No
3e568773-b91d-5826-abae-d4327aab2305 | note | Add Photo
152e5cdd-799e-4cac-a250-2b3661c62bca | checkpoint-no-value | GM Fire Sign Off
1d67a7e9-7ef3-4ed8-bae4-aa81243f69fc | signoff | GM Fire Sign Off
64c99996-1750-4b86-856b-284ddfad53b4 | checkpoint-no-value | Principal Contractor Sign Off
a5bb4567-9ed3-40a1-8185-9bf2237e6efb | signoff | Principal Contractor Sign Off
91a2aa73-570b-4e17-a0d1-57985ee8d888 | checkpoint-no-value | Consultant Sign Off
60b14a5b-cd68-4d0b-ae9b-e3e83e4fca41 | signoff | Consultant Sign Off
24b36bd9-712f-4c0a-a1c5-6175a5ee6f3f | checklist | ITPS-103 Ewis Fit Off AS 1670.4 |  | ITPS-103 Ewis Fit Off AS 1670.4
9eaea976-894f-4b0e-8ac7-5b8193ed84f0 | section | Details
a2c6e2df-291b-45eb-b3b7-0d8995c66879 | checkpoint | 1. WIP
7e1025a2-67cd-5c74-94b7-312cf126e735 | note | CIBSE C6.2.8 Warden Intercom Phones
4a9a2b51-d984-54a1-beac-a5d002008a19 | note | Are the Warden Intercom Phones mounted at a height of not less than 1200mm & not more than 1800mm?
066776a1-03b7-5f97-9ca9-64c088c5d825 | button | Is there one WIP per EWIS zone installed within 4m of the exit? | Yes, No
15692d32-aacf-5519-b5ec-a47f4ea65de0 | note | Add Photo
b7de626e-aaa2-4b6a-ad41-29ffd8788028 | checkpoint | 2. SPEAKERS
07ce6252-a936-5d53-8731-fcd7f6943fbf | note | CIBSE C5.2.2 Set Points
e729d4bb-9677-5956-9de1-d19b49521552 | textbox | Drawing Reference and Revision Number:
2bc7142e-3840-5f4d-8af4-a32922153da9 | button | Have all speakers been installed to the latest RCP? | Yes, No
4670ac26-29cb-5dc9-af77-4510962b0768 | note | Add Photo
9ca1b6f9-ca56-428e-a867-77b7cd1039ca | checkpoint | 3. STROBES
c19c023f-1b19-532e-938c-a9a0fa01f312 | note | CIBSE C5.2.2 Set Points
67fcb16e-4774-579e-b169-e89bc7fc3650 | note | Have all strobes been installed to the latest RCP?
851326f5-db54-59cf-9c2f-af02c1ccccf1 | button | Have all strobes been labelled "EVACUATE" with 25mm lettering? | Yes, No
dcc71407-bb94-5887-93b7-99ae5761a7ce | note | Add Photo
5ec687af-3ba6-4cd0-9bb0-fa0c7b909f64 | checkpoint-no-value | GM Fire Sign Off
ad6249e6-96f9-4cda-bb3a-a444d96939c8 | signoff | GM Fire Sign Off
8a9edded-a972-4b6c-a442-ceddaf99dd8d | checkpoint-no-value | Principal Contractor Sign Off
14fab572-83dd-4bc1-9da7-882a8a67e220 | signoff | Principal Contractor Sign Off
0f1cb2b5-b567-474a-88db-89b4c49ed47e | checkpoint-no-value | Consultant Sign Off
5f34e887-2572-4941-936a-40a43f203f6b | signoff | Consultant Sign Off
a1209b5b-86e6-48bc-9342-ca49600d80d5 | checklist | ITPS-104 Fire Alarm Cable Tray |  | ITPS-104 Fire Alarm Cable Tray
ef2637ba-c18c-4eef-b178-3b01aa27894a | section | Details
46d4c003-82ce-4974-a363-c8a562d7991c | checkpoint | 1. LOCATION & INSTALLATION
868ef562-3cba-547b-8cd9-a6c7fee161e6 | note | CIBSE C5.2.2 Set Points
0e3ecac7-e6b6-5b9f-81a4-5e82838bc834 | note | Is the tray as per drawings and model?
8dfd8adb-2d17-59be-9657-cafe3633693a | note | Have all sharp edges have been removed to prevent injury or damage to cables?
92bc4850-3ea3-571a-bf21-6c3f2753235c | button | Is the tray supported at intervals of no more than 1m? | Yes, No
986be37f-ad94-5813-bf22-5970b5159919 | note | Add Photo
4ff7a3e3-fc52-4865-a2eb-15259638570c | checkpoint | 2. FIXINGS AND FITTINGS
05d45ef8-b133-509a-a19e-ef0109f2540b | note | CIBSE C5.2.2 Set Points
072becc6-22f7-5a95-8023-af08189e1a64 | note | Have the appropriate fixings and fittings been used (for indoor/outdoor use as applicable)?
42096020-d1bb-591a-a76b-017121123924 | button | Are Seismic fixings as per the design documentation? | Yes, No
78e786da-2784-53a5-bf80-bdd496102208 | note | Add Photo
7d47aa4d-dcc1-438e-a0df-465113d0fca5 | checkpoint | 3. CABLE SPACING
0b62a68c-5ba6-5838-b3f5-33d4cae5a7d4 | note | CIBSE C5.2.2 Set Points
c888d018-4015-5d2c-ada7-5c78155afd10 | note | Generally, where possible install in the following groupings:
46038383-8c70-546c-ac50-011c7c65b213 | note | Detection Cabling & 24v Cabling
fb556a92-3978-5c85-b1a8-6b56aee60a8b | note | EWIS/OWS Cabling
2d3bafb3-6769-5b53-a6dd-a436d4316c0a | note | WIP Cabling
137ad864-ca47-5bfd-836f-c5a23a3295af | button | As per AS3000, 3008, and S009, is the segregation of ELV and LV cabling at least 50mm? | Yes, No
e2de8888-0f43-5df9-822b-cb6ecde0e4b5 | note | Add Photo
46af5ab1-1418-4252-aeb0-8b187b5c0507 | checkpoint | 4. SEISMIC
1b1d48d7-5a1a-5730-83cb-a41ebc9756f1 | note | CIBSE C5.2.2 Set Points
e456e815-5411-5ef8-99ae-cdab7dec3f39 | button | Has the cable tray been installed as per the seismic drawings provided? (Use of stablity strut or catenary wire may be required) | Yes, No
74658fb8-c45b-5dc2-b2a7-6478891ae49d | note | Add Photo
bb35aa44-39c7-46d2-b2b4-ba4d79ac2804 | checkpoint-no-value | GM Fire Sign Off
93634982-7421-4b82-9af2-5320be3635e8 | signoff | GM Fire Sign Off
1d7ed560-84ac-4aad-a6a7-0446092d26ad | checkpoint-no-value | Principal Contractor Sign Off
e7188cf8-47c1-4dc1-9f27-03b731bd60ea | signoff | Principal Contractor Sign Off
6c09eb24-26dd-4472-be09-139e74835247 | checkpoint-no-value | Consultant Sign Off
515bf598-0731-4eae-9d44-4dd76805363b | signoff | Consultant Sign Off
9924d1fd-34b6-474c-93ff-b568245aa98b | checklist | ITPS-105 Fire Indicator and EWIS Panel Installation |  | ITPS-105 Fire Indicator and EWIS Panel Installation
9796b3af-0e66-4f42-8235-b430874845d6 | section | Details
8a0fa072-4855-4d05-bc38-c373f3e0bbbb | checkpoint | 1. LOCATION
6372e197-e18d-530a-95c1-4a4834006249 | note | CIBSE C5.2.2 Set Points
e6aef5c4-45c2-5b7f-a525-0182ab7c189d | note | AS1670 (Section 3.9)
a16d8041-6a8f-5f2b-a42f-b6470a6302d8 | note | Do you confirm the CIE is:
3d1fe314-26b4-58d2-8557-ea17edf254c4 | note | Not in an area used for storage of combustable material; and
dc594615-2892-5567-842a-8b02b60bd8c1 | note | Not obstructing evacuation of the building; and
00e8caa9-006f-5826-8bc3-45512d9544ea | button | Not in a room containing sprinkler valves, pumps and motors? | Yes, No
a0aa2dc9-f6ee-5ec3-aed6-0b9ceb166805 | note | Add Photo
595ab0e9-d8d6-4a37-8790-30b87a41bbf7 | checkpoint | 2. LOCATION
03eaa0c3-6f27-5175-9c64-9e5b212abb74 | note | CIBSE C5.2.2 Set Points
e1ec6743-b182-545f-b996-8a416569fbd8 | note | AS1670
27a2ca88-4410-5031-b153-9a52081d52e5 | note | Has a minimum clearance of 1m in front and 0.5m to each side been maintained?
ffe241e7-0667-5775-9636-7c9e49d798f8 | button | Where obstructed by a door, are the words "FIRE PANEL" in contrasting colours? | Yes, No
864c8b5a-8f1c-5d4f-b054-cd9cdfa48189 | note | Note - Where the door reduces the sounder, an external sounder may be required.
2b8ea2a7-35f3-5128-a854-27fc56ed1b81 | note | Add Photo
d67aa9b8-b73a-46e9-9a72-f77af7e1ed8a | checkpoint | 3. CONTROLS AND INDICATION
4ca5fa7c-982d-5764-8b6f-0c3140d69d9e | note | CIBSE C6.6.0 Brigade Interface – FFCP
fc1be8ca-a1dd-5eca-b525-8ea69cdd8b8c | note | AS1670 (Section 3.9)
4ecab2f7-1018-5dc3-9d72-9efe99488c36 | note | Do you confirm CIE has controls that are:
16244bf4-7aef-5a27-8098-1e4a2b4103cc | note | Not less than 750mm from floor level; and
ee2ad131-5b6d-5cb8-a9ae-dd383620297a | note | Not more than 1850mm from floor level; and
590eb56d-5f94-5b7d-b8cc-8f903552461d | button | The access to controls is not obstructed? | Yes, No
04315a10-f999-58ca-807e-cd25f4c30d80 | note | Add Photo
90356477-b07b-4220-8cef-4a90c3e38c5b | checkpoint | 4. CLEARANCE
4bd6c155-24db-5712-b512-aa54cfbdbf1c | note | CIBSE C5.2.2 Set Point
7fe61bec-c704-57fe-81f2-f7696bdcb80f | note | AS1670
cf179953-ac2b-58c5-8d7d-353b8c0982f0 | button | Is there a minimum clearance of 1m in front and 0.5m to each side? | Yes, No
81a98bd2-a3a3-531b-8217-173394a64378 | note | Add Photo
cc880e85-afa5-4650-ad9c-b824a0afbca4 | checkpoint | 5. EXTERNAL ALARM
a5017dc4-4391-5094-ada2-f0af38c274a9 | note | CIBSE C5.2.9 Alarm Functions
6929225e-fdd0-5a05-82ce-7e683d635004 | note | AS1670
21b9acdc-2890-57ff-a007-c899483d9f5b | note | Is an external wall mounted VAD is located on the front façade no more than 10m from the DBEP?
9c33ade1-f83e-542e-a2d4-2c7cd006fddb | button | Is it visible from at least TWO directions, and mounted with the words "FIRE"? | Yes, No
8803e4cc-3e9b-5422-986b-c8ae1e27f9a3 | note | Add Photo
b2d11abb-3f85-4ff7-88c2-9ab45677d9c8 | checkpoint-no-value | GM Fire Sign Off
536e3dcc-7e31-46e6-9e58-9d2153193cf6 | signoff | GM Fire Sign Off
7ca2fc6d-250e-40e8-86c0-826ec524ebde | checkpoint-no-value | Principal Contractor Sign Off
11b3bd6c-b607-447b-859f-739674ef04d2 | signoff | Principal Contractor Sign Off
6d1fd2a3-5243-42ec-b537-edc6d055dd81 | checkpoint-no-value | Consultant Sign Off
05856a27-b9e4-4422-868b-b6ef45728130 | signoff | Consultant Sign Off
8bfbd928-0863-4bc4-a3c7-7847686af671 | checklist | ITPS-106 Sprinkler Pipework Rough In | itp | ITPS-106 Sprinkler Pipework Rough In
22d31cd1-b630-46d3-a020-76bbf359182d | section | Details
f82c9533-6439-4e5e-b7e0-0676b3420647 | checkpoint | 1. PIPE LOCATION & HEIGHT
a187af8f-69b3-5233-92ca-d3984d30e32f | note | CIBSE W5.2 State of the System
2d187bac-2175-5b8e-b0b0-27e8595b2bee | note | AS2118.1-2017-Section 14.14
12e17198-24c4-561d-9686-673dce044c30 | textbox | Drawing Reference and Revision Number:
791f0d3e-a55f-5f5a-b3b1-1fed7d9b2df1 | button | Have you reviewed the Fabrication Cut Sheets? | Yes, No
da560eb9-e795-53bf-8e5a-2e483783fe26 | note | Is Pipework setout as per dimensioned install drawing?
1c3302bb-4df7-5a51-b74b-39adc953e4f4 | note | Are Pipe heights correct?
90f592aa-7abb-5814-93de-1988e610b2b8 | button | Have Pipework alterations been approved and recorded for as-installed records? | Yes, No
08da0f5c-84cc-50ed-9f80-854772251812 | note | Add Photo
9582bc50-7fcd-4e51-bcd4-6d0c4e2091a4 | checkpoint | 2. PIPE SUPPORTS
9c406d8a-0d88-50f3-a695-b92de4d81c95 | note | CIBSE W5.2 State of the System
51a88e62-28ad-5acf-9e5b-4c61d55c1466 | note | AS2118.1-2017 - Section 7.8
c080d3e0-2b24-5a98-8710-746a5c45b121 | textbox | Drawing Reference and Revision Number:
52cc81b6-d4e4-5dc8-a62d-e3e82466826e | note | Is the Pipe hanger type as per the install drawing?
5fc44721-590c-576a-8e65-f86a979680c1 | note | Are Hanger fixings as per the install drawing?
81a77425-6ae0-5e76-afe8-cf529a7cb503 | button | Are hangers spaced correctly? (not exceeding minimum spacing) | Yes, No
f5f0abda-1bf5-5173-9c8e-e3dfb392cd68 | note | Add Photo
91860f8c-dbc5-40e0-87fc-8086794a9fae | checkpoint | 3. CHECK GROOVES DEPTHS
d8b3184c-7c16-53df-a4be-a7b511b7e018 | note | CIBSE W5.2 State of the System
42a52dca-17d6-5e52-beb2-a51de0d0ed81 | note | AS2118.1-2017 - Section 7.1
d360560e-6601-57c6-9084-bf6240ac9acb | note | Are groove depths within tolerance?
dc9f8b13-f8f0-5efc-8a9d-cb1b4905d8f8 | note | Are pipe heights are correct?
c96f1f23-fd34-5850-a8d5-c32ad4a91bc2 | button | Have any pipework alterations been approved and recorded for as-instaslled records? | Yes, No
3ac93a50-dd03-5cdd-b273-dd170e9dba3e | note | Add Photo
ee94c532-f8bb-49ed-ad06-67136be2221e | checkpoint | HOLD POINT
4b70125b-5f35-595e-b4b9-0fcceff2a8d8 | button | Confirm Safe to Proceed | Yes, No
de2df280-5336-49b3-93c2-35d6aabb8fbf | signoff | GM Fire Sign Off
eac7d56d-1f2b-443b-a8dc-36e6e4a469e2 | checkpoint | 4. VICTUALIC COUPLINGS INSTALLED
d81cd6bc-3f53-55f0-b533-45864245a004 | note | AS2118.1-2017 Section 7.10.2.2
f0318c71-a032-5dc7-9c59-5d038010ba53 | note | CIBSE W5.2 State of the System
0e9bff68-0b5f-519c-bf55-15efb384a65f | button | Have ONLY Victaulic brand couplings been used? | Yes, No
5d45a001-1bfd-5fdd-9ecf-9d93e934415f | note | Add Photo
aa229b1f-2e25-4842-bf1d-7200d1c3843b | checkpoint | 5. CONCEALED SPACE SPRINKLER HEADS
34f57cb9-7737-5f36-9933-9b2eafb8cc98 | note | CIBSE W5.2 State of the System
fc5e635e-e161-5b50-8a57-973994262c30 | textbox | Drawing Reference and Revision Number:
3951d313-71d3-559f-a577-6c911a2e871f | note | Have ALL concealed space sprinklers been installed as per dimensioned install drawing?
b7ba56f1-85c5-57c4-a357-c99051234d88 | button | Have the correct sprinkler types and temperatures been used? | Yes, No
6f393ee0-ad88-5f61-a9cd-7544205f8d21 | note | Add Photo
f9f62352-b9b2-4bcc-ad07-d523424e7626 | checkpoint | 6. EXPOSED SPRINKLER HEADS
407c841e-1360-5545-bdbd-f429ecee9fa9 | note | CIBSE W5.2 State of the System
4338835b-c29e-5169-b1a2-3e37333f0591 | note | AS2118.1-2017 - Section 5
00e65924-3ec4-5b7e-84e7-8458a49106f1 | textbox | Drawing Reference and Revision Number:
010ae8ad-47e2-5a97-b569-ecbfc00d3d48 | note | Are exposed sprinkler heads installed as per dimensioned install drawing?
b0f4597d-bca5-5680-a037-4c5b90223e43 | note | Are sprinklers clear of obstructions?
9b1db404-659a-5928-9c8e-aec25226559e | note | Have the correct sprinkler types and temperatures been used?
3e478a44-0e24-5cc7-a35d-3a4b5d721270 | note | Confirm sprinklers do not exceed the maximum distance from the soffit?
eb955328-3983-57d1-b867-138ad3e62c7b | button | Have sprinkler guards been fitted where risk of damage exists? | Yes, No
44c90463-10fb-5b22-bb3d-fd4e9af3703e | note | Add Photo
15fd716b-65e5-4798-b9fa-d55db5a7b3ee | checkpoint | 7. FLEXIBLE DROPPERS
c3ac1e44-1bc3-5bb2-ba7f-b5268a8df9de | note | CIBSE W5.2 State of the System
1185960a-3a5e-5f0f-b80b-2cf530d094c8 | note | AS2118.1-2017 – Section 7.6
6a3e60d4-3bff-511f-924b-810685432966 | textbox | Drawing Reference and Revision Number:
56821d0f-a1b0-5884-81af-c1feb311d6e7 | note | Is flexible dropper installed in correct location?
3ba2e6bd-099d-52b6-9e0e-9243de961c31 | note | Correct sprinkler type and temperature?
448b6b77-3958-56ab-a17e-09c76267419f | button | Is there sufficient length to reach on-ceiling location? | Yes, No
b38327d3-717f-51d0-a1eb-1dc4665c7820 | note | Add Photo
06948990-aac2-4e0b-82c6-8038c0778a91 | checkpoint | 8. SPRINKLER INTERFACES - VALVES, & MONITOR SWITCHES
573b1a33-8b23-5188-b44e-e8d0b9fcb01f | note | CIBSE W5.2 State of the System
e2892b87-88dd-59c1-a457-4b927eb82cf7 | note | AS2118.1-2017 – Section 8.13.5
cbad7d0e-4f7d-54ea-b421-904fc34f334e | textbox | Drawing Reference and Revision Number:
2d83484c-6279-5426-9523-7e49c4a7090f | note | Have Isolate valves & flow switches been installed?
798f78c7-8b15-5ee5-b95f-881c2b0770d2 | button | Have labels been installed? | Yes, No
7bd261bf-ab20-5118-85fa-a4c9309b3200 | note | Add Photo
45a62451-b554-4557-8de6-575627b30dcf | checkpoint | 9. REMOTE TEST DRAIN
33b43340-9043-541f-a209-ffd8036a6f7c | note | CIBSE W5.2 State of the System
e52db621-6e6a-5e1e-ae1c-8f9c500d520a | note | AS2118.1-2017-Section 8.14
ca4c9f91-226a-5d11-a861-962cc45bdf74 | textbox | Drawing Reference and Revision Number:
f3736f9e-eb10-5586-9834-f167bd2a7863 | note | Is the Remote test valve installed as per dimensioned install drawing?
8758e221-bc2d-57b4-bffd-4c487bc60c78 | button | Restricted orifice installed? | Yes, No
a7540f73-50d4-57ac-85bd-da64fe8c17fb | button | Have labels been installed? | Yes, No
e2b7af16-de86-51f6-b2b5-1584a1ecb021 | note | Add Photo
2cdbdf82-243c-4b43-be44-f9a821535b89 | checkpoint | 10. SEISMIC
e1fde7b1-81fb-50c2-a98d-b5c467f204f2 | note | CIBSE W5.2 State of the System
b8803c41-eca4-5ddc-a508-cdf4c599cd8f | note | AS1170.4-2007 (R2018), clause 5.4.6 and section 8. AS1170.0-2002, AS5216-2018 & ETAG 001 PART 6, ANNEX 1.
f5f6ee0b-7b3a-58c0-a2a7-d85482b6651c | textbox | Drawing Reference and Revision Number:
e2a5f1a8-649b-55b6-92bf-eacc08940a6d | button | Are Seismic braces installed in accordance with Engineered drawing(s)? | Yes, No
211d453e-555f-5393-b418-902a295f6ab4 | note | Add Photo
48f8f6a2-1a20-521f-be40-528f1862556f | note | CIBSE W5.2 State of the System
f3eb7448-b6e0-5912-874d-e248eb7b8596 | note | AS2118.1-2017 Section 7.9.6
46c61920-26ce-5082-85ce-860efe6a7864 | note | Has painted pipe been inspected for damage?
4e2073b8-049f-5805-b5b6-413b8ff0d586 | button | Have Repairs to paint been completed where required? | Yes, No
5a7c7c41-0df8-54b7-b039-41590f87cc1b | note | Add Photo
fb324dc0-8e73-46b4-af7f-b42b500cad76 | checkpoint-no-value | GM Fire Sign Off
6a8192c0-cd76-4fbd-ada9-a6a44612c83f | signoff | GM Fire Sign Off
e7f2f1c7-7687-49ea-83df-32427ceb1600 | checkpoint-no-value | Principal Contractor Sign Off
6b12207d-c13a-4c55-842e-3682518ed598 | signoff | Principal Contractor Sign Off
5326775a-cd19-4e54-9ded-a2dafb455f06 | checkpoint-no-value | Consultant Sign Off
cc3ffc95-c3ea-47ae-91ef-1543df2cdaab | signoff | Consultant Sign Off
3bec76e4-28f6-44f8-ac85-3b33898ddc5f | checklist | ITPS-107 Hydrant Pipework Rough In |  | ITPS-107 Hydrant Pipework Rough In
62f435ba-8d8e-4267-a036-494a8af1c1e4 | section | Details
5f294a0a-3faa-4634-8986-4d6da3f280bc | checkpoint | 1. PIPE LOCATION, HEIGHT & SIZE
ffd32c4f-be32-5127-80a2-065232bec3a2 | note | CIBSE W5.2 State of the System
bf489797-3b34-5af4-badb-0b246723507c | note | AS2419-2005 Section 2
df1370a7-fa69-5a63-9271-5a3c02562509 | textbox | Drawing Reference and Revision Number:
61284cde-2bf6-5cf2-a8d0-6b88e5a1d1d6 | note | Is pipework setout as per dimensioned install drawing?
e37661db-37db-5d36-a971-9384b37a36fd | note | Are pipe heights correct?
4ac8caa0-1a9f-5e11-89cb-72b576b857a9 | button | Have pipework alterations been approved and recorded for as-installed records? | Yes, No
434c572f-9104-5d58-99c0-425f4affbd9c | note | Add Photo
8b48bcc9-98ab-46ce-9138-a2dc33e2bd4d | checkpoint | 2. PIPE HANGERS
59e3e634-59ce-52e6-8437-c2ee77b21848 | note | CIBSE W5.2 State of the System
fe69abde-8d21-586b-a4b1-a56b716c5386 | note | AS2419-2005 Section 8.7
e80ee5a0-a072-50b6-8f33-23e3781b3776 | textbox | Drawing Reference and Revision Number:
62ebf4d8-5ee6-5f53-b864-72ad680a743e | note | Is the Pipe hanger type as per the install drawing?
7c059818-87fd-5ccf-b137-8398430aa6a3 | note | Are Hanger fixings as per the install drawing?
038f21ad-d1e2-5fe0-8249-bda32d880e6f | button | Are hangers spaced correctly? (not exceeding minimum spacing) | Yes, No
22fd45bd-7875-5fd6-a0db-0baa2a3143fa | note | Add Photo
8becac1f-b7a4-4cad-9462-ff38d64a2c6f | checkpoint | 3. CHECK GROOVES DEPTHS
e1f957d6-52b0-57b0-be16-6e6493269597 | note | CIBSE W5.2 State of the System
477cae47-ad10-5428-8915-c8127e03b539 | note | AS2419-2005 Section 8
e5d9539e-4873-5814-a0c8-39090026e30e | note | Has Victaulic Groove Tape been used?
556cc282-031a-5a78-9229-6aed81a07752 | note | Are Groove depths are within tolerance?
17738adc-467b-5b42-968f-da8c3cd576ae | note | Are Pipe heights correct?
ea4fbd9f-61c4-58c4-8021-f39d5a7ae210 | button | Have Pipework alterations been approved and recorded for as-installed records? | Yes, No
4d7c24da-1b6a-530d-8aac-b89b1a536748 | note | Add Photo
39432a64-e4ac-4471-993b-9d06fdbcd43a | checkpoint | HOLD POINT
afba33c2-c413-5c38-ab5f-3ca280cde995 | button | Confirm Safe to Proceed | Yes, No
f7765e97-45c1-4a32-ae0f-44e18b84bd58 | signoff | GM Fire Sign Off
e9564d29-480c-4e48-9439-bb0bf4a56fec | checkpoint | 4. VICTUALIC COUPLINGS INSTALLED
59ee4c4a-7d03-58a5-bf1f-3122651bff7b | note | CIBSE W5.2 State of the System
e5bad6f7-ac9a-5ea2-9612-e20d139246ee | note | AS2419-2005 Section 8.3.2
32c9ebab-f1d2-519f-b5c5-d5a16aa65923 | button | Are Victaulic brand couplings the only couplings that have been used? | Yes, No
2416c755-5c63-5e10-a9cb-f9393396d5d7 | note | Add Photo
1e618d5a-39c1-42cd-977f-a9cc828ac7b5 | checkpoint | 5. ISOLATION VALVES INSTALLED
e220aa3f-c400-5ee8-8df6-4782f1c666b4 | note | CIBSE W5.2 State of the System
8133bb0e-1fc4-50f8-9379-cbe2052c1395 | note | AS2419-2005 Section 8.5.8
ba2fb75b-0544-5b44-ab13-e0ac11c9ee63 | textbox | Drawing Reference and Revision Number:
b23c65ca-dc81-55f3-a298-560a834a2387 | button | Are Isolation valves installed as per install drawing? | Yes, No
2720c1e4-842c-59c7-bcd1-fbd91f602298 | note | Add Photo
9990a9e7-a2b2-4d04-b6a1-95094169f641 | checkpoint | 6. SEISMIC
336d5c57-4f5d-560b-8d0f-c27b8d44195c | note | CIBSE W5.2 State of the System
2f2aeddc-5dcc-5b03-ab09-bf6afef35831 | note | AS1170.4-2007 (R2018), clause 5.4.6 and section 8. AS1170.0-2002, AS5216-2018 & ETAG 001 PART 6, ANNEX 1.
60ad117d-bffc-5476-85c8-947e65fe28c9 | textbox | Drawing Reference and Revision Number:
8c479782-879e-5b6b-a483-f108e18b57db | button | Are Seismic braces installed in accordance with engineered drawing? | Yes, No
de14fed1-ad22-591f-bab7-9c330ddb3d21 | note | Add Photo
e8d21069-2b8f-46ed-8c87-433e8e54c195 | checkpoint | 7. CLEARANCES
92fe754f-f0a9-581e-a270-cee67779345e | note | CIBSE W5.2 State of the System
acad1e71-fa47-5466-b199-c106d508bd52 | note | AS2419.1-2005 – Section 3.2
53b9ef26-afe4-59e1-bf47-b304ccd03f65 | button | Is the Hydrant positioned so it does not obstruct required clearance for egress path? | Yes, No
5db53a94-f72d-5659-bf4b-0766776be372 | note | Add Photo
bfb90b65-1496-4ea9-bd17-2f8cc6b30b1c | checkpoint | 8. LANDING VALVE FIT OFF (CLEARANCE HEIGHT/ ANGLE)
f3eda29b-093e-5d28-8fab-801199ccefbc | note | CIBSE W5.2 State of the System
4d64f2b0-7043-5a3b-a91a-3fb3c032b747 | note | AS2419-2005 Section 3.5
6b8a53a4-b198-5193-8fdf-43e688dbf518 | note | Have you checked:
c6248400-2178-5ed6-a94e-b7af64f6678c | note | Landing valve height; and
8a7e0f3a-c7e7-5bf5-bc9e-5346040a6eee | note | Landing valve is at the correct angle; and
db367ee5-0801-5280-a1b0-b138afbdd42e | note | Coupling angle and orientation is correct; and
9c016779-8fd9-5b5a-9f4d-ae0e95bf43b1 | note | Required clearance for the handwheel has been maintained; and
46393b6a-34d5-5741-a570-3d54ad927ef6 | button | The required clearance for the nozzle has been maintained? | Yes, No
45b26a73-39b4-5bae-81e9-8dbbdf5189bf | note | Add Photo
025e5666-b374-4170-893d-cd69f744a01f | checkpoint-no-value | GM Fire Sign Off
8918c39a-aed0-4fb0-8f91-243647f422ab | signoff | GM Fire Sign Off
76d0465a-8448-4d8e-86a8-b66f6e787352 | checkpoint-no-value | Principal Contractor Sign Off
7d241e3e-6169-4ec8-85a3-1db7d877b8bf | signoff | Principal Contractor Sign Off
4e5d3770-13e9-4843-80cb-9b65e299abb6 | checkpoint-no-value | Consultant Sign Off
f7f1df53-9c29-4916-ab6a-efde3b89ddd4 | signoff | Consultant Sign Off
2656663b-619a-463e-a85a-7656148ddd77 | checklist | ITPS-108 Sprinkler Fit Off |  | ITPS-108 Sprinkler Fit Off
cd93f98c-e3fc-412c-8a96-9d669fdfac57 | section | Details
06e893d8-8dc7-4a34-9837-8945b91a7532 | checkpoint | 1. SPRINKLER LOCATION
e363a997-0723-529a-9ceb-8b1b11d23328 | note | CIBSE W5.2 State of the System
960f821f-3c51-5982-86b2-f34c0550626f | note | AS2118.1-2017
9ab77831-6ab5-598a-a224-ec4f8e3f77e5 | textbox | Drawing Reference and Revision Number:
b064aeb1-532b-5de5-b045-5fb630a930a5 | note | Is the location as per dimensioned reflected on the ceiling plan/ install plan?
34c81f6e-a066-54bd-95e7-47ecfd8cc2a5 | note | Are the Sprinkler temperatures and finishes appropriate for the environment?
ca2423b7-848e-56a6-8709-b7cb6d9c8fe8 | note | Maximum spacing from walls is not exceeded
29c42419-cb48-596a-a3a7-f9988b6343ff | note | Is the wall spacing within requirements?
7a69dbaa-ec2c-506e-97fd-0b55c286301a | button | Is the spacing between sprinklers within requirements? | Yes, No
67726c2f-4e19-53e4-80ee-b08872f0307d | note | Add Photo
a4cb7c67-696b-4eef-bf24-8f9bb83518f4 | checkpoint | 2. SOLID SPRINKLER DROPPERS
287db7f7-dcf1-553b-ac10-84b7975f47b9 | note | CIBSE W5.2 State of the System
f94892ff-cdfa-59fb-a677-03a98efe8f4b | note | Is the arm piece supported by hangers?
5b822bf2-5509-5616-ab62-88389b483a3a | note | Is Dropper square?
0185e34a-7c41-5f8f-91b8-418056c0b493 | button | Is the finished sprinkler height compliant? | Yes, No
4eec11c6-0019-57ff-9586-567bba07a051 | note | Add Photo
a09f3569-8406-4fc8-85f5-b4af6e358619 | checkpoint | 3. FLEXIBLE SPRINKLER DROPPERS
1569f2ce-6348-5297-b7f4-6f886fd1e63e | note | CIBSE W5.2 State of the System
5d40cec5-393f-50b0-9b29-bbaf34f9bab3 | textbox | AS2118.1-2017
b492140d-4130-5a43-b9d0-cf2605230192 | note | Has the appropriate lengthed dropper been used?
87c4713e-dedb-5326-b716-36fff3d1a463 | note | Are Sweeping bends within tolerances?
11d16c1f-01af-50c0-89da-e346838bdac1 | note | Was the correct bracket used to secure nozzle?
f5a7a28a-d02a-5ae1-b437-bc91e45c2ba7 | button | Is the finished height compliant? | Yes, No
c0bb13f5-d884-56a3-a016-3bb3dbecce6a | note | Add Photo
ea91ad81-a014-48d0-be9c-32a6942d375c | checkpoint | 4. OBSTRUCTIONS
216da580-6944-5af0-8bb4-e6f8871ed51b | note | CIBSE W5.2 State of the System
2c1d3cbc-c8fb-5e66-bf03-51ac41cfce73 | note | AS2118.1-2017
33b2f271-9a85-5185-8f7a-01aac8e9897b | note | Has minimum clearance been maintained for 'On Ceiling' obstructions?
263208b1-06ea-59aa-b466-2ad0ddfbb37e | button | Has minimum clearance from sprinkler been maintained for 'Below Ceiling' obstructions? | Yes, No
fa862bea-8f62-5c7d-b746-d2bf917004e3 | note | Add Photo
26b9a9a8-5bae-4d1b-9ced-d87fa0df73c7 | checkpoint | 5. ESCUTCHEON PLATES
9d0c7edb-f3f9-5df0-8eed-a7375e08172b | note | CIBSE W5.2 State of the System
6b3c5d65-fe29-5954-8677-54f75fd97496 | note | AS2118.1-2017
b2c94200-a435-5292-af8b-82e4fe669585 | note | Have outer escutcheon plates been fitted?
fd4d4c39-24e1-5fcb-84c8-d2bc019b5536 | button | Is surrounding ceiling clean? | Yes, No
aae65c67-daec-569c-ae34-b963fe869aff | note | Add Photo
4ef3fb00-f60c-44a2-8fc0-ec2a3ebfdd71 | checkpoint-no-value | GM Fire Sign Off
1e0a9961-618d-4ff7-afe9-b0f5b332e642 | signoff | GM Fire Sign Off
c5f1611e-70c3-4a72-b3b1-72d40b2b9034 | checkpoint-no-value | Principal Contractor Sign Off
4c142fd5-b3ef-49be-a501-50ac108ec908 | signoff | Principal Contractor Sign Off
b3069219-cb3f-49e6-9841-21765f2c3bb7 | checkpoint-no-value | Consultant Sign Off
926cd227-f131-40ed-a3c3-b3922924e99e | signoff | Consultant Sign Off
3c94fee6-d985-40ce-864f-83e38f30066a | checklist | ITPS-109 Portables Fit off |  | ITPS-109 Portables Fit off
4eaa3a14-d9c1-4f90-aab6-b6e250ef39bc | section | Details
2e861c61-9830-4f94-9ed2-906f1f987fe4 | checkpoint | 1. FIRE EXTINGUISHERS - GENERAL LOCATION
e64466c1-9a88-5bca-b5c6-b1a8bb74e68b | note | CIBSE C5.2.2 Set Points
7d9b8303-2cc4-52a8-801d-e45ebd07ee34 | note | AS2444-2001 - Section 3.2 states extinguishers shall not be located in positions where access could present a hazard to the potential user.
7daf8496-0c03-59ff-8c91-7194a7811c97 | note | Is each extinguisher located in a conspicuous and readily accessible position?
5c105334-b1c8-50d0-ae72-5716aa5ab3d8 | button | Where practicable, are extinguishers located along normal paths of travel and near exits? | Yes, No
f1d81fc3-9bbe-53ec-b7f5-b68086f085d9 | note | Add Photo
2af9710d-ebcf-4649-b14e-2a66bffefc8a | checkpoint | 2. FIRE EXTINGUISHERS - MOUNTING DETAILS
4205f145-aee5-52bf-846b-827814b32d77 | note | CIBSE C5.2.2 Set Points
0acc50cd-43fd-5e60-91ff-ab07caab9bfd | note | AS2444-2001 - Figure 3.2
ce3a60d7-f6a8-5408-a446-4c8efc55f105 | note | Have Location Signs been installed at a Minimum of 2000mm off the FFL?
1580328d-7c99-5e64-9afe-961c8ed07cda | note | Are extinguishers installed at a maximum of 1200mm to the top most part of the extinguisher?
85fe1f7e-c895-5dbc-bbd1-675f3ad6eb40 | button | Are extinguishers installed at a minimum of 100mm from the FFL to the bottom most part of the extinguisher? | Yes, No
f4db7362-8527-5b50-a757-6b6e1e6b08e3 | note | Add Photo
695e50b0-7e81-4674-af6e-8f4699550f98 | checkpoint | 3. FIRE EXTINGUISHERS - VISABILITY & SIGNAGE
f599fe6d-a6a7-5b68-b24e-a2cc24d44332 | note | CIBSE C5.2.2 Set Points
92b96452-eace-5d78-9ee8-3d61e541dd50 | note | AS2444-2001 -Section 3.4
d2563b05-b4be-5558-ac85-d999fd110916 | note | Are extinguishers, or extinguisher location signs, visible from a distance up to 20m in all directions?
916355c3-d1ba-5885-b1a5-b59cb4e055d7 | button | Are the location and type of extinguisher signs installed as required? | Yes, No
96912b2e-547b-5c6d-a319-3b5881c9b5fd | note | Add Photo
7e90ea0a-cbd8-4759-900c-cde805fb2d26 | checkpoint | 4. FIRE BLANKETS - GENERAL LOCATION
6e602443-3cb7-5c0f-9869-80cf9e5403c1 | note | CIBSE C5.2.2 Set Points
82a001f8-cb0d-58a7-a344-5bbbd282d805 | note | AS2444-2001 - Section 6
bb804644-405e-5a2b-ac20-7340c3087214 | button | Are Fire Blankets installed in a readily accessible position, and not in a location where access could present a hazard to the potential user? | Yes, No
d02dcfd9-dc83-5fa2-9e8e-3b197f47dea7 | note | Add Photo
e752bb83-4877-4df8-acaf-e9a5a277c80f | checkpoint | 5. FIRE BLANKETS - MOUNTING DETAILS
79d37f54-1664-5f37-b36a-6d69e8c1360f | note | CIBSE C5.2.2 Set Points
3747f57b-f806-54a4-95ce-9965eed40d2b | note | AS2444-2001 - Section 6
28f260ef-bbea-5452-8d67-a0e8af971962 | note | Have Fire Blankets been mounted to withstand the loads imposed when removing the fire blanket from its container?
c0d01a3d-6701-5fca-bf75-4b9a48629b42 | button | Is there sufficient room so that fire blankets can be quickly removed without impedance from nearby obstructions? | Yes, No
51f03e58-7045-5c08-97ae-bf087f91d112 | note | Add Photo
71d6f08a-517e-4ad5-93c6-00653cfc0312 | checkpoint | 6. FIRE BLANKETS - SIGNAGE
5dc2af7e-441e-5f9e-89ef-4477445c8fbd | note | CIBSE C5.2.2 Set Points
8cd8c058-5d35-55af-a37e-6568f83b1a98 | note | AS2444-2001 - Section 6
a1e2db7e-804a-519c-b9f5-1555d165439a | note | Are signs located above or adjacent to fire blankets?
f59229ac-a02b-5636-a17e-3a5355f8fd2f | button | Are signs 2.0m above floor, or at a height that makes them most apparent to the average person? | Yes, No
11f1b1a6-cc53-51a6-823a-dd7d5e1e3e4b | note | Add Photo
890d110d-f125-4fe0-869a-ea7952a18029 | checkpoint-no-value | GM Fire Sign Off
d19777bd-7736-4818-961c-941822f4a204 | signoff | GM Fire Sign Off
55e6cb51-3be9-4219-bc9d-6e6c2c256cdf | checkpoint-no-value | Principal Contractor Sign Off
c26cbe95-20c8-4fa0-bdca-ce3253ccda95 | signoff | Principal Contractor Sign Off
bf962b44-56bf-4231-8b85-69362893f0f8 | checkpoint-no-value | Consultant Sign Off
eb1a28d7-7aea-4be0-8bfc-d125dc08c25f | signoff | Consultant Sign Off
dfd69d60-d8ab-4913-be4f-ce6e7e6ae080 | checklist | ITPS-110 Valve Set Installation & Fit Off |  | ITPS-110 Valve Set Installation & Fit Off
2b04f83a-d165-4319-b1b6-2ce23c9c4d36 | section | Details
6449cbf5-c6a1-4669-8884-ffa797472e7c | checkpoint | 1. UNDERGROUND SUPPLY
a464b0a6-5346-5877-903e-cb3599163102 | note | CIBSE W5.5.2 Flushing Procedure
a175d988-82b3-5a6e-be9e-b98b89d5cb7d | note | AS2118.1-2017 - Section 7.9.7
a6387bf6-2a8e-59f7-9be4-66115a757fc0 | button | Has all supply pipework has been flushed by a hydraulic contractor? | Yes, No
09705a84-d5b2-5d21-b380-fec3ea1d26ea | note | Add Photos
64cbc970-d63d-41b9-b1a2-81bdb8235d9b | checkpoint | 2. CHECK GROOVES DEPTHS
0d0c8f8f-d9d5-5699-8214-564fbd68ebfd | note | CIBSE W5.2 State of the System
f3a597bb-4344-50c3-9375-a4f7045204d0 | note | AS2118.1-2017 - SPRINKLERS: Section 7.1 | Yes, No
5277547a-18da-5cdb-b9e5-96a3d3d77c3c | note | Has Victaulic Groove Tape been used?
3053c81d-c108-557c-bc8f-24646f089d14 | note | Are Groove depths are within tolerance?
d117b1ef-8f82-5694-946a-1ad057c1e124 | note | Are Pipe heights correct?
93fe9d78-738d-5dd1-b653-c379732ddcca | button | Have Pipework alterations been approved and recorded for as-installed records? | Yes, No
c0e1f919-b445-58ca-9661-52a2f8772b5d | note | Add Photo
cde92c7c-1f13-4c49-bcb8-58348a4ec24b | checkpoint | HOLD POINT
185b22cc-0518-57c2-86ba-607a06ffe936 | button | Confirm Safe to Proceed | Yes, No
59df514e-18f8-4abe-9825-c40eecc9a153 | signoff | GM Fire Sign Off
386163ac-76b9-499d-b75a-5e6a7338b565 | checkpoint | 3. VICTUALIC COUPLINGS INSTALLED
b4e507c2-ca52-5d6f-abc0-381723cbf862 | note | CIBSE W5.2 State of the System
3f334da4-f470-5d85-9c08-1d191279b19b | note | AS2419-2005 Section 8.3.2
5823586a-ffd9-5a68-a0ea-f388b3d7dcaa | button | Are Victaulic brand couplings the only couplings that have been used? | Yes, No
febc3e94-a25b-5873-8bb6-9b47993cd558 | note | Add Photo
6f68c017-4882-47c1-bbee-1c751bce0656 | checkpoint | 4. CONTROL VALVE ASSEMBLY
d7a6032b-a2cd-53c4-905e-8ac46ce1ef36 | note | CIBSE W5.2 State of the System
30258b79-84f1-5dad-a493-bcd02eb334f5 | note | AS2118.1-2017 - Section 8.1
7a304873-2d94-5830-868b-bed367a1a954 | textbox | Drawing Reference and Revision Number:
31fe27ff-5b85-5c14-8ef1-5c08958a339d | button | Is the assembly is installed as per drawing? | Yes, No
d3c954da-3787-5e81-bd4a-27b2e7212f64 | note | Add Photo
98a7bf15-fed2-44a7-ab69-81b9c5aba243 | checkpoint | 5. PIPE SUPPORT
3dc5f226-b0b5-579f-8d63-3b306882f777 | note | CIBSE W5.2 State of the System
e6178f5b-714f-5ab7-aee9-2261bba5cf0e | note | AS2118.1-2017 - Section 7.8
72268aef-b5e1-58ea-9b0a-73805273515f | note | Are pipework supports as per drawing?
beb8aa76-a1e3-5b8f-a180-44d0816649ef | note | Are the supports capable of supporting assembly weight?
74b8c2f1-8094-5359-9d48-3942a82b2c46 | button | Are the supports capable of withstanding forces during operation? | Yes, No
c50ca823-72d2-573d-b473-9420ff3f8691 | note | Add Photo
1903e252-71bd-443f-b37f-2eac9f560ee6 | checkpoint | 6. VALVES
17792783-f055-52d3-b9c8-fec688f85d0c | note | CIBSE W5.6.2 Mechanical Checks: Automatic Control Valves
ebcea25c-44f5-53dc-b0eb-1519cd523e6e | note | AS2118.1-2017 – Section 8
466e7d71-1b92-5663-9bf2-71a6749130d2 | note | Are Valves installed as per drawing?
f68a0745-71d0-5007-bfa1-0d89c18ad69c | note | Are valves are installed in the correct orientation?
70872051-f921-5e9c-979c-bb18cfa78df3 | button | Does the clearance allow for manual operation and future maintenance requirements? | Yes, No
91e316a9-1530-52a9-a291-e30432d4459e | note | Add Photo
0e0deed8-7b30-4572-944b-eab08320bfac | checkpoint | 7. INTERFACES
225b708d-cf44-5a6c-8be1-e829b331456b | note | CIBSE W5.6.2 Mechanical Checks: Automatic Control Valves
12c80133-eca9-5287-ae98-389d0be7610d | note | AS2118.1-2017 – Appendix H
63b9778f-8550-5198-9cf6-17fdb8dd6939 | note | Are valves/switches installed for connection by other trades?
dd6d1521-7591-54d6-a832-236438f8c8ae | button | Have clearances been provided for connection? | Yes, No
f7f0b807-6f6d-5a1e-a766-ac39852d66a7 | note | Add Photo
65dfa71b-b1c1-480c-844a-0fa2fcdaa48b | checkpoint | 8. PAINT / FINISH
9893e53c-2d38-5454-b3be-40e59d4137b1 | note | CIBSE W5.2 State of the System
d333bde6-00a2-5e7e-b05c-a363d9e11dc8 | note | AS2118.1-2017 Section 7.9.6
9d1b5de9-a1cc-5900-965c-86530803a3c4 | note | Are exposed mild steel pipes painted gloss red (unless specified another colour or galvanised pipe)?
fbd77eb2-5767-539f-a947-26e07c3f76d6 | button | Have threads been de-hemped and tidied? | Yes, No
29b50117-a2da-5eaf-986b-5232c0c67336 | note | Add Photo
e8032c8f-34cd-513f-af7e-deaa2402cef2 | note | Add Photo
a0e00af4-6bf0-4f2d-9ff6-b96875c4abc6 | checkpoint | 9. SECURING VALVES
efae4b0c-caef-53b8-ba65-490fdb99c48a | note | CIBSE W5.2 State of the System
67c9c7ea-26e2-503a-adb5-63a6e341c88e | note | AS2118.1-2017 – Section 8
31123513-3ecd-54fd-910a-aa43941fd103 | note | Are valves secured by 003 locks?
ab5ea199-8823-5a88-aca2-8a99ad80c0e6 | button | Have straps and chain been installed? | Yes, No
4336aa81-358a-534c-ac66-ca629245ebdb | note | Add Photo
1ca35220-4cee-4ad8-9741-d847adc8d160 | checkpoint | 9. SECURING VALVES
69cb1209-705b-563b-92ba-c904aec402e2 | note | CIBSE W5.2 State of the System
42b8d40f-19ab-5281-8e75-390f5967a314 | note | AS2118.1-2017 – Section 8
a74aa968-d1ab-5f85-98e5-fc064bc0a9fd | note | Are valves secured by 003 locks?
19baab35-2622-538c-b879-e88010c6423f | button | Have straps and chain been installed? | Yes, No
8dd0f59c-8eb5-5e3b-b32e-b5ccd669df90 | note | Add Photo
d39a4ad4-8ebf-4ed1-9d1c-48f7f5004bf4 | checkpoint | 10. LABELS & SIGNAGE
a7fdef1c-a904-5c14-81f8-27cee71a4dc7 | note | CIBSE W5.2 State of the System
b0bed829-f767-5d1c-a0dc-c0325b42b36a | note | AS2118.1-2017 - Section 3 (3.3.4)
874697fb-c885-59e8-9934-83d7c6233f96 | note | Are Equipment name labels secured?
d6b09339-b2f7-521c-8306-fa3f41ccb420 | note | Are Valve position labels secured (normally open / normally closed)?
6adcbed7-8b9e-5084-b4f2-6bb01a192bc6 | note | Have "Sprinkler Stop Valve Inside" signs been fixed at the valve set enclosure entry?
409fee4c-a418-59e2-a117-123e2c825996 | button | Has the Sprinkler Block Plan been installed? | Yes, No
dd979100-1c9e-5222-9a33-0b83a74d6ae2 | note | Add Photo
8096a543-93e5-42e5-a405-11acba01104c | checkpoint | 11. SPARES
6055d0fc-bd9b-51cb-90a9-9174bc38954b | note | CIBSE W5.2 State of the System
9d41303b-32c3-5d6b-bdf8-d041401ee8cf | note | AS2118.1-2017 – Section 6.7
a73a008b-dbfd-542b-b4d7-5d8f1ed1b224 | note | Has the correct size sprinkler spares box been installed?
0c5c8b77-a943-5225-a4b6-97c0ce15e049 | note | Have the correct number of sprinklers been provided?
8a3f6e24-d883-5f06-9136-a4cddbc4eae7 | button | Has a sprinkler spanner been provided? | Yes, No
bdcb7dd5-1d65-50af-887d-2b114b652318 | note | Add Photo
29fe5f39-326b-4c81-967b-6f5000091a3c | checkpoint-no-value | GM Fire Sign Off
6c4dd1ca-5a6a-4605-a9ac-813eb3539950 | signoff | GM Fire Sign Off
1aeeeff1-4b4f-45dc-a405-42c6a4dd1338 | checkpoint-no-value | Principal Contractor Sign Off
e831054e-1d41-4832-93dd-4c940a406a9d | signoff | Principal Contractor Sign Off
afd375a5-f884-4181-96cb-5eaf1c7c4389 | checkpoint-no-value | Consultant Sign Off
1d856dab-ec95-45bd-8ff2-bbbbbcc5c07c | signoff | Consultant Sign Off
8687af50-552f-487a-ae54-d4f481d8a169 | checklist | ITPS-111 Tank Installation |  | ITPS-111 Tank Installation
fc0e8317-548d-4314-b3a9-c07312c23739 | section | Details
a22365f1-7c85-446f-aeca-cdc5f0a3c120 | checkpoint | 1. LOCATION, CLEARANCE, ELEVATIONS
a390fb86-8a21-5f7b-9ef5-96d2e36abcdc | note | CIBSE W5.5 Pre - Commissioning
41de5e67-a48e-5e1e-8667-3e823ea89b92 | note | AS2304 - Water Storage Tanks
1d036232-5b2d-5b62-b72c-97754da694d7 | textbox | Drawing Reference and Revision Number:
123cdc47-61a8-55c9-9d5f-b273dc247b91 | note | Are Structural Elements as per AS2304 – Section 3?
880196a4-1bef-54b3-a33f-7e070c213793 | note | Is the correct Installation drawing onsite?
370f7b4a-5dc4-5480-9fd9-b073c10b5420 | note | Is Ladder selection and orientation as per the submitted design drawings?
d09f8987-9a11-5a9c-809c-0ee8ba86f544 | note | Is Nozzle selection as per submitted design drawings?
e8ab122d-63e7-5bf6-8d1d-bd98d1117261 | note | Has the poisition of the Tanks been confirmed with the Principal Contractor onsite?
1337aa11-e97e-5c94-8e35-7eada4101b25 | button | Have you check the subcontractors Competencies and Authority to work? | Yes, No
7ebd5802-a038-5d1b-a071-868c8c3b19c6 | note | Add Photo
ea598a35-444f-49c9-b71b-f08c8acfccde | checkpoint | 2. COMMISSIONING
565b5dd7-e8f9-59d9-a9be-8b5149d03233 | note | CIBSE W7.10 Commissioning Certification
0fc247a7-ea76-5f06-b109-148ffaa8518e | note | AS2304 - Water Storage Tanks
8d32936f-dc40-5d54-8243-acc01dac22e1 | note | RECORD, CHECK, INSPECT
1d9e31bf-e5b6-5106-9c2f-aa7cec8306a3 | note | Structural inspection was complete prior to filling; and
7abac534-48ed-5e4a-be18-00766db538e3 | note | All ladders have been inspected for conformance and clearances and position of tank accessories (AS2304); and
7a4b34d3-754b-5793-a059-3f7ec804e70c | note | Hydrostatic inspection was performed after tank is filled to maximum capacity; and
6b56ef14-79a0-5a7a-be00-10038b731436 | note | Any defects have been recorded; and
94c9b296-5d29-5c46-8111-fdb2e871c859 | button | Have Certificates and warranty periods been submitted? | Yes, No
2309e647-db38-583b-bb23-15217316cc86 | note | Add Photo
534b0b66-b26c-4978-b907-d140028e545e | checkpoint-no-value | GM Fire Sign Off
fcd8d888-7c5a-45e5-ace3-f7e4a6f251ed | signoff | GM Fire Sign Off
ef0307f8-7bde-4199-9def-e6e84c270287 | checkpoint-no-value | Principal Contractor Sign Off
0955f83e-ac69-4f98-8257-d90b177dd5a4 | signoff | Principal Contractor Sign Off
f62bf0ae-1cf2-4404-b5eb-b1e71c484066 | checkpoint-no-value | Consultant Sign Off
17a05a8d-05a0-4eaa-9442-87ada44c57e4 | signoff | Consultant Sign Off
3ad1f367-b421-4c13-8523-432f26b7d95a | checklist | ITPS-112 Deluge Rough In and Fit Off |  | ITPS-112 Deluge Rough In and Fit Off
09742c20-7e18-4cda-af54-f4e370232910 | section | Details
d6b6a001-f53c-4cd1-b1e0-0fa711e824f8 | checkpoint | 1. LOCATION - VALVESETS
6048ba7c-f85a-57ab-9b2e-e367d048c198 | note | CIBSE W5.2 State of the System
c5cec673-ba62-5ff3-b582-5c71255f746f | note | AS2118.3
395d2a2a-dea4-5b9b-8bd5-91b7aa58e602 | textbox | Drawing Reference and Revision Number:
cb99ea1a-2bc8-5c11-840e-aa10bfe44e70 | note | CHECK:
789acea7-0770-5d59-a5c2-7cf130a84ec1 | note | Valves located outside building shall be considered protected if the external wall has a FLR of 60/60/60 or be situated at a minimum distance of 10 m from the wall.
e7008cb0-4149-585a-bd42-bb658eecbe1f | note | Valves located inside the building shall be situated at a minimum distance of 10mfrom the perimeter of the protected area.
0b79a12f-b98a-5c82-94b4-6f0331c504bb | note | TRANSIT TIME:
05f1ba47-4e6f-5b4d-9b7c-41d68584c731 | note | Deluge valves shall be located as close as practicable to the system they are controlling. This will help ensure that the transit time to the most remote zone is no more than 30 s.
e93af753-b756-5b18-9d0b-59d6a3b26456 | note | Add Photo
55bf3d0f-f443-4630-b355-632320be7291 | checkpoint | 2. LOCATION- DELUGE HEADS
15dd762a-7f96-5c93-8fad-15a00850bd9b | note | CIBSE W5.2 State of the System
287625b8-3af6-51ab-ad36-d53d4942370e | textbox | Drawing Reference and Revision Number:
0762ed55-510c-54ba-b414-2f9d369e5776 | note | Are Deluge heads located as per dimensioned reflected ceiling plan / install plan?
db81fe18-3439-52d4-804e-aab34b06b957 | note | Confirm sprinkler temperature and finish are appropriate for environment; and
1a9c07c2-8f56-5cb9-9635-960f689f8f76 | note | Maximum spacing from walls has not been exceeded; and
ff57a180-d7e2-5c1e-9e55-9c6a059cb939 | note | Maximum spacing between sprinklers has not been exceeded; and
80e6e82b-8eb2-590c-bad9-ecf3fadfac18 | button | All is as per manufacturers detail and FER? | Yes, No
3f0552fb-f445-5f0c-9b7c-421fea6ec099 | note | Add Photo
2375959d-5204-4409-88d9-c465f25e0742 | checkpoint | 3. DELUGE HEADS & PIPEWORK
cdd34905-990b-59ef-a99d-a110dfa5c589 | note | CIBSE W5.2 State of the System
0bd1721d-7159-542e-aa27-d58465dc01e4 | note | AS2118.3
9208134b-620c-51e0-b8d4-0569d96de49f | note | Open sprinklers are be nominally 15 mm or 20 mm diameter, and either upright spray (SSU) or pendent spray (SSP) pattern only.
09a4e3ae-69f9-5c0d-92b2-b235768c162d | note | Deluge system pipe and fittings not normally filled with water or foam solution shall be hot-dipped galvanized.
ff775110-5139-5896-9690-f5dded889a1b | textbox | Deluge Sprinkler Head Type:
64f90dca-840d-5e9f-b2ba-af3cc8cb94a7 | note | Add Photo
965ebf20-c160-4d9f-88aa-14f27c6ecd6d | checkpoint | 4. WHERE SPRINKLERS ARE USED AS DETECTORS - SYSTEM PARAMETRES CHECK
43d3fe80-dd28-5509-a113-561509fffe4f | note | CIBSE W5.2 State of the System
54ba5703-71a8-50e3-85a8-a8694437b7c8 | note | AS2118.3 Section 2.9
2c523186-95ba-5c7f-b42f-d8d038e77d6b | note | Where sprinklers are used as detectors, ensure the piping layout shall be designed to ensure a response time of no more than 20sec after the operation of the most remote sprinkler or manual operation.
cc18ceaf-57b0-56d3-a03b-b37197d7ba23 | note | Manual control shall be located at each deluge valve and at a strategic point/s within each zone.
d0d8589f-6419-5f49-b822-c45041949c50 | note | Deluge valve trim shall be in accordance with figures 2 &3 in AS2118.3.
0fca5736-fd25-5d3e-b954-426e9800c044 | button | Ensure a remote test drain line is installed (close piping deluge systems) | Yes, No
a88f5468-3924-593d-984a-5f2ab1586ed8 | note | Add Photo
2ce9bceb-620b-491b-a2e9-3ac0848f82d6 | checkpoint | 5. SOLID SPRINKLER DROPPERS
f5a57e1c-f068-52da-92ec-78e7db105b6c | note | CIBSE W5.2 State of the System
c0177a8d-13f5-5fbf-a32a-0b6a59e00f69 | note | Is arm piece supported by hangers?
3b3d37eb-0c5f-51a2-ab99-39d65dd05916 | note | Is the dropper square?
8d5a6245-6d5d-563b-b4bc-e50552468890 | button | Is the finished sprinkler height compliant? | Yes, No
d93769e0-d042-5bd1-9b6c-0f8b2e119234 | note | Add Photo
64570fe2-3ce9-4065-a903-9a907ffbf2c5 | checkpoint | 6. OBSTRUCTIONS
aeabbd54-626d-58e2-a720-c88330be9cba | note | CIBSE W5.2 State of the System
50e8484b-d4ce-565f-8425-f27216fdead0 | note | Has minimum clearance been maintained for "On Ceiling" Obstructions?
2f24e6aa-9fe3-54cc-9410-44cb8c7d4397 | button | Has minimum clearance from the Sprinkler been maintained for "Below Ceiling" Obstructions? | Yes, No
3e385781-0eaf-496b-bdf4-303b46ed9ec3 | checkpoint-no-value | GM Fire Sign Off
6e80da72-0fe8-4333-9b72-5c963eb53b21 | signoff | GM Fire Sign Off
e07e976a-f94e-46c1-b399-4f1fddb06718 | checkpoint-no-value | Principal Contractor Sign Off
5c764144-8f36-4061-97d0-fa3077e1ce76 | signoff | Principal Contractor Sign Off
6541ed41-7780-41f8-81c5-dbf7dcace285 | checkpoint-no-value | Consultant Sign Off
16d58737-5e4b-430c-b2f2-412224e64465 | signoff | Consultant Sign Off
58719156-38ff-47d1-8c2c-80a3f5a1dc8f | checklist | ITPS-113 In Slab Sprinkler Sleeves |  | ITPS-113 In Slab Sprinkler Sleeves
99a2c5d2-736d-410d-8011-ecb695e22873 | section | Details
6300af7c-f34c-4047-afca-8ae2ba384c15 | checkpoint | 1. TYPE, SIZE, QUANTITY - CHECK
ebc8a22e-30af-51e5-8aa1-46a9d8dfd04c | note | CIBSE W5.2 State of the System
d0c5ae5e-8040-5d6e-bfbe-069d51f2e0d8 | note | AS2118.1-2017
fac90cdc-0fc0-5860-a484-1e7d4f395715 | button | Are sleeves the correct size, type and quantity to criteria and specified drawings? | Yes, No
579228ea-f1c3-52c8-a47c-06dad59d509d | note | Section 9.5.2
3e4e58b7-4552-51f9-8f88-26d25836f17b | note | Has pipe with a minumum DN 25 been used;
3ae42212-71ea-571f-aced-5e3c21570a12 | button | Or where a pipe supplies a single sprinkler protecting an external balcony, canopy or carport, or supplies a single exposure sprinkler, a minimum of DN 20? | Yes, No
0323cd64-b94f-565e-ab50-1e569f71989b | note | Add Photo
c7404944-0e9d-4014-8cfd-506796d72e88 | checkpoint | 2. LOCATION - CHECK
fe5ff496-48ae-5b63-a890-889dc2208ba0 | note | CIBSE W5.2 State of the System
7076c8ab-8e05-5d5a-a504-a587572e9da4 | button | Have sleeves been installed as per specified layout and design criteria? | Yes, No
eecd17a0-d443-5868-87c6-b473e2b76746 | note | Add Photo
03b7cc8a-9342-4af3-b664-0c6269abbd88 | checkpoint | 3. INSTALLATION - CHECK
a8ed2b66-8090-56fc-9012-8fc07dd41ec8 | note | CIBSE W5.2 State of the System
2ea86e41-581d-578b-aeba-12053e7a108a | note | Are sleeves joined correctly and tied in?
68e2c9a4-7d9b-5229-94e0-da4a5603a84e | note | Have sleeves been checked for damaged?
8ada77ba-261a-5ad5-921c-bb9a4564b81e | button | Have you ensured sleeves are not resting on form work? | Yes, No
2c08af15-41cd-59e0-9aa5-6402d80547f7 | note | Add Photo
376fb219-4c94-4d0e-a16f-aac9e43e8d9c | checkpoint-no-value | GM Fire Sign Off
9eb85361-cfea-4414-b356-29e5d4dbeb0a | signoff | GM Fire Sign Off
5478753a-c535-4d97-857c-8e8d7381b7a2 | checkpoint-no-value | Principal Contractor Sign Off
da4d61e6-24cb-467b-9842-6f95b7de3d02 | signoff | Principal Contractor Sign Off
a0b32623-7842-4188-a64f-cd8538cbbf80 | checkpoint-no-value | Consultant Sign Off
a51e5f8d-0384-45d9-85a8-2aca1c96b5e5 | signoff | Consultant Sign Off
7f6f804a-e3c5-4574-8d7a-08c4cad13356 | checklist | ITPS-114 ASD Rough In |  | ITPS-114 ASD Rough In
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
194d4211-d273-4ce0-b4cd-6a96b9c5d52a | checkpoint | 1. LOCATION
196e9112-db4b-54cc-9bf9-08e0d2e02a34 | note | C5.2.2 Set Points
1497423f-41d0-51cd-81e1-75a2e1198289 | note | AS1670.1
87c63f73-924f-50d4-81cb-128511d44a1c | note | Have you check that the ASD device does not cover an area great than 2000m2?
61b67e0c-6d59-59ef-98fa-27f8e39e92c4 | note | Is the ASD unit in an accessible location with no obstructions?
ce18931f-e4ff-53c9-b9a9-7368bdcf7e05 | button | Is the ASD unit free from damage? | Yes, No
a0164f2a-f0d8-5a44-bda2-7af9f22d7324 | note | Add Photo
5973b7f8-12fd-4f99-a66a-97f1b2a9ad22 | checkpoint | 2. SAMPLING POINTS
f33faaeb-0b70-542a-bfcf-26130b6e8bc0 | note | C5.6.0 Sensors/Detectors
21595fd6-85b1-56f8-94ae-66a55b9344fe | note | AS1670.1
7c6c7d96-59c4-5a2f-9cf0-948d2c81e3ea | note | Are ASD points unobstructed, unpainted and free of burrs?
46b84e96-dbcd-587e-98ac-205cfd12a115 | note | Have ASD points been labelled and identified as required?
c5cbe3f9-0760-5afe-9056-8774d86697a7 | note | Are ASD points installed in accordance with spacings of point type detectors?
cf820255-2af6-544f-b899-4270a1886e72 | button | Have you confirmed ASD points are no more than 600mm below ceiling? | Yes, No
7816eb51-0764-5547-b7c6-e691580dfc80 | note | Add Photo
ae113c84-4b5b-4c61-81b0-4837ac7d45d3 | checkpoint | 3. EXHAUST
cb399a00-77d1-5689-aa6a-063cf7b21f2b | note | C5.6.0 Sensors/Detectors
16f50128-f9e9-51ac-9d02-0613883b2edd | note | AS1670.1
94c03e48-9861-5454-9b5f-9b54982dce28 | note | If the ASD is mounted outside the protected area and the potential for pressure differentials can occur between the sampled and exhausted air:
708b6107-2dd2-594a-95f6-51463a01f5eb | button | Are the exhaust outlets returning back to the protected area, or as per system design? | Yes, No, N/A
f7eeac9d-2e29-5708-947a-1df8645a2273 | note | Add Photo
d64973f9-5d7b-4fcc-8b05-c76006bb7ae3 | checkpoint | 4. OTHER INSTALLATION REQUIREMENTS
83beb1b7-bb5d-56ee-bc7f-3c93224d7c5c | note | C5.2.2 Set Points
57330365-b796-59ce-b277-7ee8b69bc89c | note | AS3000, AS1670.1, AS3013, AS/CA S009
40f78918-027b-58b2-b1de-c7b93a035a09 | note | Are all sampling points AND capillaries red in colour OR have visible red stripes at least 2mm wide at intervals no more than 2m?
25fd2b5f-50df-5f01-9a7e-31e6f9af3ef8 | button | Is the pipe orientated to ensure identification of markings is visible? | Yes, No
28249dd2-f16a-5f42-9dd2-85db9b174da6 | note | Add Photo
3a5f34db-81b1-4754-b0ff-2022228b8ff0 | checkpoint | 5. CABLING
b4024ad9-aa4e-532f-a292-e8ff057db65f | note | C5.4.0 Wiring
6b744e7a-0c38-5a35-bb32-f7391bf5e183 | note | AS1670.1, AS3000
1001f4e6-02bc-5bb6-ae97-4ae9f4dc26a0 | note | Is the cable installed the correct size & type?
a015bb34-6378-5f27-ba96-fb1f3fad9efa | note | Has cable been secured at regular intervals?
90c2147f-c351-5867-9a77-f6e4302aec97 | note | Has 24v cabling been installed where required?
08c0f632-a749-54be-8188-5b7c943253b1 | button | Is the power supply in accordance with AS1670.1 Cl 3.15? | Yes, No
9d5d5bc9-2815-592a-bf08-65e48f69f7a0 | note | Add Photo
120aad56-a103-49bb-af7e-3a8dd5c2f152 | checkpoint | 6. PIPE LAYOUT
73407f14-ce6e-512a-81d1-c5b46957f94c | note | C5.2.2 Set Points
a90530a5-ec85-58c7-9ccd-1bd0dc0137b6 | note | AS1670.1
7365b95f-cc84-5d22-8291-e6b914c00339 | textbox | Drawing Reference and Revision Number:
2175bd18-c2d1-5f10-8571-3b0f4342aa88 | note | Is the ASD pipework as per Aspires or Calculations?
1a6eaff3-c569-51ff-ad13-ec28a658bc19 | button | Have you confirmed the pipework layout with measurements? | Yes, No
f746b1cf-1c01-5bfc-b6b0-d57a7bf8a3f6 | textbox | PROVIDE measurements:
375b0072-6b90-594d-8510-731f20e25a0f | note | Add Photo
51d40205-b8c7-4747-a107-43a888f436be | checkpoint-no-value | GM Fire Sign Off
80841e58-4705-4987-966c-e31793ae3cdd | signoff | GM Fire Sign Off
e6ad46fa-b388-4576-9ed6-27c4c8cd1abd | checkpoint-no-value | Principal Contractor Sign Off
f9d5d875-25c2-4873-88a0-930030c7765c | signoff | Principal Contractor Sign Off
c52acb33-a31b-40a7-8b24-11a84e2638f0 | checkpoint-no-value | Consultant Sign Off
75790914-1d1e-45b3-83f3-5fe672292fb7 | signoff | Consultant Sign Off
c7adbb4e-8a2a-4072-ac4d-6b7dc792913b | checklist | ITPS-200 Fire Detection and Alarm Commissioning |  | ITPS-200 Fire Detection and Alarm Commissioning
0b0fb1f7-72bc-4c4c-9146-6df670b3fe7e | section | Details
7ea73a77-a9d6-4785-a315-82c9478fdbd9 | checkpoint | 1. CONDUCT 100% TESTING OF ZONING
01c91a1c-6ad9-5092-abb4-aa784e3e5482 | note | CIBSE C5.2 Dry Fire Commissioning – Automatic Controls
383939e6-b2fc-57db-9877-4833cf331ce6 | note | CIBSE C5.2.9 Alarm Functions
4ef0b21d-d28b-500b-9d4b-2e19033cd0b0 | note | CIBSE C5.6.0 Sensors/Detectors
115d2038-327a-5eff-916a-33e28f18a54d | note | AS1670.1-2018
e24ce614-a9ad-568d-b1ce-4b4c16fabd49 | note | Are Detectors activated when tested?
43451d0a-9643-52ef-852f-34febf824048 | note | Do indicators function correctly on Detectors and FDCI?
4b548046-3b30-5afc-9433-fe4d548f1939 | button | Has "GMF-COMRPT-001 Fire Detection Zone Commissioning" been completed? | Yes, No
5d01355c-575c-5626-8ce4-c914e90ff5f4 | note | Attach relevant photos and a copy of GMF-COMRPT-001 below:
e82a1ca5-493b-422e-b6af-b606b65df4c9 | checkpoint | 2. CONDUCT 100% TESTING OF SMOKE AND THERMALS
c2f6497f-0320-5121-8e53-3d65209f75e1 | note | CIBSE C5.2 Dry Fire Commissioning – Automatic Controls
0dac7939-3f78-58cd-aec7-7ec4654cbec6 | note | CIBSE C5.2.9 Alarm Functions
f6e516e6-cf93-582c-9d56-84d0557b4db3 | note | CIBSE C5.6.0 Sensors/Detectors
0ecc71b6-fa82-5ede-b68a-7cdabc1ddd58 | note | AS1670.1-2018: Ensure Detectors are activated when tested and correctly indicates on the detectors and at the FDCI
ab222eb2-a10c-534a-ae1b-fd223a6b19f1 | note | Are Detectors activated when tested?
af09c703-3810-5eb3-b92b-31e19da694d7 | note | Have all dust covers have been removed from detectors?
7f9d61e9-0477-590d-b1ec-53bb11ea8557 | note | Do indicators function correctly on Detectors and FDCI?
9be3a74a-16bb-5cc9-88fc-9d05528e8f8e | button | Has "GMF-COMRPT-002 Fire Detection and Alarms (Smokes, Thermals, Duct Probes)" been completed? | Yes, No
d3566ce9-ad4e-52ee-bf21-253d8256c0aa | note | Attach relevant photos and a copy of GMF-COMRPT-002 below:
05a0b61d-b940-4760-b607-ba33c0cd8b28 | checkpoint | 3. CONDUCT 100% TESTING OF MCPS
ffe206e5-8e0f-502b-934f-7da6f23ad99a | note | C5.2 Dry Fire Commissioning – Automatic Controls
cf33cb29-3394-5dbb-bf0c-887d0e923636 | note | C5.2.9 Alarm Functions
b55995e1-dae7-5b76-abc0-371e7441dd0b | note | C5.10.0 Manual Call Points
d5888afc-1d03-587a-bfb7-a69dd6664ef3 | note | AS1670.1-2018
a7fb6a26-03e7-5fc6-8cea-4c3538f977ab | note | Have you checked:
f23ea05c-02a5-5ceb-9197-5e18406ecde2 | note | The correct operation of each manual call point; and
7517a87d-2553-5fca-af4e-e3ca1b508b2c | note | That the activation of manual call points on the same circuit as other actuating devices does not cause existing detector alarm indications to be extinguished; and
94cc7f41-26a8-5d3e-a244-03a58864fbfc | note | That manual call points are not subjected to alarm dependency; and
d94be4c6-1b4e-57d7-806b-7c4d55c42b3e | button | Has "GMF-COMRPT-003 Manual Call Points" been completed? | Yes, No
d2cdce9f-3de7-548b-9afb-2f55f6d25ab3 | note | Attach relevant photos and a copy of GMF-COMRPT-003 below:
73d94d7d-8099-44f2-8a38-3b5eb1675fc3 | checkpoint | 4. CONDUCT 100% TESTING OF DOOR DEVICES
387e9cb7-c8d7-5992-ad85-1cac4bbed8e1 | note | C5.2 Dry Fire Commissioning – Automatic Controls
d69f7b5f-0af8-54b5-b90d-9f4acfe6dd01 | note | C5.2.9 Alarm Functions
00773f5d-8afd-56f6-a291-b74bf6b7279b | note | C5.8.0 Modules Input/Output
9660c558-b99f-5c24-b83c-62076b43c5cf | note | AS1670.1-2018
2f6773e8-4e5d-54c7-bfe1-f33ed1244ec5 | note | Has the operation of each device/door release been checked after install?
e1e7b305-7d39-54fe-897a-cf02aae67be5 | button | Has "GMF-COMRPT-004 M.D.H / Auto Door Commissioning" been completed? | Yes, No
6a4b409e-e36b-5e4f-bffc-6249388a1d8b | note | Attach relevant photos and a copy of GMF-COMRPT-004 below:
bd783e18-0695-4032-ba7f-0cfc54b1c6d0 | checkpoint | 5. CONDUCT 100% TESTING SPEAKERS AND ZONES
34eaaed5-defa-5cc0-8982-c2431d77083f | note | C5.2 Dry Fire Commissioning – Automatic Controls
0391570b-0833-5296-a9cf-6f0b4f2e0a37 | note | C5.2.9 Alarm Functions
a8ac59df-ee9c-5d40-8224-9163b347bab5 | note | AS1670.4-2018
127d1f43-c277-5bdb-adc0-92e39369d656 | note | Have the audible signals, visual and tactile signals been checked? (automatic operation)
8acf6dcd-b057-56f0-a3ca-fa422d58933d | button | Has "GMF-COMRPT-006 Emergency Warning Commissioning" been completed? | Yes, No
070221f8-ed5d-561b-b859-48600bf09d83 | note | Attach relevant photos and a copy of GMF-COMRPT-006 below:
2b7c9768-4465-40f0-8532-1eddb4dfc681 | checkpoint | 6. CONDUCT 100% TESTING WARDEN INTERCOM PHONES
e22acb3e-9220-50db-86a2-dc4f552da431 | note | C5.2 Dry Fire Commissioning – Automatic Controls
ba7f1a92-c577-5cbf-89d5-2c64dd3addb4 | note | C6.2.8 Warden Intercom Phones
6c742f4a-3656-5b53-9fdb-14becec1b266 | note | AS1670.4-2018
1fa23a12-d52a-5d99-8c58-7fabe4a885aa | note | The WIP audible call signal shall have a SPL of not less than 80 dB(A) when measured at a distance of 1 m from the WIP.
12d61d9c-cf71-5853-a593-0bc40e90e713 | note | The SPL of the WIP handset audible call signal shall also be met when the WIP handset is mounted within a security enclosure.
a34afad0-7be4-5d59-9d2d-b3df74952800 | button | Has "GMF-COMRPT-007 Warden Intercom Point" been completed? | Yes, No
78c89fc5-64b0-5ebc-bd5a-e3629fb832b7 | note | Attach relevant photos and a copy of GMF-COMRPT-007 below:
3838d421-3789-45ad-be46-de3ef7d15734 | checkpoint | 7. CONDUCT 100% TESTING CASCADE AND EWIS ZONING
a198e95a-e8ab-58e0-9c8a-75440bcf9429 | note | C5.2 Dry Fire Commissioning – Automatic Controls
4261b4d6-bd26-53b3-a7a0-a6f5c4eb0f44 | note | C6.2.5 Cascade Sequence
aafed843-6ad1-5bf9-8520-8bdb0a722c7d | note | AS1670.4-2018
18d36569-4a00-5e1e-a541-43f9c56b642d | note | Have the audible signals, visual and tactile signals been checked? (automatic operation)
9b5e68bd-b5ca-5f50-b7bd-d2c3f0fed70a | button | Has "GMF-COMRPT-005 Emergency Warning Cascade and Matrix" been completed? | Yes, No
f21cc58d-f2ba-5a43-b291-18d5ffc58357 | note | Attach relevant photos and a copy of GMF-COMRPT-005 below:
229920cb-f2fd-4d26-b511-2227ec1b59bd | checkpoint | 8. CONDUCT 100% SPEECH INTELLIGABILITY TESTING
5b8b60a6-ca3e-5da8-8c8f-d76cdac81ab6 | note | C5.2 Dry Fire Commissioning – Automatic Controls
0b3a763f-c427-5136-a088-b1c4ceb54a93 | note | C6.2.5 Cascade Sequence
27e6508d-b915-5a76-b38b-d7d20e89eef3 | note | AS1670.4-2018
bb685c01-095b-59da-98c9-7c3e0e1720d0 | note | Have the audible signals, visual and tactile signals been checked? (automatic operation)
1b14c777-115f-56ab-90ee-8146a541a93e | button | Has "GMF-COMRPT-008 Speech Intellegability Readings" been completed? | Yes, No
004f1592-a5ed-567f-85a5-e87a89a469a7 | note | Attach relevant photos and a copy of GMF-COMRPT-008 below:
051ed8d4-afe3-4b1c-8432-2cf906669505 | checkpoint-no-value | GM Fire Sign Off
f3fdb097-e0ec-4225-91c3-15a98123a2da | signoff | GM Fire Sign Off
645387f1-2fba-44b6-a734-87b0bf49f256 | checkpoint-no-value | Principal Contractor Sign Off
fcfedeb1-f339-4083-aa2e-63b87fec525d | signoff | Principal Contractor Sign Off
120ad49f-ec61-4619-ba6b-614a89b99107 | checkpoint-no-value | Consultant Sign Off
ca476f22-73db-4081-9521-4861bc57ed2f | signoff | Consultant Sign Off
316c2467-2b0f-4ba3-8ca9-59cdb136c87b | checklist | ITPS-201 Interface Commissioning | itp | ITPS-201 Interface Commissioning
b557499a-50e7-4cfe-8045-44d9ee38ff05 | section | Details
67e29964-dfe1-4c5a-a009-f6e3506ececb | checkpoint | 1. CONDUCT FIRE MATRIX TESTING
47a73b1b-26fc-5fab-90f4-7d820ecfbc35 | note | CIBSE C6.2.4 Fire Matrix
1955edb7-0088-5000-ad59-9457c1a0d4bb | note | AS1670.1-2018
ebd0e7f8-296e-5171-8f0c-05263df3db57 | note | The ‘end-to-end’ test should include the activation of associated detection devices to confirm that all required functions operate correctly in accordance with the system interface matrix.
ef8aa7db-0bd3-5c64-8160-110cfa2df711 | button | Has "GMF-COMRPT-009 Systems Interface Matrix" been completed? | Yes, No
8e5d2910-1b85-5a8d-a3f2-0b4efc2edcd3 | note | Attach a copy of GMF-COMRPT-009 below:
d109f3ac-96e9-45ba-91a6-00853c1aa9dd | checkpoint | 2. CONDUCT FIRE FAN CONTROL PANEL AND BRIGADE INTERFACE TESTING
6c068bb3-a3bd-5157-bb49-ae415ebedf89 | note | CIBSE C6.6.0 Brigade Interface – FFCP
27449a38-b3e3-5364-b8aa-fb6c0207c1c8 | note | AS1670.1-2018 Appendix A
77ea653c-b0c9-5d34-83c0-a002067813e8 | note | Check Fan Control Operation as per Matrix.
d5bc484d-7806-59a9-8863-e7ccab41d1f1 | button | Has "GMF-COMRPT-010 Fan Control Matrix Testing" been completed? | Yes, No
055c94be-07b2-529a-b8b2-e915183feb25 | button | Has "GMF-COMRPT-011 Fan Control Overrride Controls" been completed? | Yes, No
8e946845-06c0-5adb-a4fc-295850474689 | note | Attach a copy of GMF-COMRPT-010 and GMF-COMRPT-011 below:
85cff2a9-9c2d-41b9-b40a-e6779197caa4 | checkpoint | 3. SPRINKLER INTERFACES FITTED OFF
8e7c2249-ffe4-55e2-841c-51da29be6e1a | note | CIBSE C5.8.0 Modules Input/Output
40c13817-91f2-5b6f-ae27-b545bb0c1586 | note | CIBSE C5.2.9 Alarm Functions
ebab7849-cdd2-5e1c-ab6b-96f4cd51da45 | note | AS1670.1-2015
5e1c34b7-2d05-5183-ad37-d3ea5205c620 | note | Prior to any interface testing, have you checked all systems listed in the system interface schedule are complete and operable?
d6c58edb-3c3a-5634-be51-690863949c6f | note | Have you checked all systems interfaces to the FDAS?
78f18995-6a29-5372-a767-c1bf4a1a376a | note | Has "GMF-COMRPT-020 Sprinkler Zone Commissioning" been completed?
e85914e6-6960-5a1c-b10b-23986d739642 | button | Has "GMF-COMRPT-021 Pump and Tank Indication" been completed? | Yes, No
0f1362c6-8e59-5175-b04b-d53712a00a9c | note | Attach a copy of GMF-COMRPT-020 and GMF-COMRPT-021 below:
4df281d3-3483-434e-815a-47846e6e8773 | checkpoint-no-value | GM Fire Sign Off
ef8da32b-681a-45d5-ad91-1b56e33faf53 | signoff | GM Fire Sign Off
af453e9d-71e9-4ad0-90a7-8e89f3c1775d | checkpoint-no-value | Principal Contractor Sign Off
70694b2e-54be-4b75-b91f-8f42f2b7576f | signoff | Principal Contractor Sign Off
b8a7575a-d203-43bf-8ac7-59051572a8fd | checkpoint-no-value | Consultant Sign Off
95d48c46-6339-42f6-a0c3-e208e6186c24 | signoff | Consultant Sign Off
65864d34-eb40-4695-b8ee-6f760ceaab91 | checklist | ITPS-202 ASDS Commissioning |  | ITPS-202 ASDS Commissioning
e7ae627d-a6ec-47bc-92ab-baaf0d812d3a | section | Details
4ff7d7bd-01c3-435e-82b3-1db5bb4ba82d | checkpoint | 1. VISUAL INSPECTION
e27b5bdf-f2d0-5574-8758-12102648731f | note | CIBSE C5.6.0 Sensors/Detectors
bc84c359-97d4-5a20-9266-4d434c554959 | note | AS1670.1-2018 Appendix A
2bbf3d91-e21b-5d60-8221-7785d8b3cef6 | button | Have you visually inspected every sampling point to ensure it is not obstructed? | Yes, No
0c2c877e-06fe-5a97-b208-53fb6713b9b1 | note | Add Photo
c927ce69-b9bd-404e-b27d-f4fe4ece2042 | checkpoint | 2. ALARM TESTING AND TRANSPORT TIMES
fc042619-a54d-51f8-a88a-dc3f98977ffc | note | CIBSE C5.6.0 Sensors/Detectors
1bbf3848-caeb-5e69-a2fc-d6c66ab0705b | note | AS1670.1-2018 Appendix A
ce46227e-2653-54fe-963d-86f5685c6eb3 | note | CHECK AND RECORD
20ffb578-c95f-5e40-ad8c-9b4627011131 | textbox | The response of all capillary sampling points using a test medium placed at each sampling point:
5c0959f5-9db1-5f49-a412-1a6709bc83a8 | textbox | Measure and record transport time (TT) from the EACH sampling point:
5f3bbb6d-f08a-52ad-8fc7-d50fb9397254 | button | Has "GMF-COMRPT-012-ASD Commissioning" been completed? | Yes, No
d6c88fe6-ea21-5ed7-b735-e47b3356706d | note | Attach a copy of GMF-COMRPT-012 below:
f3ddc8e1-222e-47a8-a848-e0a583e2a2be | checkpoint | 3. OPERATION - ALARM, FAULT AND ISOLATE
20e29040-dd2e-5d30-b203-58de9f6f789d | note | CIBSE C5.2.9 Alarm Functions
51044bed-13a4-51d4-af19-7d1e9f410e8a | note | AS1670.1-2018 Appendix A
2cba15ac-a5fa-5bd4-8392-dee413518d38 | note | Have you checked:
331f584e-f597-5faf-9c9e-c9a88e0791f0 | note | The operation of remote indication of alarm and fault signalst; and
05f7d211-3502-5753-80c4-1dd456fdf587 | note | The operation of airflow failure indicators; and
ab2307b9-86d5-5a90-a108-3b9b2111f546 | note | The operation of the system failure indicators; and
263b667b-f033-57fc-b6a0-8cd4eb35fb25 | note | The isolate and reset functions; and
276b2869-0399-5112-83df-34ac9ba41b3c | button | The fault and alarm test facilities (where provided)? | Yes, No
7559a2b4-ccb9-406d-939b-bfb390f41ed4 | checkpoint | 4. ASD MATRIX (If Applicable) - Including Thershold Testing
5468d8dc-4b2f-5fbe-9f1c-41b05b860590 | note | CIBSE C5.2.9 Alarm Functions
691caf87-4278-50b6-8098-89063f941093 | note | AS1670.1-2018 Appendix A
aa93136f-202d-5d38-84ba-6bf74247df15 | button | Has "GMF-COMRPT-013 Double Knock Testing" been completed? | Yes, No
28e499dd-226f-5e74-99fe-4231a348152a | note | Attach a copy of GMF-COMRPT-013 below:
736c92bf-0c27-4705-89be-7d572d704e88 | checkpoint-no-value | GM Fire Sign Off
f815614b-5c94-4490-83a6-513f92f37fc6 | signoff | GM Fire Sign Off
84f77113-c506-4288-95e5-557e80928b46 | checkpoint-no-value | Principal Contractor Sign Off
496dfdcb-fc00-463c-ac04-4dffaccb76af | signoff | Principal Contractor Sign Off
72ad022e-b3b6-4ed6-8a36-e547f25d57e5 | checkpoint-no-value | Consultant Sign Off
5f4083a6-70e7-461e-bf84-e0eeaf928153 | signoff | Consultant Sign Off
965fd8e6-fea0-4198-b1ee-6c4561d0baf1 | checklist | ITPS-203 Pipework Pressure Testing |  | ITPS-203 Pipework Pressure Testing
9baa397e-2362-495b-acff-bf1a2e8717a6 | section | Details
7c8b9715-b524-450f-81a5-88ce53b255ee | checkpoint | 1. SCHEDULED TEST IS APPROVED - CONFIRM
f1109310-2009-5991-a11b-e23d5a12024b | note | CIBSE W5.5 Pre - Commissioning
4376bddd-258a-58a6-921e-1cf01dab149c | note | Have you received Approval for test time and location?
11e3c1c7-3a13-5890-bd91-15dbbecf7a57 | button | Has the site been notified? | Yes, No
534aac09-9795-56c0-a1e4-e169a82c3a81 | note | Add Photo
8c7aab16-e527-4b5b-8c15-6c1ceca60aba | checkpoint | 2. EXCLUSION ZONE - CHECK
05cc8393-9cf2-5645-8ced-e173abcb92bd | note | CIBSE W5.6 System Checks
c7e5609c-1757-5b33-aa45-0e01ec505c59 | note | Has an Exclusion zone been set-up?
20a12f78-95f6-53f3-88a3-b8e12d4404d0 | note | Have you erected appropriate barriers and signage?
d82211f0-bb03-51de-a55e-95e5af68ea0d | button | Have all workers/occupants been notified and have they exited the area? | Yes, No
f4939b31-94bd-548c-bcf1-16dd5936a75d | note | Add Photo
37b77778-7b4e-4a7c-80c9-e1481d7356b7 | checkpoint | 3. VISUAL INSPECTION - CHECK
1982a907-5b28-5c2c-b46a-7138d78af973 | note | CIBSE W5.3 Check before Filling
c949abe9-2d6d-57d1-9d0a-90c3ed2bbe3b | textbox | Drawing Reference and Revision number:
7803ad65-0bd7-5a76-bdc3-7b451e86dd7b | note | Is Installation complete?
3a7adaf6-52a9-51ff-97da-ba195de3163d | note | Have End Caps been fitted with lockable ball valves? (BLANK END CAPS MUST NOT BE USED)
3f3853c8-f224-522c-9727-18f766badb21 | button | Are all outlets sealed? | Yes, No
2ad204c6-5991-5e7e-92a3-c85afb5f1122 | note | Add Photo
b86acce2-d450-403e-a38f-22296f21d4cd | checkpoint | 4. FIT TEST PUMP AND CALIBRATED GAUGE - INSTALL
e7fa6189-a218-5f3f-bc03-040a8c9299bf | note | CIBSE W5.3 Check before Filling
a329ba5e-7139-5f91-8f70-a1528252a0d9 | note | AS2118.1-2017
486616f8-2954-5c07-b69f-c86eda4e1e87 | note | Is the Pump installed in a safe location?
df2235ee-9f2c-5f0b-b474-03632eccf042 | note | Is the Callibrated gauge in visible location, and accessible to photograph?
69992629-da5d-5f74-bfe5-f64abd0396d8 | button | Have the Pump and Callibrated gauge been tested? | Yes, No
f7acdf52-4a1b-53c6-8b95-e85c59b3485c | note | Add Photo
af550ed2-9313-4b08-8217-18fe93d3ac53 | checkpoint | 5. CONDUCT BREATH / LUNG TEST
2688db0d-089c-5e17-b8fa-56b7448c4778 | note | CIBSE W5.3 Check before Filling
4f2eb327-4677-5571-8004-b9a2c7d11ecb | note | AS2118.1-2017
ee89d1ef-d7e2-5236-aaa6-907730b31aa0 | note | Perform Lung/Breath test where possible;
371c8344-b389-599c-b284-605dc0f72cac | button | Is the system sealed? | Yes, No
9828a985-61fb-5cbc-a13e-8b40306c8269 | note | Add Photo
fc602b2d-42cd-4c0c-a95d-2770834f8595 | checkpoint | 6. FILL SYSTEM - STATIC PRESSURE ONLY (OR AIR PRESSURE)
e2796515-d659-5efe-9b81-bcc4698bb75a | note | CIBSE W5.4 System Filling and Venting
7ceeb102-ee52-532d-8661-bf33ed17686c | note | Prime system to towns main pressure OR 300kPa (depending on test);
57c3ca9c-1b11-51f2-a3a8-5138996141d7 | button | Are there any leaks in the test area? | Yes, No
3f3b9424-1ad0-52cd-9efb-341c10e14128 | note | Add Photo
c08df24a-bde0-4304-8935-3fcc88f942c0 | checkpoint | 7. START PRESSURE TEST - CHECK
76043dae-f327-5547-b03e-0982037017fa | note | CIBSE W5.4.1 Pressure Testing
154f3b53-b0a3-5688-8ecf-665e0f0e76c3 | note | Increased pressure to 600kpa start pressure;
29762f82-8e54-5744-befc-e11d3c3ed1cd | button | Are there any leaks in the test area? | Yes, No
8ed93269-9f06-5bf1-ae2c-53d1039870b4 | note | Add Photo
f97f80c8-e880-4bf3-ac38-fdb75784a2d6 | checkpoint | 8. INCREASE PRESSURE
18d83e97-23f8-52bd-9abf-fc1b14293ab6 | note | CIBSE W5.4.1 Pressure Testing
96b56ed9-0cc7-59e4-bb89-0539dad58a8d | note | Progressively increase pressure in 100kPa incraments; and
912b4d72-6577-53da-9c09-295f5e6495c6 | note | Inpect test area for leaks at each increase; and
15b00e43-b5ca-519c-b02c-d6306d2b4f44 | note | Repeat until pressure reaches 1600kPa;
107ab46c-6124-57d6-8e58-e89c0f61e6f9 | button | Were there any leaks in the test area? | Yes, No
9da61df0-3f84-5eec-a4ce-bb7f8ef0c306 | note | Add Photo
ba845480-d310-4eba-ba4b-3398da09ec5e | checkpoint | 9. HOLD PRESSURE
64a2de0b-4daa-5588-a445-4024d673d4da | note | CIBSE W5.4.1 Pressure Testing
db03b9e0-c124-57eb-b30f-c024ed09a14b | textbox | Record Start Time and Photograph Guage:
c576d7ae-4f53-5205-8d18-56c04a1ef25a | note | Hold pressure for 120 minutes.
031748d6-f6f4-5c72-8271-a8ff1dfe1119 | button | Was there any pressure loss? | Yes, No
ad73f853-c2c1-541f-a5a3-73d7a38c7511 | textbox | Record Finish Time and Photograph Guage:
9357d6fa-2e09-544a-b81f-3c997b82d94f | note | Add Photos
3bfcba24-c87f-4281-bdca-9464f35038cd | checkpoint | 10. DE-PRESSURIZE SYSTEM
cb6f77cb-08e5-52e0-bca9-c176c6fe2313 | note | W5.4.1 Pressure Testing
707e6687-4f20-5023-b22b-abee441e8bab | note | Release test pressure from system.
95ef4d13-f678-55e6-ac9b-fd87432ad985 | note | System remains primed with towns main pressure.
f18e1e4c-bef0-507d-a849-de40fc939a36 | note | Add Photo
83ca59c5-0250-40db-a938-9fa6dba339cd | checkpoint-no-value | GM Fire Sign Off
d3ca0d1a-dd8f-4bd0-8d26-756c01f263dd | signoff | GM Fire Sign Off
9e4f03f5-4df5-497c-8834-88f87b1c6f79 | checkpoint-no-value | Principal Contractor Sign Off
cd903a4c-4d19-412f-b26e-30cf3ebc68ac | signoff | Principal Contractor Sign Off
043804a2-65b4-4fb5-b49a-6d7bd3e89a1d | checkpoint-no-value | Consultant Sign Off
74c56228-2e6d-4e60-8add-11a793d8e73b | signoff | Consultant Sign Off
0092de82-83d7-4a5f-aae2-f28f29c7c00d | checklist | ITPS-204 Electric Fire Pumpset Installation and Commissioning |  | ITPS-204 Electric Fire Pumpset Installation and Commissioning
17cc8836-0152-4bdd-a015-838ed659f046 | section | Details
8da5a7f0-459f-463c-8137-d69bd05ce7d1 | checkpoint | 1. CHECK AND CONFIRM - LOCATION
ba286382-a2da-584d-b580-4f9cd163eeea | note | CIBSE W5.2 State of the System
a96b387b-5d62-54d7-996d-0942753f9013 | note | AS2941.1-2013 – Section 11
03ea85f6-6983-5e37-9326-3494bf6298de | button | Has the Installation Pump been installed in a position that is protected from falling debris, and vehicular and mechanical damage? | Yes, No
1b7916f5-a82f-5a07-97c8-f582869d5ddf | note | Add Photo
85e2748b-6484-450a-bc03-fcdd03bb1c25 | checkpoint | 2. CHECK AND CONFIRM - CLEARANCE
35b8a1a3-5135-5825-84a1-89755a79f7dc | note | CIBSE W5.2 State of the System
b57fce3a-3f9e-5624-95e9-8f337b0889f8 | note | AS2941.1-2013 – Section 11
057ac3f1-95cf-5adb-a8d9-92f5aac18e54 | note | Is there at least 1.0m of clearance around the perimeter of the complete pump setup; and/ or
7598f1a2-0799-5418-8d2d-c21e5fba7e01 | button | for multiple pumpset installations, there is a clearance of atleast 600mm between each of the installed pumps? | Yes, No
0bbaa6e0-eef2-5d7d-8303-eb579ca017bb | note | Add Photo
22ba982c-9e68-4506-8e54-c0982bb53067 | checkpoint | 3. CHECK AND CONFIRM - ELEVATIONS
de3ca965-955a-576f-b7ca-fce6c10af965 | note | CIBSE W5.2 State of the System
016ba858-7b8b-51d0-801c-d96daeda5750 | note | AS2941.1-2013 – Section 11
28bcd133-b098-5325-b058-38a49a993037 | note | Have pumpsets been installed with the centre-line of all suction pipes at the same elevation; and/ or
c4be27df-c331-54ef-b80d-bd17e185a74e | note | if the pumps have been installed at different elevations, the elevated pump is installed on a properly constructed mezzanine floor; and
3570f8c5-2615-588d-8bec-d104db00cd0b | button | with head clearance of minimum 2.1 m to the underside on both levels? | Yes, No
847a706e-c5a3-5ef9-9054-06500d1c78bb | note | Add Photo
5ddf52a6-340c-417d-b292-dd5283affe20 | checkpoint | 4. CHECK AND CONFIRM - PLINTH
244a65f4-ee11-53fe-bc2e-c17a83588567 | note | CIBSE W5.2 State of the System
439d69aa-8361-5a0d-af8b-e38157a3ad49 | note | CIBSE W5.6 System Checks
8840b8b9-e26c-5489-b0b9-839fbda26dd5 | note | AS2941.1-2013 – Section 11
1078cc30-b55a-5a00-ad96-ec2cc7b3f68d | note | Have pumpset baseplates been mounted on concrete plinths with a height not less than 150 mm above the floor?
37fc871e-3c5e-530a-9b51-98705aab97b1 | button | For fixing purposes, does the concrete plinth extend 150 mm past the edge of the baseplate on all four sides? | Yes, No
19cbf510-b254-5f5e-a858-639ac1341bc5 | note | Add Photo
a895b6f8-b2c6-49b5-9d0c-bf2814bbe957 | checkpoint | 5. PRECOMMISSIONING CHECKLIST - CHECK
6e8161f2-4883-5688-b354-3a6b1b75b1b9 | note | CIBSE W5.5 Pre - Commissioning
09adaff5-1c66-5abd-8e86-dec9d14e7e1b | note | CIBSE W5.4 System Filling and Venting
0ab90b32-0511-5594-ae7e-7215b9224a6f | note | AS2941.1-2013 – Section 12
fff9ed1f-17a8-5dbe-ba46-50c4fe8e7657 | note | Have you checked the coupling alignment to ensure that the unit is aligned within the manufacturer’s specified tolerance?
c38d76d0-5bb9-5272-88d4-fd9b5cd93c3b | note | Have you confirmed the direction of rotation?
af875bb4-b3fe-5968-b575-dc5ca2acc2b4 | button | Has the battery electrolyte level, and the battery leads and connections been checked? | Yes, No
ca0fa529-0405-5b02-a87f-e929a0612832 | note | Add Photo
a77b6ded-0acd-4460-a080-64d6d496b7c5 | checkpoint | 6. PRECOMMISSIONING CHECKLIST - ENSURE
1cd60801-a752-51cd-9c07-313ee2063395 | note | CIBSE W5.5 Pre - Commissioning
b69d40cc-81bb-5e4b-a010-6c888a33e0da | note | CIBSE W5.4 System Filling and Venting
3f87e51f-cb02-5cdd-9782-a23aff3fe2cf | note | Is the delivery from the pump under test the only supply to the measuring device?
66d1f6f1-6b94-5411-bae3-f99dea5fdc00 | note | Does all flow from the pump passes through the device?
512cc766-a326-5896-b501-83d375728b79 | note | Is the pump primed and lines are clear; and
ceac0534-fe4a-532f-9fab-45fd0b66e9fd | note | valves are correctly set (open, closed or adjusted to required pressure); and
bc8c0f7f-f8a6-5ff8-ad5e-8d24823e0f63 | button | is water available? | Yes, No
0ad1936a-fb3a-5899-b816-4c00e9e530d3 | note | Add Photo
72356353-2043-40cb-ba83-011d6bba33a6 | checkpoint | 7. PRECOMMISSIONING CHECKLIST - ISOLATE
c2268621-5349-56cc-9d30-3eec1e24f8b6 | note | CIBSE W5.3 Check before Filling
6aefa105-5c31-5267-9983-c9b8066fad58 | note | CIBSE W5.4 System Filling and Venting
d097e3f8-2f65-5299-a7a8-c4b7ee640afb | note | AS2941.1-2013 – Section 12
25321773-62d5-54d3-ab04-484ce686b370 | button | Have you isolated all other water supplies to the fire protection systems, such as the automatic pressure maintenance pump and any other compression-ignition engine driven pumps in the system? | Yes, No
7f5a70ac-21f1-5305-8403-f4a3c6241c02 | note | Add Photo
cf3d14b6-8b40-4641-8d40-7c51eb43ad6f | checkpoint | 8. PRECOMMISSIONING CHECKLIST - REPORT
4a2734c2-3e01-591f-9334-157327cfc16a | note | CIBSE W5.5 Pre - Commissioning
47524082-2e61-57f9-ac35-c84e08351e0a | note | AS2941.1-2013 – Section 12
142c62c3-b08b-51d1-82c7-57e08080da54 | textbox | Pump plate details:
80fbab18-c48a-563a-a82e-1fc1713be00a | note | Add Photo
ee5e9fbb-1096-4aff-a9c3-ce36f16723f4 | checkpoint | 9. COMMISSIONING CHECKLIST - RECORD
79242b28-7f3c-558b-aa49-15e6754e2055 | note | CIBSE W7.10 Commissioning Certification
94390342-e0f4-5032-890e-a913fda20229 | note | CIBSE W7.2 Flow Rate Measurement Tolerances
7215edf4-b212-50d1-9ffb-7029417e6076 | note | AS2941.1-2013 – Section 12
cede6397-98c8-5c7f-9f82-37ac4928b24f | textbox | What is the pressure in the system at which the pump starts automatically?
7475b17d-e752-5064-b5c1-a33076b03577 | textbox | Pump shutoff pressure:
4a68da98-34b5-5796-97bf-7b777b0946bf | textbox | Motor shut off pressure:
c2dec665-9aae-5cae-9376-b64610783a15 | textbox | Delivery pressure at maximum flow:
057eb7c4-c2c1-5fb9-afd8-7f1d6841418e | note | Add Photo
394a339a-f711-47bc-8a11-10879d99e99e | checkpoint | 10. COMMISSIONING CHECKLIST - RECORD
a14e51ae-a82b-522c-b5c7-e2ba17e29b6e | note | CIBSE W7.10 Commissioning Certification
c0d781b6-f99a-5830-8553-577429ebf067 | note | CIBSE W7.5 Preliminary Flow Rate Check
72276dbb-43df-56ed-8373-7e9d6a3a8a01 | note | AS2941.1-2013 – Section 12
50abb808-6275-5ee9-9c33-552c1bedc740 | textbox | Record the pressure on discharge gauge and motor current at three other flow rates between shutoff and maximum flow, one of which should be at the duty flow rate:
f98b6357-d826-5c22-8a13-9a1a647d79bc | note | Add Photo
1f5e1081-8e96-4c51-95f8-82d99a440871 | checkpoint | 11. COMMISSIONING CHECKLIST - RUN AND RECORD
03d59834-fe48-51f3-958e-c7082452d78f | note | CIBSE W7.10 Commissioning Certification
aa4a07b6-49a2-5c79-9482-63358d274a6d | note | CIBSE W5.7 Static Completion Records
8d3505a9-b796-5aab-be3b-88636b40ac06 | note | AS2941.1-2013 – Section 12
88806aa3-b6a2-5dad-aaa0-d880ffe7342c | note | DURING OPERATION:
b7c0f700-852b-547e-ae4f-67a7dde69b42 | note | Have you checked the temperature of the bearings and stuffing box leakage and noted any abnormality?
e9e77a38-c950-5acb-871e-ec0019b791f2 | note | Have you checked that all alarms and indicators, both visual and aural, have been activated; and
f3a5d974-eae8-5b95-b49a-9059f31d2aac | button | Alarms and indicators, both visual and aural, revert to normal stand-by status when pump is stopped? | Yes, No
df77e145-2880-5f39-9c9c-ae6c0a3fd52b | note | Add Photo
dfb1aa8a-a486-4b17-a50b-ee11da1915b8 | checkpoint | 12. COMMISSIONING CHECKLIST - RUN AND REPORT
dbda3259-9876-5dc3-b5e3-49c8c2082d05 | note | CIBSE W7.10 Commissioning Certification
04c25e2c-ac41-5178-bf01-442e3464530e | note | AS2941.1-2013 – Section 12
2d5ac19a-1b7f-5c57-8787-316f5da00201 | note | RUN AND REPORT:
5922c553-447d-5194-bd10-ad5ea400e794 | note | Is the electric pumpset, together with its associated control gear and ancillary equipment, functioning correctly?
5b8951c3-7164-5277-97c9-d2934492982c | button | Does the pumpset satisfy the intended performance conditions? | Yes, No
e5635721-c5f7-5f7d-b770-10fb71f3f042 | button | Are there any operational abnormalities? If Yes, detail below. | Yes, No
dab2a3c4-2832-576b-8d06-055fe40cbaad | note | Add Photo
2a1352ee-d174-441c-8bdc-00c46e64732c | checkpoint-no-value | GM Fire Sign Off
8c96b99f-c093-4d0a-b230-dd0367cf2de2 | signoff | GM Fire Sign Off
a28193fb-ac45-405a-8a61-8cb08d19859e | checkpoint-no-value | Principal Contractor Sign Off
49a25cc6-5a80-49f8-a939-6e5a3e6d4170 | signoff | Principal Contractor Sign Off
34d078d2-bd9e-40cd-a593-3b867580dd8b | checkpoint-no-value | Consultant Sign Off
dc263e50-b386-4858-97b3-fa0d296db303 | signoff | Consultant Sign Off
f9b82975-7dd8-4453-b6c7-fee428244c82 | checklist | ITPS-205 Diesel Fire Pumpset Installation and Commissioning |  | ITPS-205 Diesel Fire Pumpset Installation and Commissioning
6e33cc19-d2d6-4ada-8903-b2a30c0e7046 | section | Details
b0fb7c1f-be35-49df-80ba-3780f2f40d70 | checkpoint | 1. LOCATION
56fd1c14-9939-5dee-8947-716bd7f3bfa2 | note | CIBSE W5.2 State of the System
4a3e91f6-f645-59c9-b38a-99fadfbb3ed7 | note | AS2941.1-2013 – Section 11
2e0e07ac-4293-59f0-af42-da67597b3222 | button | Is the Installation Pump installed in a position that is protected from falling debris, and vehicular and mechanical damage? | Yes, No
6de4cb6c-a763-5ca9-8fed-1fb6c2f4af35 | note | Add Photo
ff069525-7a2f-483f-9256-53f6c9fcf6c6 | checkpoint | 2. CLEARANCE
a0523979-0581-555e-bdcf-f64b2b48c898 | note | CIBSE W5.2 State of the System
71976a4e-8eb5-5659-a955-6f60b18a367d | note | AS2941.1-2013 – Section 11
da2ed4c4-28b5-5f61-9064-00f383f245f2 | note | Is there at least 1.0m of clearance around the perimeter of the complete pump setup; and/ or
f2e11a65-21f6-5823-98cd-cee8c64291cf | button | for multiple pumpset installations, there is a clearance of atleast 600mm between each of the installed pumps? | Yes, No
bb2e060a-4e9a-5760-8c35-c1ae630df0ed | note | Add Photo
14819233-af6e-46b8-9cff-2810fad16024 | checkpoint | 3. ELEVATIONS
bea43390-c692-518e-be3a-3f07aaad02d2 | note | CIBSE W5.2 State of the System
89011d48-653d-5cd0-a4a7-b61bb99bb9a3 | note | AS2941.1-2013 – Section 11
ccf0329b-98ff-52f9-9844-9c72c415dcd0 | note | Have pumpsets been installed with the centre-line of all suction pipes at the same elevation; and/ or
b4b7037a-8095-5e87-9e2e-ab8a28c2bd86 | note | if the pumps have been installed at different elevations, the elevated pump is installed on a properly constructed mezzanine floor; and
bb28b034-50e8-5549-a3cf-b5f36a2938c1 | button | with head clearance of minimum 2.1 m to the underside on both levels? | Yes, No
b6d57b0b-40a4-5b9a-b33e-bb496326f27e | note | Add Photo
1edaa5e8-8294-4e7b-bf98-c05e55705476 | checkpoint | 4. PLINTH
fb45e47e-6f82-5e5e-9954-15d13a592a9e | note | CIBSE W5.2 State of the System
aff72cce-d5f7-5760-be59-cee01f7c8de4 | note | AS2941.1-2013 – Section 11
f86d3156-0628-5b01-a791-5bcf2bda1258 | note | Have pumpset baseplates been mounted on concrete plinths with a height not less than 150 mm above the floor?
01845580-b2b7-53f4-8cd9-f95d700ad0aa | button | For fixing purposes, does the concrete plinth extend 150 mm past the edge of the baseplate on all four sides? | Yes, No
fed88508-a23d-5e5a-bf94-bbf669041d17 | note | Add Photo
e5cd19f8-9626-4976-88ac-00605c81c986 | checkpoint | 5. PRECOMMISSIONING CHECKLIST - CHECK
032e5ef5-c14b-52a2-9cc1-8bdcf6915649 | note | CIBSE W5.5 Pre - Commissioning
0184340d-fc38-558f-9efb-2634d2531358 | note | CIBSE W5.6 System Checks
22119313-fa11-5ef9-a9b4-b5866b3664ce | note | AS2941.1-2013 – Section 12
56f166b6-6796-53b1-814a-3f77b0ff7825 | note | Have you checked;
2d6cdba2-a84d-5347-9520-fd3053083765 | note | The cooling supply system; and
b56a7a8b-fc50-56b2-b40b-ef0b8929ea09 | note | Engine fuel supply; and
8a00c3ce-4156-5788-b3b6-5851c5955fb5 | note | The coupling alignment to ensure that the unit is aligned within the manufacturer’s specified tolerance; and
490e29a9-2ae2-5c4b-a07c-9bc9768c2034 | note | The direction of rotation; and
36f6b5f4-d522-5bc7-8ac2-3f795556d90c | note | That the engine lubricating oil is at the correct level; and
0fb6170b-2437-554a-9f02-095fe734bb14 | note | The battery electrolyte level and the battery leads and connections; and
eaa2e120-3072-53fe-b418-c091057c4e1f | button | That the exhaust system is intact? | Yes, No
1c70b14d-a4c3-5267-8646-35de9844485e | note | Add Photo
efb1f151-206a-48f1-b7ae-66ddfbc16483 | checkpoint | 6. PRECOMMISSIONING CHECKLIST - ENSURE
00545612-42eb-5e3d-9818-fe4a5b3b8e8d | note | CIBSE W5.5 Pre - Commissioning
d00c4e4e-a3ea-51fe-b3b9-c591fe8ee4b0 | note | CIBSE W5.4 System Filling and Venting
2e46f5d2-d898-55e6-a50f-519cc91c0b2e | note | AS2941.1-2013 – Section 12
88ffbd4c-ef73-5b78-bcd3-0fbb36128d6d | note | Is the pump primed and lines are clear; and
10f20c09-18d1-5e2d-b916-32e82e78a79c | note | valves are correctly set (open, closed or adjusted to required pressure); and
b7dacdfa-cddf-54f2-8790-0cc8c5b6a89b | button | is water available? | Yes, No
0303915a-dc3f-5c8c-9503-ef8f6f2b589e | note | Add Photo
174fa2a3-fc3d-433f-b28a-cf9ee1acfeb0 | checkpoint | 7. PRECOMMISSIONING CHECKLIST - ISOLATE
92f8babd-6179-53cc-b01b-c2ee8a11e749 | note | CIBSE W5.3 Check before Filling
769525ae-9639-5a68-9d5f-eba19b341e7f | note | CIBSE W5.6.2 Mechanical Checks: Automatic Control Valves
f20cf215-55a5-5c66-a10e-36f99f893852 | note | AS2941.1-2013 – Section 12
2ca6b603-7f6b-522f-834f-25243f5d01ed | button | Have you isolated all other water supplies to the fire protection systems, such as the automatic pressure maintenance pump and any other compression-ignition engine driven pumps in the system? | Yes, No
5a5790d9-64fb-57fe-aa7b-71fb20fc1977 | note | Add Photo
216f4e18-ffc9-48c5-9b0c-01aad970e5ff | checkpoint | 8. PRECOMMISSIONING CHECKLIST - REPORT
21cce9c1-ba32-576e-bce2-a370f512878c | note | CIBSE W5.5 Pre - Commissioning
a06a7b4a-2b3b-507f-95f6-4c5895c147fa | note | AS2941.1-2013 – Section 12
f0af2b85-8563-5f07-a920-6f088bbb3206 | textbox | Pump plate details:
b12c201c-c65e-511a-9294-86b5fe169f67 | note | Add Photo
d3041934-b3dd-4674-923d-63811bfbddf9 | checkpoint | 9. COMMISSIONING CHECKLIST - RECORD
b35b217f-20ac-521c-a491-123642fcf8af | note | CIBSE W7.10 Commissioning Certification
713a419d-7282-5a5e-8c64-6092ff75e9cc | note | CIBSE W7.2 W5.7 Static Completion Records
974b948a-f657-5275-a358-c82850bcead1 | note | AS2941.1-2013 – Section 12
abcdd0b7-b952-5c7e-8893-42b2eced50c6 | textbox | What is the pressure in the system at which the pump starts automatically?
94af3c0a-8708-5b43-8833-9805959f4a32 | textbox | Engine oil pressure:
b326b53b-05f3-5fbe-b082-5b7818ff2bc2 | textbox | Pump shutoff pressure:
b9c3bc80-e23b-5227-89a7-586c7dd2dafd | note | Is the Coolant flow correct; and
b484eb27-b549-58ef-aacb-3fc8063c5832 | button | Are the fan belts rotating and intact? | Yes, No
ed88122c-f563-5215-89ed-e110c1360f76 | note | Add Photo
d0fcf2af-ac02-55d5-8a54-a3300a6cbf92 | checkpoint | 10. COMMISSIONING CHECKLIST - ISOLATE
31c9039e-77dd-5238-9a91-4847c79a893c | note | CIBSE W7.10 Commissioning Certification
458d8d43-2c2b-520e-9980-21164fd8b9b2 | note | AS2941.1-2013 – Section 12
8cf4e34b-d321-5a43-b5c9-ce59eb0d99a6 | note | ISOLATE the flow meter, partially open the test valve, and flush to remove any debris or foreign matter;
ad280eee-7938-556e-a294-80522d781047 | textbox | open any meter-isolating valves, open the test valve, and record pump delivery gauge pressure when approximately full load flow is indicated on the flow meter:
42877115-d135-5191-ad75-288f76ffe0f0 | note | Add Photo
3eae3fc5-ae3e-4adf-aa81-d9ba6ca473fd | checkpoint | 11. COMMISSIONING CHECKLIST - RUN AND RECORD
97446759-b5a5-5576-9093-f6861021d2de | note | CIBSE W7.10 Commissioning Certification
3d85685e-8286-5796-8697-65ecd24a86d4 | note | CIBSE W5.7 Static Completion Records
eb2c9a60-f932-53cb-a664-255069d18cef | note | AS2941.1-2013 – Section 12
dbc05f0f-7073-566a-b0fb-1fd0131a3f10 | note | RUN the pump for 30 min at maximum flow and record.
69844e77-91cb-5acc-808c-2b56e7f779a2 | textbox | Suction and delivery pressures:
da47edfc-5f2c-5915-bd79-a47f14a5524b | textbox | Engine running temperature:
375ae34d-7c98-5290-9ea3-eac2651a76d9 | textbox | Engine oil pressure (within the engine manufacturer’s limits):
89670628-cba4-5b37-b524-86d360ae5f2b | textbox | Air temperature at pumpset:
367cf7b7-2209-57d7-9d1b-84da10dee831 | note | Hold the engine shutdown mechanism closed and simulating an automatic start signal until the engine has attempted to start for five automatic starting cycles.
0ac237bc-edf1-5011-a8ea-c75c9a8d409c | button | On the sixth starting cycle, return the engine shutdown mechanism to its normal starting position. Does the engine start immediately? (Clause 9.3.6.2) | Yes, No
411457fa-1958-5ebf-9f24-dc78e2812c4e | note | Add Photo
19c72dd0-bb03-4383-bb2f-acaaf74d3a63 | checkpoint | 12. COMMISSIONING CHECKLIST - RUN AND RECORD
dbd750df-8f93-5969-a9ce-b502bcc52883 | note | CIBSE W7.5 Preliminary Flow Rate Check
71ac038b-b191-51af-bbe2-cc0c2b21eeee | note | CIBSE W7.2 Flow Rate Measurement Tolerances
4bda30ec-19f6-574d-b3df-0ba6cf4f8304 | note | AS2941.1-2013 – Section 12
592fc7b8-1697-538a-ae4a-f16b6d0adcf4 | note | RUN the pump for 30 min at maximum flow; then
ab6044af-8e8b-5280-9e57-4b3b3a961600 | textbox | Discharge pressure at three other flow rates between shut-off and maximum flow, one of which shall be at the duty flow rate:
2cc76deb-58b3-5883-a8a6-81d7cf2288fe | note | Add Photo
604a9a07-9b53-4153-98db-b8b23e751d88 | checkpoint | 13. COMMISSIONING CHECKLIST - RUN AND RECORD
7c214fb4-a751-5ebe-85ca-56fe9eec79a9 | note | CIBSE W7.10 Commissioning Certification
60ad6a83-613b-5281-9ac9-b7a1fca5d9df | note | CIBSE W5.7 Static Completion Records
d0603662-b5b7-50aa-a828-1ab88303c7d8 | note | AS2941.1-2013 – Section 12
52501375-e4c8-5d79-834b-017597e1c95d | note | DURING OPERATION:
05272895-dfa0-53ac-9f6a-102b2a63b987 | note | Have you checked the temperature of the bearings and stuffing box leakage and noted any abnormality?
971a31bf-1044-5010-ab03-77f892ad7707 | note | Have you checked that all alarms and indicators, both visual and aural, have been activated; and
42f043fb-41c3-516e-987e-4878461de6f9 | button | Alarms and indicators, both visual and aural, revert to normal stand-by status when pump is stopped? | Yes, No
df1ea77d-0dc7-52dd-8e21-a80ae1c4386d | note | Add Photo
bb95d631-b44d-4bd0-9cd6-7c67d474ac41 | checkpoint-no-value | GM Fire Sign Off
8ff1138f-398b-4a41-a128-662ab3e04516 | signoff | GM Fire Sign Off
9c845fc7-9757-4f3b-9343-be96c3637139 | checkpoint-no-value | Principal Contractor Sign Off
2beed6d6-d7c9-4f35-9133-2f6e036d11fc | signoff | Principal Contractor Sign Off
602fc202-3566-46fd-adb8-c222b5970ef9 | checkpoint-no-value | Consultant Sign Off
9e9b6c55-22f5-46fa-85f0-ea28918324a2 | signoff | Consultant Sign Off
fecfee9d-ec5d-4874-bf12-533a625a5bed | checklist | ITPS-206 Sprinkler Commissioning |  | ITPS-206 Sprinkler Commissioning
ca68a939-a378-4fb2-aeb1-48a793a95f38 | section | Details
4dd53df1-a057-4588-8e7b-b344ebd41fe6 | checkpoint | 1. CONFIRM WATER SUPPLY & PUMPS PREVIOUSLY COMMISSIONED
e575108d-76d4-539c-bb4e-4695c534e9d3 | note | CIBSE W5.2 State of the System
1f09d5ec-021a-559a-8244-8c522ac689a8 | note | AS2118.1-2017 - Section 14.9
668755d4-a914-5728-82a3-f90f6e639adf | note | Water Supply & Booster Pumps have been commissioned
01043056-df9c-55d9-8dd4-c711a1c544be | button | Are all Valves in the correct position? | Yes, No
b9b0859b-1032-4f63-ba8e-ad36a9557cf2 | checkpoint | HOLD POINT
1beee92b-3604-5814-bdb6-7c72a7b1c84d | note | There is a risk of damage to pumps if system is not ready for sprinkler commissioning . Refer ITPS-204 and ITPS-205.
c1a929ae-1708-4e87-9052-43cddb7f90a7 | signoff | GM Fire Sign Off
7b3905bc-6250-490d-a17f-e4be67a7af37 | checkpoint | 2. CONDUCT FLOW TESTING TO PROVE SYSTEM PERFORMANCE
07d4e70f-1528-5863-8b9c-3ccd9506a416 | note | CIBSE W7.5 Preliminary Flow Rate Check
fb39e813-d10d-507d-9b68-6f2679790b87 | note | AS2118.1-2017 - section 4.2.2.
e4f098db-4032-5439-8669-f85fa7b2ded4 | note | Test
4c192c3e-1e85-53c9-902b-0b57be341bb5 | note | 1) Confirm flow & pressure requirement
85c148bc-bc25-5b2a-b83c-906c5ebac8e6 | note | 2) Secure flow meter to annubar test line
bba1469f-1d98-5e06-a826-779f10d4b4ac | note | 3) Manually start booster pump 1
aae9d3c6-0a18-5278-bd5d-97a7d71def27 | note | 4) Incrementally open annubar test valve
d5b68f78-a05e-5a44-9c85-dd1f9d5ff69d | textbox | 5) Record test flow & pressure at each stage:
9ec09ea9-3cb8-5f8a-89a9-09ac2114ae16 | textbox | 6) Record pump data at each stage:
2d14351e-11e5-561a-a4ef-05be884f51b7 | note | 7) Confirm system achieves pass result
750b96bd-96ce-599d-ae00-a683bee7d7bc | note | 8) Close annubar test valve
1c983cd2-2cbe-5bba-8c19-47e6e84797e5 | note | 9) Stop pump
8fc026f1-3147-58f6-aeb7-f1a4584ad7e7 | note
98c89bb7-24af-551a-af4b-873bf5cef63f | note | Has the Sprinkler Block Plan been completed?
bbfe559a-3da3-5a10-a446-71eccc7b0c53 | button | Have you recorded this on the Pressure Gauge Schedule? | Yes, No
0779462d-8545-59c8-aab6-21ec7f543b1f | note | Add Photos
5d09f5cb-88cd-40e6-9247-7ad07bcc914f | checkpoint | 3. CHECK OPERATION OF DBA PRESSURE SWITCHES
4b979112-2f69-5ed9-af97-6e1ab7c3fede | note | CIBSE W5.6 System Checks
cfc1f612-0a31-590a-8d87-d9708d8c3b33 | note | AS2118.1-2017 - Appendix H4
04586bc5-65cc-5167-b341-597f1ce83cf6 | button | Does the pressure switch change state when system is activated (Rise in pressure switch)? | Yes, No
54e67a49-d6fe-5d7f-9d0d-4b35536a39b1 | note | Add Photo
47048997-2108-449a-80b5-18716ec5c05b | checkpoint | 4. CHECK OPERATION OF PUMP START PRESSURE SWITCHES
510aa0d7-044f-5d13-858e-c24e98bd5e34 | note | CIBSE W5.6 System Checks
0be2338e-6977-5ab0-a4c4-73ebc1f6facf | note | AS2118.1-2017 - Appendix H5.4
ad93c66a-5f89-58a4-b28d-3c647483200f | note | Are the pump start pressure switch settings in accordance with pressure gauge schedule?
dbe976e4-265c-5226-b0fe-d0c66680a5c8 | button | Have you checked the operation of All pressure switches individually? | Yes, No
63332290-62ac-51e4-a922-6d77d053f63e | note | Add Photo of Pressure Gauge Schedule
e81ec666-9fff-4343-bfc2-a99c475734da | checkpoint | 5. CHECK OPERATION OF DRY FIRE INTERFACES
4aaba76c-22c4-5e62-a341-a07aebed8bc5 | note | CIBSE W5.6 System Checks
73d6a02d-2806-5a73-8884-c5bd4f2336d1 | note | AS2118.1-2017 - Appendix H6
2385f222-a2f7-5c06-a244-0627b6d0689b | note | Activation of ancillary Pressure Switch (Rise in pressure switch) registers at FIP
e8b91d39-5c71-5ed0-920b-9fe8a2773784 | note | Activation of flow switches register at FIP | Yes, No
949b8463-9345-5019-84bd-3d111ed46f5c | note | Change in valve state/position register at FIP
4fcc45ee-9426-54df-8560-b32bc9d21d92 | note | Attach the valve list
dda2bea7-bc98-4f11-a37d-a114328c9c84 | checkpoint | 6. COMPLETE FORM 71 & ALL TEST RECORDS
f9977a64-cc53-5134-ba11-477e0132a8b8 | note | W7.10 Commissioning Certification
1f866f9a-e38e-5ae5-a00b-a56129bf822a | note | NCC 2019, AS2118
e2f8acd3-f7e4-5cc0-8957-8da694454317 | note | Flow test pass result on Form 71*
bdd2b65c-c591-5ddd-989b-5a4c10df8a53 | note | Record the pump start pressure switch set points:
7cb85c17-e34c-51c3-9f5f-037552f18ed8 | button | Record the dry fire interface test results: | Yes, No
59dec512-a6db-59b8-943b-f2f38215dfc4 | note | *Form 71 - Fire Hydrant and Sprinkler System Commissioning This form is to be used for the purposes of commissioning water based fire safety installations, as required by the Queensland Development Code – Mandatory Part (MP) 6.1, which is a building assessment provision under the Building Act 1975, section 30.
3c8c39e7-4e20-5889-b27f-af8b8736284b | note | Add Photo
f8e96ba7-eef1-45b9-b1f7-c3ab4cd21383 | checkpoint-no-value | GM Fire Sign Off
85a72054-7852-4536-8d2d-e1f07374d080 | signoff | GM Fire Sign Off
5a0a3752-a2f8-4b69-aa93-dd279a91117f | checkpoint-no-value | Principal Contractor Sign Off
274250b8-213b-4b5f-a5cf-1afc73107c47 | signoff | Principal Contractor Sign Off
d347bc8f-f8ab-4165-9067-39818a51e417 | checkpoint-no-value | Consultant Sign Off
0dd3a928-64d7-4fd8-863c-9f154d89bae4 | signoff | Consultant Sign Off
df32432a-3b8c-457d-a522-0a6ff579b1f0 | checklist | ITPS-207 Hydrant Commissioning |  | ITPS-207 Hydrant Commissioning
721e2277-4532-4f29-8e17-ed6caa5da4ce | section | Details
e776210c-575e-41a1-aff6-8e8018471cd9 | checkpoint | 1. CONFIRM WATER SUPPLY AND PUMPS PREVIOUSLY COMMISSIONED
3a70585a-928e-5189-868a-58802ba2b8aa | note | CIBSE W5.2 State of the System
b8859d2c-7c6a-56ec-b0fe-1132c8aa7cd4 | note | AS2419.1-2005 - Section 4 - To comply with Part 4.2
868a21a6-04c6-53a5-8f34-fa443998cdb0 | note | Have the Water Supply and Booster Pumps been commissioned?
7e9eae9c-50af-5368-bece-20f5f8b1cde8 | button | Are ALL Valves in the correct position? | Yes, No
e7269523-4168-4511-92cd-c384167ed8cd | checkpoint | HOLD POINT
a7120f6f-8f71-55cf-a085-59dc75a3d333 | note | There is a risk of damage to pumps if system is not ready for sprinkler commissioning . Refer ITPS-204 and ITPS-205.
1f2beeb0-3c07-44ab-8d1e-62da7677fbe3 | signoff | GM Fire Sign Off
766303a3-8fd0-43f4-9273-13279d8daa2b | checkpoint | 2. CONDUCT FLOW TESTING TO PROVE SYSTEM PERFORMANCE
d0199cf4-d4e2-55b2-beaa-b97413bad4a4 | note | CIBSE W5.2 W7.5 Preliminary Flow Rate Check
97d6531a-e76a-5598-8501-f13799c1d1e1 | note | AS2419.1-2005 - Section 2
b0d5e5cb-7978-5feb-986e-2f50697a5882 | note | 1) Confirm flow and pressure requirement
e9df99ad-a899-538e-b6b1-d272d9c039f7 | note | 2) Secure micrometre and calibrated gauge to hydrant outlet
dafe6cd3-87bf-5092-8746-48de13aa270e | note | 3) Manually start booster pump 1
cb18c3e8-90f4-50f9-a9c0-8022f5543876 | note | 4) Open hydrant valve to required flow rate
d095fc3d-99f9-532c-a65d-791b93acb6a2 | textbox | 5) Record residual pressure at required flow rate:
6a5d0021-0cfd-594f-a364-6481a6ac07e5 | textbox | 6) Record pump data:
25fb0e89-ad27-548f-9b3e-276552e07fb5 | note | 7) Confirm system achieves pass result
20866518-a4ac-5947-b600-4b78bc4c7e76 | note | 8) Close hydrant
5193aa31-864d-540d-9828-eaba41183676 | note | 9) Stop pump
2bcc1c9b-1f06-5484-9eae-c4b2c99f29c1 | note | Attach Hydrant Block Plan and Pressure Guage Schedule
8fd67300-3c75-4aae-9fff-3a82fb7ac5f1 | checkpoint | 3. CHECK OPERATION OF PUMP START PRESSURE SWITCHES
e7a3b51e-1fb5-5fa5-87d0-d3b6750e8017 | note | CIBSE W5.6 System Checks
46bb6798-085b-53b8-b1c0-b969993611b2 | note | AS2118.1-2017 – Appendix H5.4
0e72b020-dc6c-538c-a1d4-650bfd67d439 | note | Is the pump start pressure switch settings in accordance with pressure gauge schedule?
9384e2a2-e602-5cbf-861a-3749d74dcad5 | button | Have you checked the operation of all switches individually? | Yes, No
8a45f261-43d8-5912-ab51-cf80b2f462f0 | note | Attach Pressure Guage Schedule
e5a89728-cd05-422a-8b67-36c8f113329e | checkpoint | 4. CHECK OPERATION OF DRY FIRE INTERFACES
219924ff-a863-5453-b702-4c7a1ffa58c1 | note | CIBSE W5.6 System Checks
aed82c2c-05b0-5545-8c94-1dd60d7a6c45 | note | AS2118.1-2017 Appendix H6
c6801587-8c18-55d2-8257-b99ac2a62037 | button | Change in valve state/position register at FIP | Yes, No
2dbd1365-99db-5fe9-8537-59fd4cdf89f5 | note | Attach Valve List
23927d3f-07ac-48e7-9acf-820b1b7db23a | checkpoint | 5. COMPLETE FORM 71 & ALL TEST RECORDS
9ce18ec6-9918-5621-9ff3-ec94f01e84e6 | note | W7.10 Commissioning Certification
637ebcf9-755b-5a95-9aa4-9d179f1b35ca | note | NCC 2019, AS2118
fbe26b75-8581-522a-9f5c-cbf467c62c79 | note | Flow test pass result on Form 71*
54800295-0e0f-5618-8011-388d9a7589fb | note | Record the pump start pressure switch set points:
c4b7f9cc-8104-5ee6-878e-cd9147c777de | button | Record the dry fire interface test results: | Yes, No
f4eb9aa0-a765-5c96-a5c9-057fa093954c | note | *Form 71 - Fire Hydrant and Sprinkler System Commissioning This form is to be used for the purposes of commissioning water based fire safety installations, as required by the Queensland Development Code – Mandatory Part (MP) 6.1, which is a building assessment provision under the Building Act 1975, section 30.
e1ad30be-f7d2-57d4-bd3c-dbe1e64300d6 | note | Add Photo
3cf273a5-1cce-4ea8-b754-cfae7c0fa5d3 | checkpoint-no-value | GM Fire Sign Off
b33c20c1-58b0-44df-b4ed-d1cf5eaaf001 | signoff | GM Fire Sign Off
116ef8e6-810b-406d-a6ff-fd19d5404c75 | checkpoint-no-value | Principal Contractor Sign Off
c4e76ff4-21f9-41a6-94a2-d0c5b1333420 | signoff | Principal Contractor Sign Off
c6c70128-fa3b-46b2-83e9-5b4cc611039f | checkpoint-no-value | Consultant Sign Off
74426572-d062-4698-85f5-eab07c7f153f | signoff | Consultant Sign Off
24c1fb86-eca9-4b2d-8793-5ef65575cd31 | checklist | ITPS-400 Temporary Fire Strategy |  | ITPS-400 Temporary Fire Strategy
08d6cfa9-521f-4912-a7e9-6185ef1eeee9 | section | Details
3cd44620-c59f-4612-b4ee-56b18c702c3d | checkpoint | 1. INSTALL AND CHECK PORTABLE FIRE EXITINGUISHERS INSTALLED AT FIRE EXITS
d319ebb2-6dc6-478e-a95f-f807fccd312b | checkpoint | 2. INSTALL AND CHECK HYDRANT BOOSTER INSTALLED, BLOCK PLANS, LABELS
d4b462bb-c348-4eef-8328-1c8200e25ac1 | checkpoint | 3. CHECK EXTERNAL ATTACK HYDRANT IS WITHIN 20M OF BOOSTER
70865faf-f43e-42e6-8a8d-890ef8f45c83 | checkpoint | 4. INSTALL AND CHECK SYSTEM IS PRIMED WITH WATER (TOWNS MAINS)
e1ddf3d9-8c86-43e3-8f57-1f76129bc15d | checkpoint | 5. INSTALL AND CHECK HYDRANTS INSTALLED PRIOR TO JUMP
0e9e8aae-754e-48a3-9366-99a6f0c75153 | checkpoint | 6. CONDUCT WATER PRESSURE TEST OF HYDRANTS
efdbb532-7988-47c8-8ea6-f77a1be31776 | checkpoint | 7. HOLD POINT DETAILS
5e94d7ef-46da-5f81-9fd3-d666a314f628 | button | Hold Point Required: | Yes, No
187a6994-2a8a-4fe2-a3ea-ad9efa918ea0 | checkpoint-no-value | GM Fire Sign Off
6395d83f-473c-41fb-81ca-a45f72645190 | signoff | GM Fire Sign Off
432cac73-acdd-4a7d-b38d-a5f9b9e35991 | checkpoint-no-value | Principal Contractor Sign Off
2a3de1a6-7fcd-4df4-9b13-8aa08bae3ec2 | signoff | Principal Contractor Sign Off
dfddef1d-c76f-4613-8f63-250bf856a713 | checkpoint-no-value | Consultant Sign Off
4295924b-ca5b-4f88-9f21-32eb21504e94 | signoff | Consultant Sign Off
8664de78-eabe-4d0d-ae55-3f4d38baccfe | checklist | ITPS-401 Site Temp Asset Lists Extinguishers |  | ITPS-401 Site Temp Asset Lists Extinguishers
bc9a766e-45aa-463c-b48a-517bb71a7dcb | section | Details
5bd5dede-d5e8-4def-b5fe-7b287f078b2b | checkpoint | 1. ASSETS 1 TO 10
49967800-6d16-5c89-8d3e-8f12ae988470 | note | Add Photos and Numbers Below:
83ea09f7-c146-4713-992b-c9cc50df4137 | checkpoint | 2. ASSETS 11 TO 20
7dccf4bb-d44c-588b-9a34-5853c120fca9 | note | Add Photos and Numbers Below:
5228a0a8-10d8-4fb0-a0a0-eab44b09d45c | checkpoint | 3. ASSETS 21 TO 30
06c6659e-6da2-5264-a3ba-dcdb3034d4eb | note | Add Photos and Numbers Below:
afa2e2d4-4600-4008-8c10-57430571416a | checkpoint | 4. ASSETS 31 TO 40
6b06a32d-0cf4-5279-9b73-d46bf00fc99d | note | Add Photos and Numbers Below:
c9294617-056b-423b-aeaf-09d7b3b6f9da | checkpoint | 5. ASSETS 41 TO 50
8e4dee10-1fbb-54c0-b0bf-d46a830c983e | note | Add Photos and Numbers Below:
07d8d916-eeef-4bea-a542-6781013f0446 | checkpoint | 6. ASSETS 51 TO 60
d3dc04d5-40c7-5948-9d10-71da93fe5831 | note | Add Photos and Numbers Below:
62454714-ca1c-47cb-b2e0-7315e2c1ebc7 | checkpoint-no-value | GM Fire Sign Off
54d1a62b-9d10-450f-bb36-3e4e42b5a3fd | signoff | GM Fire Sign Off
06c64477-b125-41e1-8ae6-c114e055c10e | checkpoint-no-value | Principal Contractor Sign Off
adbfd8d0-3cd3-4859-9467-565b2baa3552 | signoff | Principal Contractor Sign Off
24fbc084-51dc-48be-8961-dd3675241507 | checkpoint-no-value | Consultant Sign Off
76168a90-598b-4126-815d-232bd22e084a | signoff | Consultant Sign Off
1e70382a-cd84-5ae1-8862-c1c058edde43 | checklist | Lendlease Contractor Schedule H Checklist |  | Lendlease Contractor Schedule H Checklist
7a748d55-533f-527b-b0f9-60e8fa293f5f | section | Incident Reporting
38cbcaa2-534b-452f-a320-76d33f74f460 | checkpoint | Incident Reporting
b5b35a37-7382-54ba-8bfb-811dbf4572bf | button | Any incidents were immediately verbally communicated to Lendlease | Yes,No
6801e20c-e2f1-5a7f-a0d5-fe47c4fd717b | button | A copy of Incident Notification Form was submitted within 4 hours | Yes,No
66e9a4c6-0421-5ef0-8732-cd78bca8e3a8 | note | Detail any incidents from the past month below and attach relevant forms below.
826609b4-fc54-5a39-ad75-e1293f234680 | section | Workers compensation first, progress and final medical certificates and Return to Work Plans
0c9492a0-811a-544b-b5bc-2fc846063034 | checkpoint | Injuries and Illnesses
e20f96b2-5ee3-56b2-b5c5-912388171f1b | note | The following have been provided;
5492c177-794d-5136-81c9-8f8430e1d1c8 | button | First Medical | Yes,No
823e0dc6-15b2-594f-962a-261c0a26bf92 | button | Progress Medical | Yes,No
09fd6dbb-22b0-55d9-bec1-c657d23b526c | button | Final Medical Certificate | Yes,No
d36edd68-abcb-576d-b8fc-6978886ed6b8 | button | Return to Work Plans | Yes,No
a20041b8-0ee5-5f04-a4e5-2f9b0b26598b | button | I have submitted any necessary Injuries and Illness forms within 2 hours. | Yes,No
b9e71c13-fb0c-5796-9a4d-1f3ce13a3ae0 | section | Reporting
e2cefbe1-7b4c-58cb-9296-52013acd2aff | checkpoint | A copy of any regulatory notices has been submitted to Lendlease via email immediately following receipt from regulator.
4094ba7a-5738-5658-93bd-78c5dff3acda | checkpoint | Daily Pre-Starts have been delivered to the office by 9am each morning.
4fb06383-4684-5418-9d3a-cc9f4daa39dd | checkpoint | I have submitted a copy of Toolbox Talks to Lendlease weekly, including records of attendance.
67b6449c-0fcb-586a-8ebf-2addf988ee69 | checkpoint | I have conducted a miniumum of 1 EHS inspection per day and a copy of EHS inspections for the month have been submitted.
2c6854ff-7dce-52fd-90e9-e611023a913b | checkpoint | Labour Statistics and Man Hours
c45fef96-b2bf-597b-b3ce-585cf62a4bdb | note | Contractor Labour Statistics:
3961a981-e885-5a9c-877f-050b8d38419c | button | Has been completed weekly? | Yes,No
2fcfc2ff-fc1b-5978-9631-1633f919466f | button | Has been submitted before the 26th day of each month? | Yes,No
506b1288-bedf-5659-a27b-52efdb96cd11 | button | Is attached below? | Yes,No
c5929b96-f03b-5652-94b3-156328f9754d | checkpoint | SWMS
1bfaab1b-8e49-53ee-9e9e-873030346dbc | button | Copies of updated SWMS have been submitted to Lendlease | Yes,No
e4104c40-5765-5a71-b723-f81d0bcfb590 | button | Contractor SWMS review register has been submitted to Lendlease | Yes,No
1adcbe56-3cdc-5f92-af30-4e947fc6e60f | button | Updated copies of signed SWMS have been submitted after onboarding each worker | Yes,No
d064d5c0-d0e0-5fe2-a4de-7727e0a3ff4a | checkpoint | Workers are trained and competent
973bcb55-6152-5f6d-a2b0-4d5902cff6f6 | button | Copy of current training register has been submitted | Yes,No
58d3b39a-17b8-56a7-9770-52ce522e2ef8 | button | Copies of licences, qualifications, training records for any courses attended during the month | Yes,No
3495576f-5639-59ab-a767-a607784a3cf2 | button | VOC (Lendlease Template) for concrete saw/angle grinders and Plant to be submitted for all workers before operation | Yes,No
aef74d7b-d587-5e34-9266-884de37191d4 | checkpoint | I have submitted copies of daily pre-start inspection records for the month
d77f5e32-8a3c-5a96-97b8-96e1ee4e803b | checkpoint | I have attached a copy of the up-to-date Plant & Equipment Register
863d56e4-a279-57b2-a68e-d4b15f9c5577 | checkpoint | Copy of current and up to date Electrical Register has been submitted ( 3 monthly unless new tools added)
1c11da09-d5b8-50be-807f-7a10f77c3645 | checkpoint | I have attached a copy of the Fall Prevention Register
f73063a9-6e9f-572b-981e-bc4461355341 | checkpoint | Lifting gear to be inspected, tested and tagged
e9a421ee-a73c-5e73-8691-a5ecb3c66c99 | button | I have submitted to Lendlease and attached below a copy of lifting equipment quaretly testing register | Yes,No
92bd2845-9677-5a10-9f62-2f292143cd1c | button | I have submitted annual inspection certificates to Lendlease | Yes,No
d8e7b937-09da-531f-a96c-18f76041589f | button | Monthly inspection register has been sent to Lendlease as per Lendlease Lifting and Slinging Guideline | Yes,No
ae92f7c6-9451-56f7-ae90-9960f5122f4b | checkpoint | I have attached copy of Hazardous Substances Register highlighting any chemicals brought on site this reporting period.
a02a0ab0-ff4d-53ee-8a92-1c3a98928fa7 | note | NOTE: Subcontractors are required to use Chemwatch to log all chemicals utilised
ba1f906f-1a0c-5a9f-a883-1abf31d17b82 | checkpoint | A copy of the Ladder register has been submitted this month
3d903859-b52d-52dd-aabf-1957c83c9f42 | checkpoint | I have attached a copy of Safety Data sheets for chemicals brought onto site within this reporting period (this month)
23484093-b5c0-5552-a60d-8d92e054fe12 | checkpoint | Temporary Works Design Register
75720ec4-cb43-5a56-a617-c22bb12e8de3 | note | NOTE Temporary Works Design Register must be submitted prior to mobilisation capturing of all Temporary works to be implemented by the trade
fcd4c867-242a-5081-80f1-6d415a64ea0b | button | I have attached the updated Temporary Works Design Register | Yes,No
5d21287a-0bce-5c38-a159-cd6673bf2998 | button | I have attached Evidence of Engineering Certification | Yes,No
d80834eb-8560-5715-b772-28441493f097 | button | I have attached Evidence of 3rd Party review of engineering | Yes,No
92ddcd9e-8e9b-5040-844d-c86a13562740 | signoff | Signatures
54b61932-c1fe-5b18-9a20-c6abcec6b8dd | checklist | POLICY-005 Safe Work Procedure |  | POLICY-005 Safe Work Procedure
90e555f1-b7db-5342-8f6e-ab9bb0160482 | checkpoint | Task Details
35e1d1ba-0df8-5940-a259-bccb2e916c8f | note | Use this form to record your safe work procedure after analysing a particular task in your workplace.
fb9e0a76-393d-592a-91df-e815f04daa63 | textbox | Work Area:
88a56175-6e66-5759-acca-aff345430919 | textbox | Task:
da1bc784-0a9f-5d8c-920c-1ef0c5a72b5d | textbox | Safety Risk: e.g. electricity, moving parts, noise
73bf96f4-9e1e-51a1-a557-4789936e6b2d | checkpoint | Personal Protective Equipment (PPE)
6455ae14-9591-5d78-a126-6b32f61c8232 | note | The following PPE must be worn, and precautions taken, when doing this task:
9f713af5-73c1-59dc-b084-7a3c2cf3b600 | tickbox | Work Gloves
6ec63488-d4c6-5096-8d62-8158b75870b4 | tickbox | Safety Glasses
64c63526-5a83-5c7d-a3fa-bbb76c5b5c62 | tickbox | Steel Cap Boots
83f78842-c3cd-59b1-9ff7-a8a0017d78dc | tickbox | Ear Protection
72bcb4cb-bf42-5039-b494-9375956a3b79 | tickbox | High Visibility Vest
30b3c185-f375-5785-99bd-75f1c6181665 | tickbox | Head Protection
943a7197-78bf-5b79-99b5-476d057fb450 | tickbox | Respiratory Mask
dee2c30b-edc0-5cd4-aaeb-4bf5a219de4e | tickbox | Face Mask
16c50b5b-5bd7-5e8b-bdcd-08c57fc113d6 | tickbox | Protective Clothing
7a9b8916-016c-5db4-a6f5-12378ee517c0 | tickbox | Wash your Hands
cc546369-bca4-51b6-ab24-8e4406ba760e | checkpoint | Supervisor Signoff
4570fb2e-7310-5ac1-a58f-8ade9076d7c2 | signoff | BY SIGNING I CONFIRM I HAVE APPROVED THIS SAFE WORK PROCEDURE
6faa1732-cd0c-59fd-9f51-6c60dff51223 | checklist | REPORT-002 Hazard |  | REPORT-002 Hazard
8111ace1-1386-5c1f-8290-3df28e3c8d3f | section | Details
7016619e-d9e9-575d-a598-04fc8176f882 | checkpoint | Hazard Report
43f0228c-2fe3-5c6e-85e3-84048cef3fea | note | GM Fire employees shall complete a Hazard Report in the event they identify a hazard that may result in injury or incidents to person(s), property/plant, the public or the environment.
82bf4eeb-5f0e-5f93-8ead-f55641b15686 | note | The principal contractor will be informed immediately and provided with a copy of this report.
423d5ed9-def2-5985-8cad-6c2afa7e0d08 | checkpoint | Hazard
c157c7de-d92d-505c-adbd-f9a7620ee7c6 | textbox | What is the hazard?
e23dd611-f6df-5b35-a2ee-6c2f1af58ca8 | checkpoint | Contributing factor
9664582b-bef9-5594-8875-1f56cd1aab82 | note | What are the contributing factors?
655bdfbb-ee2b-5728-aae5-5d3b6624ae50 | tickbox | Environment such as noise, slip or trip
9eb4f112-dc84-55ca-95ee-606b2ae625f4 | tickbox | Equipment/ materials i.e. wrong or inadequate
bdecd7f1-1e7e-59b7-8cff-fa37b4488ea3 | tickbox | Work Systems i.e. inadequate training
f9ec5884-395b-5fc3-8193-6f73553c064e | tickbox | People i.e. production pressures, lack of communication, lack of procedures
90dff80b-44cc-5e29-b4ee-fe7e1df7551e | tickbox | Other
d7af76c9-77a3-5b3d-85f2-229e182aed20 | textbox | If 'Other' please specify:
5b8936dd-da50-5d1e-a2b4-e9a5b6b57cc3 | checkpoint | Corrective Action
43a01400-3788-576b-a07c-ee5c2b0958e7 | textbox | What are we going to do to fix the problem?
dc1a0db9-5b08-56a1-8f09-eb0c829dcf7b | textbox | Who
7cb0663d-55b6-50d9-816f-cf668d5aa4df | textbox | When
09c0367c-9df2-5a1e-b57f-ce79d5be231a | checkpoint | Completed By
e8cad4f8-a779-54c4-8306-b65b38b7a52b | signoff | Signature
c2f28b0e-e821-54c1-a0ba-ee5986254ed9 | checklist | REPORT-003 Chemicals Review |  | REPORT-003 Chemicals Review
8111ace1-1386-5c1f-8290-3df28e3c8d3f | section | Details
76fb3e05-0ac8-4a4f-bb63-d30ea883739f | checkpoint | Details
fcbbdfbf-a580-58e2-aca3-6db3938b62ef | date | Date:
3d0346a2-15c4-5dd1-83d7-39fc0feb5a90 | textbox | Time:
eefd7d21-c3a8-5249-9155-dcea38b4b61b | checkpoint | Existing Register
96c307f7-229a-58ec-8971-6703204bb9aa | date | Last Revised on (date):
e98ad3cc-027f-5273-ad68-b11ab5b72cea | note | Upload a photo of the "Register-006 Hazardous Chemicals" as it is on site today.
586de132-0677-5158-8fb0-c38150ef6201 | checkpoint | Chemicals on Site
c1791c45-bbc2-5226-98ec-daa09d584a45 | textbox | Location where Chemicals are being stored:
64ef467f-1d6e-5a89-a833-62bedc96024f | note | Upload a photo of each Chemical on site
8cbd2a0e-3c28-53bd-b9da-5a65540b2443 | checkpoint | SDS
0dbf4695-dd94-54f8-b2bb-e4da68cc1f63 | button | Have any of the SDS sheets expired? | Yes, No
edcab06a-642e-5627-89fb-26a64e7739af | note | If 'yes', cease use of Chemical and contact GM Fire Management immediately.
c1c991c6-f8b7-58b3-bc66-63d765265e0f | note | Upload a photo of ALL Safety Data Sheets (SDS) on site.
58bfb4fd-b3d4-5f94-a67a-e067a225bcd0 | checkpoint | Declaration
c387a439-caf3-57d6-9d2f-ee67f6d50db0 | button | All Chemicals on site have been approved for use by the Principal Contractor | Yes, No
4f739c58-52c1-51f6-b261-1f8b7f974967 | button | All Chemicals are stored securely | Yes, No
6d438445-ff59-5c63-922f-bb4443e6bf75 | button | Any Chemicals that are no longer required on site have been removed and or disposed of as per WHSE guidelines | Yes, No
0da0ee29-0ac0-5051-ad4a-3e439a9e4b19 | signoff | BY SIGNING I CONFIRM I AM THE REPSONSIBLE PERSON FOR HAZARDOUS CHEMICALS ON THIS SITE, AND THAT ALL INFORMATION I HAVE PROVIDED IN THIS REPORT IS CURRENT AND TRUE.
42c7df9a-ccb8-5d7f-9abf-a956b1f84163 | checklist | REPORT-006 Incident Investigation |  | REPORT-006 Incident Investigation
8111ace1-1386-5c1f-8290-3df28e3c8d3f | section | Details
6412ac75-35b3-555b-a89e-87d89553cfa8 | checkpoint-no-value | Incident Investigation Report
26c7a877-82ff-5d4d-9964-4e831bec896a | note | GM Fire shall complete an Incident Investigation Report in the event of any injury involving medical attention or off site treatment or in the event of any incidents involving a near miss, property/plant damage or injury to the public or the environment.
c7009061-5139-5526-a062-83adc69dbabf | note | The principal contractor will be informed immediately in the event of the above. Following discussions with the principal contractor, a decision will be made as to who will conduct the incident investigation. The principal contractor will be provided with a copy of the completed Incident Investigation Report.
0bb42031-c4a8-5bcf-80ff-6fc5304ee4f4 | checkpoint | Class of Incident
319b1c6b-9f44-55ea-b16c-b1a07631b0a3 | tickbox | Injury
0adde8bb-4f35-5400-993c-c7d0180c2af2 | tickbox | Property/Plant Damage
621668cf-7542-5404-a731-45e940e7d4ee | tickbox | Near Miss
95d75d3d-669b-5354-b3b0-96b4a129a1c0 | tickbox | Environmental
67776edd-303c-58ed-b6a4-4c93c3ad56de | tickbox | Other
c5515547-5acf-5223-adaf-ff810432bbba | textbox | If Other - Please explain
e433ee97-85b5-52fa-97a9-25ca60ea13bc | button | Reported to Princpal Contractor | Yes,No
857bb4fc-18cf-5306-a76e-802c247b752f | textbox | Details:
e1d07f73-ecd2-514f-8842-5a2e0effd57f | button | Further Action Required | Report to Authorities,Other
820f14d5-50a0-5c15-96c5-71e6e32d06c6 | textbox | If Other - Please explain
bc36afa9-00da-5f53-99b5-0b99d61a7935 | checkpoint | Details of Incident
92284681-efd2-53d4-8e0b-d46de0d7e437 | date | Date of Incident
673f8d24-ff72-5e07-b453-93880d52a9f4 | textbox | Time of Incident
325ed646-43a2-5fc3-9425-0bef6e03fe7f | button | am/pm | am,pm
4b70799d-acc0-5966-a907-0ef28ba3f126 | textbox | Witness Name
541505a5-4428-5a09-a1c7-efa380a6cf43 | textbox | Witness Contact
fdfff4a4-8f76-588d-97bd-e1944521b0f4 | textbox | Nature of Incident
725a55af-18c7-57c8-afe2-bfa092de1b6a | textbox | Location of Incident
3f3be10a-9abd-53e3-82f0-2667d7e71aa8 | textbox | Description of Incident
b482344c-2e6d-577b-9ddb-70e3d053f88b | textbox | Details of damage to equipment/property?
5acc9a29-5ef8-55dc-93ab-9320efe0254e | checkpoint | Injured Person/s (if applicable)
24e6a102-3cb8-5740-9562-2f6fcc5871ca | textbox | Name
c68b8d90-60e8-5111-8e35-d7857559c628 | textbox | Address
e678a59a-6b1f-5756-b6cf-2d17da084cb1 | date | Date of Birth
66d64f8b-744b-59a5-8649-41a77a1b3902 | textbox | Occupation
f3631539-86a5-543a-ad2e-dad8be5e4b52 | textbox | Employer
df6586a3-039d-5599-8263-333b90fa2c9b | textbox | Referred/transferred to
2653d5b4-f6f4-5d10-b061-5710923ec319 | section | What factors contributed to the incident?
673b3686-24cc-52e8-a200-da491c74d4d4 | checkpoint | Environment:
5bebb027-96f0-5460-890a-132a143a47e3 | tickbox | Noise
5e04e3c6-c511-54d9-855b-61b79ba33d83 | tickbox | Layout / design
be7367f6-b65c-5e31-9806-b57e064484b1 | tickbox | Lighting
b344a257-3875-58bf-9242-ae1b70d9c52a | tickbox | Dust / fume
c1b98094-8764-57ae-8d8f-23524f9f5e83 | tickbox | Vibration
c6079cb7-cfed-539d-a3de-4ffe5242c1a5 | tickbox | Slip / trip hazard
85c76db0-7b13-5e0b-b320-9a0f6543aa2d | tickbox | Damaged / unstable floor
1e95cef6-f5ed-5510-89c5-ba7214c48c16 | tickbox | Other
7af769cf-fdc6-5763-a34f-36b7668432b1 | textbox | Other (if applicable):
da263eea-7753-5dda-9253-36aae5136ab1 | checkpoint | Equipment/materials:
fe1e78dd-509e-5b53-8078-3c13e8d0020a | tickbox | Wrong equipment for the job
48449b5b-94f5-56fd-aa68-28179f2a1234 | tickbox | Equipment failure
34dbaa91-66eb-5b35-86e6-12b7080c0add | tickbox | Inadequate maintenance
340c7cf0-23ea-5aaf-be3e-08341656325a | tickbox | Material / equipment too heavy / awkward
d44177e4-2535-597e-9309-931a3a8d12ee | tickbox | Inadequate guarding
3d7d49b4-0c2b-5d53-bfdc-aa67787549d7 | tickbox | Inadequate training provided
000690e7-a449-5a80-a869-a79c71c27c48 | tickbox | Other
e2a3d872-b06f-56d7-868a-7dfc157a60c7 | textbox | Other (if applicable):
29bb93fe-1a56-5a6a-a4d8-caafbdc08848 | checkpoint | Work systems:
5dd9bf85-df05-50a5-9d39-ba8c92524aee | tickbox | Hazard not identified
2fbf68fc-22c1-530f-9cb2-b87b25344ca7 | tickbox | No / inadequate risk assessment conducted
0387a054-0cba-5d62-97d1-4479ebe8b41d | tickbox | No / inadequate safe work procedure
d37a698b-994a-54ae-81f2-b04aa7a1df63 | tickbox | No / inadequate controls implemented
c6ba7810-1a06-5766-8b22-30f4fdc6cfd1 | tickbox | Hazard not reported
8f15171b-ea63-518f-a1d3-40a0cdb8bb86 | tickbox | Inadequate training / supervision
22ddaef3-e684-5031-82f2-eabc39055e20 | tickbox | Other
df7a8e40-28bc-528b-b28a-0b6efe49c3d3 | textbox | Other (if applicable):
13eb0e36-06f7-5153-ba71-5b36d7104644 | checkpoint | People:
68c29607-73a8-59a9-918a-e8a1a7758f3b | tickbox | Procedure not followed / no procedure exists
f49a9eb6-f469-5486-a041-424512d20bb0 | tickbox | Drugs / alcohol
315224a4-528b-59d0-b752-048abb08d4dc | tickbox | Fatigue
2ed0f27c-86d8-5e84-a4f2-361debecd863 | tickbox | Time / production pressures
1cf8af67-af67-5409-bca2-d1a6cdab08ea | tickbox | Change of routine
91dc8070-c2b8-5f0c-bd24-be694c6f87a7 | tickbox | Distraction / personal issues / stress
06712e9c-8051-58f7-8676-16be7955cabe | tickbox | Lack of communication
feefc030-bfe5-5354-a12e-104f9508da2b | tickbox | Other
c3685b47-7234-5973-bc9c-d337e162b8f6 | textbox | Other (if applicable):
1c21ef12-b1aa-5192-a53b-a50ba28212cd | section | Corrective actions:
e23dd611-f6df-5b35-a2ee-6c2f1af58ca8 | checkpoint | Contributing factor
34fb92e3-cc81-5b39-9cc4-3570d31ea806 | textbox | (from above list)
73874509-bac9-555d-8853-d738436ac006 | textbox | What are we going to do to fix the problem?
da26fb44-6d60-52fb-870e-90b8c5ffd716 | textbox | Who
f5d8b083-01e8-5841-aea1-53e16258b921 | textbox | When
585d5a57-d317-5a2c-8c86-399f10c406d3 | date | Completion date
09c0367c-9df2-5a1e-b57f-ce79d5be231a | checkpoint | Completed By
11f31f0b-4a44-5a8b-8133-2e07b430d536 | textbox | Name
9346513a-1500-5fae-b25b-d6e769dd31d7 | textbox | Position
40b6d092-dcdd-58fd-840d-c4a54e7f5c2d | date | Date
e8cad4f8-a779-54c4-8306-b65b38b7a52b | signoff | Signature
a4212db3-265b-5d19-9d4c-fb8f4780e6bf | checklist | REPORT-010 Request Corrective Action |  | REPORT-010 Request Corrective Action
8111ace1-1386-5c1f-8290-3df28e3c8d3f | checkpoint | Details
297d7da6-d94b-5611-bd0c-702c41cc33b1 | date | Date:
eedfd367-e843-5c3e-9193-ab41c84ef7aa | textbox | Time:
7a3ad93f-82ff-58bd-8541-95c08d4b5a25 | textbox | Location:
1207ac55-2622-5c8f-951b-2639b0dc564e | textbox | Supervisor Name:
d5aaa5eb-093f-5332-af20-a8b65033877e | checkpoint | Corrective Action Report
8935e3f9-ddeb-55d4-a028-6925bb83b863 | textbox | Principal Investigator
d0e213ca-26d1-5132-b6f3-d05c03ab33d5 | note | Non-Conformance is:
1ae631a5-072b-53cf-91df-6dd2aea39da5 | tickbox | Minor
de4f5de6-b1c9-550b-8bd5-3a7b53fda615 | tickbox | Major
bd4c3acf-a07e-5421-93fa-20e23a4a5b31 | tickbox | Critical
ddfa40b8-8d09-56f1-a1da-f91e07948d85 | textbox | Details of Non-Conformity Identified
db9b8c8d-7035-5210-8db8-53f6d5fc9674 | button | What is the likelihood of Fatality? | Very likely, Likely, Unlikely, Highly Unlikely
8687753c-2eb2-584f-b974-2298103b5684 | button | What is the likelihood of Major Injuries? | Very likely, Likely, Unlikely, Highly Unlikely
a0ddfdb1-ac2a-55ba-805f-904b06bf787a | button | What is the likelihood of Minor Injuries? | Very likely, Likely, Unlikely, Highly Unlikely
5ab5854b-b2a6-57e3-bf06-6738c14f36b6 | button | What is the likelihood of Negligble Injuries? | Very likely, Likely, Unlikely, Highly Unlikely
a1447274-b77a-579d-813e-8403ec194660 | note | Add photo evidence if applicable.
5d294295-86ae-51e1-92b2-e35eee764d2a | checkpoint | Corrective Action Plan
a567af7e-c8e7-580f-a2d1-bb2fbe30ed4a | textbox | Describe corrective action
b7d89de9-a208-53f8-875e-fef30341ce39 | textbox | Is this plan permanent or temporary? | Pernament, Temporary
167dc1ac-6bf6-5cec-95fb-38014a1058a3 | date | What is the proposed completion date?
42c21dbd-9bff-5051-bd1f-f936237b2320 | checkpoint | Signoff
2923664c-ab55-5c48-87d4-1901f7c5ef27 | signoff | BY SIGNING I CONFIRM I HAVE COMPLETED THIS REPORT TO THE BEST OF MY KNOWLEDGE