## Master List Templates
Id | Type | Name | Values | Prompting Name
87dbf723-3c96-462d-bf66-e455fedf5f06 | checklist | ITPS-209 Deluge Commissioning |  | ITPS-209 Deluge Commissioning
8eea13d2-6902-4b58-986a-3c9ed55875f7 | section | Details
7817e386-1f03-4300-b563-044adf24669d | checkpoint | 1. AREAS PROTECTED
0f26962a-7b53-515d-b6b3-22f5c1ae0bbc | note | CIBSE W5.2 State of the System
f6c8df84-0587-588f-a3c6-5fb3d4f3a162 | note | AS2118.3
579b67c5-1d15-5b2f-bfaa-4893198ed8bd | button | Have you ensured areas protected do not exceed 300m/sq per valveset? | Yes, No
69a0a452-eee7-5400-b4c3-1d18d8f626f5 | note | Add Photo
e13b2f41-965d-47fe-b293-b669ac827608 | checkpoint | 2. PRESSURE TEST
b77b8a3d-9734-5cad-b586-4c6c8f11065c | note | CIBSE W5.4.1 Pressure Testing
b5dd3634-0e61-5e2b-a53d-78f9fd902b38 | note | AS2118.1
088ba1e8-65f5-5bab-b519-e8d61450a0f6 | button | Have you completed a pressure test as per ITPS-203 for each deluge system? Note: Where open sprinklers are used ensure all heads are plugged prior to pressure testing. | Yes, No
b4e01887-62fb-5ccb-9378-5e7c57b095e0 | note | Add Photo
1ae11dd8-82e8-4a6a-9c03-a5c7b3ce35dc | checkpoint | 3. EQUIPMENT TESTS - SYSTEM FLUSH
728f2aca-b05d-5e3e-89ac-d818871303ea | note | CIBSE W5.5.2 Flushing Procedure
0851b159-f1c6-5973-977a-cb3586eb9363 | note | AS2118.1
543b63ae-49e1-55ad-b2ff-593c4e0fb7af | note | Complete the following PER valveset and open sprinkler head:
ec26301e-47b5-50d4-972e-b4d24505bd78 | note | 1) Flushing of each open sprinkler head to ensure debris is removed.
9c12745e-e70d-59ce-abb7-ac762de00e99 | note | 2) Setup filtration mesh and water bin at each open head off each system (is there are a large number of heads then separate system by plugging each head).
1903c679-9e94-5e4a-8788-0686e90ca55f | note | 3) Let water flow through pipework onto filtration mesh
29b7d2ca-0540-5357-b85d-d2214726c8f2 | note | 4) Once water is clear from debris shut off water and return system to normal.
79de03cd-4a66-53e9-a70f-2b83859bb91b | note | Take photo per deluge head and record deluge head/s location:
c62db6fb-5360-49e9-b201-c73c7170ea52 | checkpoint | 4. TRANSIT TIME TESTING
c61592c5-2057-5eaf-873e-fdc3c8791cd9 | note | CIBSE W5.6.2 Mechanical Checks: Automatic Control Valves
655f698f-f7f9-5633-8f34-22bd130f6610 | note | AS2118.3 Cl 2.9.1
dca9d2ad-e275-576e-b1fe-5f22044bf59a | note | Complete transit time testing
24da5ecf-6c2c-59bf-886c-e935fd082ba3 | note | Test of the deluge valve to ensure the transit time does not exceed 30s from the valveset to the remote deluge head.
ca7a5928-1b84-55d6-9e89-7a1559ca7660 | note | Add photo of results of transit time.
3a04b841-ac9a-4574-b21d-5e715db680a8 | checkpoint | 5. RETURN TO NORMAL OPERATION
0a93862e-2b51-5279-931c-3b3f60087f9c | note | CIBSE W5.6.2 Mechanical Checks: Automatic Control Valves
83d068c2-f166-5a5a-950f-7dba0ba9b53f | note | Are all open sprinkler heads re-installed where previously plugged?
eb006e7b-ed6a-56f8-8e5a-e7b3b4e19414 | note | Have system valvesets been returned to normal condition (or approved condition where construction still occurring)?
b0c22b87-45d6-5de6-a6c7-d46ea7ff4bc3 | button | Have water filled bins been emptied as per principle contractors requirements? | Yes, No
e3e5c507-051b-5c83-9f98-b95a7e82ef8d | note | Add Photo
f4e4ad9b-dd6e-4b4c-9955-2e35567b6483 | checkpoint-no-value | GM Fire Sign Off
8b042243-f6a4-4082-8826-804c333eb1ce | signoff | GM Fire Sign Off
44ef14c4-0907-4701-b770-28081a0f23f3 | checkpoint-no-value | Principal Contractor Sign Off
85d7a163-ece4-4347-b7b8-2cd6e059e22b | signoff | Principal Contractor Sign Off
287159ad-2b09-44b6-9445-76962cf3474e | checkpoint-no-value | Consultant Sign Off
0531c335-d3e4-4752-a6dc-20e7e02a75ed | signoff | Consultant Sign Off

## Project Checklist Templates
Id | Type | Name | Values | Prompting Name
c5dc7d7c-df99-5ec2-a589-b436df406a75 | checklist | 010SAF_08 SWMS |  | 010SAF_08 SWMS
a1c9d02b-1fdf-5e00-bcb7-56aeec761826 | checkpoint | 1. INDUCTION - Attach your signature to confirm you have completed the Principle Contractor's Induction.
d39621b2-57eb-545c-b19b-913b988ebada | signoff | By signing I confirm I have completed the Principal Contractors induction.
93e7a6a9-2417-5a63-a628-5bbbe7c40d86 | checkpoint | 2. ALL STAFF
cbaa5304-d926-5145-abea-643403fc7075 | note | 003G Using Platform Ladders
4c0dcfe7-d8a0-5008-bd8b-d7bc54f1ac2a | note | 004G Inhalation of Respirable Crystalline Silica
1117a6d0-9a4c-5b98-b403-d22a7b5ad3a6 | note | 005G Working at Heights
68979298-f5d8-548e-baec-8741d208ed87 | note | 006G Working at Heights Rescue Plan
1e1b9f0c-d012-59f5-9748-6f1fbc413551 | signoff | By signing I confirm I have read and understood ALL the SWMS documents listed above. I have reviewed these documents onsite with my supervisor and I have signed the hard copy.
d3e29984-ceb2-515c-9230-7a6de1161462 | checkpoint | 3. WET FIRE TECHNICIANS
b4e0d11c-383a-5193-a4d8-06886c652d7b | note | 019T Pressure Testing of Pipework
543f3f86-57b8-5b16-b786-9b1a07dba3bc | note | 020T Sprinkler System and Associated Pump Test
e8307916-4807-52bf-87e5-102669e43c3f | note | 021T Hydrostatic and Flow Testing of Pipework
b9ed5514-0cad-5767-9bc2-787d09c4b91b | note | 022T Fire Rating
3eda0a35-e17c-5ffa-8f13-550cbe45fa28 | note | 023T Fire Alarm and Emergency Warning Systems Testing
6a966737-d7b0-592b-adaf-4fd6c5c1ce28 | note | 024T Commissioning and Testing of Hydrant System and Booster Area
ec96f917-5f59-57b4-b51e-789fed1bc3e7 | signoff | BY SIGNING I CONFIRM I HAVE READ AND UNDERSTOOD ALL THE SWMS DOCUMENTS LISTED ABOVE. I HAVE REVIEWED THESE DOCUMENTS ONSITE WITH MY SUPERVISOR AND I HAVE SIGNED THE HARD COPY.
cb6326be-0982-5008-a0f6-df63d2b7f5a8 | checkpoint | 4. SWMS - DRY FIRE TECHNICIANS
5d11d398-a985-5a6c-aeb6-18ee293dc7c2 | note | 008I Removal of Existing Fire Alarm Systems and Devices
92d6eeb4-8277-5022-83a0-fc89644f8bed | note | 009I Removal of Pipework Fittings
52103321-2daf-5ff5-83c8-2ade86fd2490 | note | 010I Fire Alarm and Warning System Rough-in
8205c84e-07ea-575b-bae8-d3015acb0b02 | note | 011I Fire Alarm and Warning System Fit-off and Installation
884a1c0d-249f-5a69-b8f2-2e03f9760652 | note | 012I Installation of Fire Alarm and Warning System Cabling
61c0ba51-1491-512b-936c-ac2c0f143740 | note | 013I Installation of Pipework and Fittings
c29e79e2-249c-55ba-b869-187073053c35 | note | 014I Installation of Fire Control Panel & Emergency Warning Systems
12c89be3-5c80-51bc-be0f-9f94b3c520b4 | signoff | BY SIGNING I CONFIRM I HAVE READ AND UNDERSTOOD ALL THE SWMS DOCUMENTS LISTED ABOVE. I HAVE REVIEWED THESE DOCUMENTS ONSITE WITH MY SUPERVISOR AND I HAVE SIGNED THE HARD COPY.
02820854-2b26-5b84-8a78-37944efc42b3 | checklist | 010SAF_08 SWMS - Wacol |  | 010SAF_08 SWMS - Wacol
8111ace1-1386-5c1f-8290-3df28e3c8d3f | section | Details
a1c9d02b-1fdf-5e00-bcb7-56aeec761826 | checkpoint | 1. INDUCTION - Attach your signature to confirm you have completed the Principle Contractor's Induction.
d39621b2-57eb-545c-b19b-913b988ebada | signoff | By signing I confirm I have completed the Principal Contractors induction.
93e7a6a9-2417-5a63-a628-5bbbe7c40d86 | checkpoint | 2. ALL STAFF
e5f4983c-79f9-5d2c-aa86-19628d97bca4 | note | GM FIRE 001 Working with Elevated Work Platforms
cb97e826-81ed-5498-a1ce-8026ccaa34ad | note | GM FIRE 007 Manual Handling
3b53ae2d-a214-5919-8837-5ff53a686f11 | note | GM FIRE 008 Working at Heights
ad6ae2e0-0d48-5ac4-ab38-827dbaaad25f | note | GM FIRE 049 Working at Heights Rescue Plan
addf5555-e97e-5e0f-a3ae-e0bdc7cb00d5 | note | GM FIRE 051 Using Platform Ladders
29dc9e88-4534-5045-931b-379ccf48318e | note | GM FIRE 060 Inhalation of Respirable Crystalline Silica
1e1b9f0c-d012-59f5-9748-6f1fbc413551 | signoff | By signing I confirm I have read and understood ALL the SWMS documents listed above. I have reviewed these documents onsite with my supervisor and I have signed the hard copy.
d3e29984-ceb2-515c-9230-7a6de1161462 | checkpoint | 3. WET FIRE TECHNICIANS
f1b0bb87-0310-5266-aeba-e3557c2bc226 | note | GM FIRE 009 Pressure Testing of Pipework
aeb50cbd-b592-59f9-889d-b43dcaf721bd | note | GM FIRE 031 Sprinkler System and Associated Pump Test
afab2c86-7bc8-5186-b3b3-7364105642c4 | note | GM FIRE 032 Hydrostatic and Flow Testing of Pipework
ec96f917-5f59-57b4-b51e-789fed1bc3e7 | signoff | BY SIGNING I CONFIRM I HAVE READ AND UNDERSTOOD ALL THE SWMS DOCUMENTS LISTED ABOVE. I HAVE REVIEWED THESE DOCUMENTS ONSITE WITH MY SUPERVISOR AND I HAVE SIGNED THE HARD COPY.
cb6326be-0982-5008-a0f6-df63d2b7f5a8 | checkpoint | 4. SWMS - DRY FIRE TECHNICIANS
c22eb604-a543-55e8-a9bc-009aa41cad12 | note | GM FIRE 002 Wiring Rough In Minor
f0a3092c-62a3-588f-ae43-2a09e0cbbfe5 | note | GM FIRE 003 Fit Off Fire Alarm System
666707d9-d1a3-5bb1-800c-46a33c145d82 | note | GM FIRE 006 Installation of Pipe and Fittings
12c89be3-5c80-51bc-be0f-9f94b3c520b4 | signoff | BY SIGNING I CONFIRM I HAVE READ AND UNDERSTOOD ALL THE SWMS DOCUMENTS LISTED ABOVE. I HAVE REVIEWED THESE DOCUMENTS ONSITE WITH MY SUPERVISOR AND I HAVE SIGNED THE HARD COPY.
54ffa9b6-9564-5398-acbd-2a1b0b571b68 | checklist | ASSESS-001 Risk |  | ASSESS-001 Risk
8111ace1-1386-5c1f-8290-3df28e3c8d3f | section | Details
1c657631-910b-56b0-9af0-2d9a539b2537 | checkpoint | Assessment Details
473adbb6-fb69-5405-a428-8b7884a9567d | note | Use this form to document the risk management process for a single generic hazard.
fc378e8f-b7c5-5e24-bb25-3834e04367ca | textbox | Work Area:
c86dc88e-97db-5fa0-b06a-a0502e2dfa30 | date | Date of Assessment:
5d4bce7e-3eca-5343-9b52-1b242e11c868 | textbox | Name of Assessor(s):
053a334e-a68d-58c5-8848-d458c5f9f044 | textbox | Position(s):
01e9a620-02da-5f9f-8be4-de5842a76d0c | textbox | Incident Ref. No:
270f8fc3-f5f3-5606-80eb-fc2c80ae4f95 | checkpoint | Hazard Identification
9c62c279-d3da-5a59-9396-1d65ba053dde | textbox | Describe the Hazard:
bfd5195d-87aa-5c40-ac91-f0b3a6ea86bc | checkpoint | Risk Assessment
02415a39-4512-5a74-9fa9-6858f967c9f4 | textbox | What harm could the hazard cause?
ecb3ac0b-a049-58e0-a908-f9b04cfa2adc | textbox | What is the likelihood of this happening?
f26db3a6-d077-54ab-86e2-c1117532ef8e | textbox | Persons at risk:
4c0c9604-1046-540c-bb70-b6fabfac55a4 | textbox | Existing control measure:
3110c5a0-1c6c-57f5-9a9d-63760bb71d52 | textbox | Consequence:
a51920be-784b-56b6-8517-dcb995b0f792 | textbox | Likelihood:
0e66c542-a647-5acf-8450-13ff3db9df1b | textbox | Outcome:
32563b01-0feb-5e94-999f-2bc4f92e2c20 | checkpoint | Control Measures
76b90171-ca9e-5052-b8f8-3dd4919f87d6 | textbox | Elimination:
43fc69e5-0980-52a5-bf33-fc59ee839530 | textbox | Substitution:
b1d9fb39-3a3a-5cae-aaa6-01dc2d82ebbd | textbox | Isolation:
cab77874-4ef7-5e70-a359-f3451bc4ad59 | textbox | Engineering:
b0a7539c-2a1d-55e9-a38a-8da5230f075f | textbox | Administrative or PPE:
a657ee17-60e5-5b52-8b2c-17e528dc3e06 | textbox | Preferred control option:
71245745-e635-5d28-b0f1-51a28405fcc8 | checkpoint | Implementation
7d1d152e-7e80-5edf-be93-a8680d6d6728 | textbox | Associated activities:
917d87f5-7091-5acc-90b4-f038ed3c4ce3 | textbox | Resources Required:
48bded83-759c-5b9e-8dee-e7ea49afbcc0 | textbox | Person(s) Responsible:
d1e51675-d356-53f5-bd76-83ae6dd26c37 | date | Scheduled Review Date:
7717528b-ba68-53aa-a357-393c48e0a282 | signoff | Signature
cf1e460c-9d6a-576b-bc22-69ccfede73b9 | checklist | ASSESS-002 Manual Tasks Risk |  | ASSESS-002 Manual Tasks Risk
8111ace1-1386-5c1f-8290-3df28e3c8d3f | section | Details
1c657631-910b-56b0-9af0-2d9a539b2537 | checkpoint | Assessment Details
fffe5ae3-ea37-5ccb-8064-75daabfb5f7c | note | This assessment identifies how to manage the risks associated with hazardous manual tasks and control the risks of workers being affected by musculoskeletal disorders as per the code of practice under section 274 of the Work Health and Safety Act 2011 (the WHS Act). Use this form to help identify and manage risks of hazardous manual tasks.
4995501e-d426-5fa0-9806-7d71e116ea14 | date | Date of Assessment:
cd06d5fd-842a-51f7-ab58-7b99e8723801 | textbox | Name of Assessor(s):
5d64bed4-8ede-5a74-bc0f-bdc2b0782a53 | textbox | Position(s):
743945fc-b70c-5d62-8994-1b5dff254fdf | textbox | Incident Ref. No:
58267725-2c6f-55fe-83b6-0579eb36ea4e | checkpoint | STEP 1 What is the Manual Task?
f242c283-6115-5e96-8daf-07fddbfafb71 | textbox | Relevant worker(s) to consult:
9cc8076b-cfa2-5839-9764-d413107ff625 | textbox | Name of task or activity:
dc66359d-4fb7-5dc5-8cb0-706747f1a93b | textbox | Location where task occurs:
6262a8fd-e49d-5db8-aaa7-2cef97efc905 | textbox | Who performs the task:
69cd06ea-87e5-5ca2-87f8-843b2a870985 | textbox | General Description:
bf2b5766-0a58-58a5-9304-cb818f3230f5 | checkpoint | STEP 2 Is the Manual Task hazardous?
5fda0003-c9d7-5c70-bcc4-c09974d4cdae | note | Hazardous manual tasks can result in musculoskeletal disorders (MSDs) such as sprains or strains. Work through the following to determine which postures, movements and forces of the task pose a risk.
7be3e64e-4295-5f7c-ac4a-64d686941f8b | note | 1. Does the task involve any of the following risk factors?
7999b185-48b7-5f9c-82a1-48d10aea6a40 | button | Repetitive movement | Yes, No
67bf1e97-5ca3-5f87-ab60-e03e66ec3c3f | button | Sustained or awkward postures | Yes, No
ce34a3b9-15c7-563c-8783-459ca6f75bf7 | button | Repetitive or sustained forces | Yes, No
bd5cfbde-4069-53dc-9d86-ba787104141f | note | 2. Does the task occur over a long time?
16d890db-1e6e-5f3b-a474-f67b89b342b9 | button | More than a total of two hours over a whole shift? | Yes, No
8f90aa7d-3d67-5258-8904-c63c63d4d20d | button | Continuously for more than 30 mins? | Yes, No
3a23b8f5-b68d-59ab-a719-42388dd61cf0 | button | 3. Does the task occur over a long time? | Yes, No
26a42158-0a82-5b4b-a71e-0d795691482b | button | 4. Does the task involve vibration? | Yes, No
43fc7fae-32db-53b7-968e-2474aa54041e | note | 5. Is there a Risk? The task involves a risk of MSDs (e.g. sprain and strain) if you answered ‘yes’ to either:
bd38465a-cae6-5e3c-a550-757d8705979f | tickbox | Question 1 and 2 (above)
c67d5467-faa6-5e85-9263-74fd5f2eb1a6 | tickbox | Question 3 (above)
0c2ffbdf-431e-5801-90aa-4dbc155f9695 | tickbox | Question 4 (above)
6116130b-bf98-5626-83e7-f740f8ab883d | note | If you ticked anything in question in Question 5, continue to Step 3.
3d7f3e4c-c4c8-5ca2-91d6-be53defb6f92 | note | Additionally, if you answered ‘Yes’ to Question 4 the task may be a risk and will require further investigation.
43bb97fe-9131-5be9-be82-2660ffb39a19 | checkpoint | STEP 3 - What is the source of the risk?
16161039-f32e-5cc7-892e-cf593cf1dc7c | note | These are the things that are causing the risk and may be changed to eliminate or minimise the risk.
a39d65d1-ca5d-5c12-ab93-c7c03dd7c65f | tickbox | Work area design and layout: workspace available; design of workstation, furniture and equipment.
4cf868a2-329e-5a30-b552-7366106caf44 | tickbox | The nature, size, weight or number of things handled in performing the manual task.
58004720-de53-56ae-8de5-71c8ce2979ef | tickbox | Systems of work (e.g. pace and flow of work; resources available; maintenance).
d181a8c8-8d81-598c-8265-6d8867fb525c | tickbox | The environment in which the manual task is performed (e.g. flooring; obstructions; lighting; hot/cold/humid environments).
75306ffa-8cad-5fb5-8c60-4770efcfbc4e | checkpoint | STEP 4 - How do I control the risk?
aa25150a-04e5-563c-b3a2-a1b4ca48597c | button | Can the task be eliminated? | Yes, No
8a1c6b9d-1379-55ed-87cd-c1b6d43f2c14 | button | Can you change what is causing the risk (the source)? (e.g. change the work area; alter the size of loads; use mechanical aids; manage environmental conditions; use adjustable equipment; implement preventative maintenance program). | Yes, No
54ee5af1-9231-5885-b111-43aecae0e71a | textbox | If 'Yes', provide detail:
beebeca6-c568-57b3-a09b-855496531832 | button | Is training needed to support the control measures? (Training needs to be task specific, noting that training in lifting techniques is not effective as a sole or primary means to control the risk of MSDs.) | Yes, No
657acf89-b650-5e48-a415-c246d6263c9b | textbox | If 'Yes', provide detail:
249717bf-db57-5fb4-b61b-9f7678983512 | checkpoint | Implementing Controls
c2565812-add4-5258-a3d1-b2739274d79d | textbox | Name of Responsible Person:
37136cd6-72e5-5e61-8e3b-c2b04dce9a59 | button | Responsible for: | Approving, Implementing
2cce2333-56a8-566f-a44a-ed1f5f32afe9 | textbox | Name of Responsible Person:
96bb6997-f5c2-546d-a9ea-3ce4e61cb69d | button | Responsible for: | Approving, Implementing
524e2b9e-19d6-5662-970b-413d240e119e | textbox | Name of Responsible Person:
3561b485-8813-5e84-baf5-c2ba798dfa99 | button | Responsible for: | Approving, Implementing
27aa0f02-8b86-584d-9b56-8c649f942b71 | textbox | Name of Responsible Person:
9669440f-d3d0-5fef-9063-5c8cde37d756 | button | Responsible for: | Approving, Implementing
89334ebf-57ec-5f05-8b4e-750b91a0dc81 | signoff | BY SIGNING I CONFIRM I AM AWARE OF MY RESPONSIBILITIES AS OUTLINED IN THIS RISK ASSESSMENT
1ac85fbd-c1e0-52f8-a16f-a7d8e29a8854 | checkpoint | STEP 5 - Review the Controls
aaceaf1e-435f-5a17-8ff0-d5cfe135ec10 | date | Evaluated on(date):
e93df662-d87b-54f0-938b-aafdb4034e37 | textbox | Name of Assessor(s):
115ccbcd-968f-575e-92d7-2f149cdd00a5 | button | Consultation undertaken with relevant workers and others? | Yes, No
13d70f23-e587-533b-a70b-b4c53a730a48 | button | Have any other risks been created by the controls? | Yes, No
97df1da8-4965-5ee2-bee8-5a3ca5dedb25 | button | Have the controls implemented reduced the risks? | Yes, No
5b3de9a8-f51c-5710-9a6a-2ce2893531dc | button | Can further controls be implemented to minimise the risk? | Yes, No
cf536b61-665a-58a0-9365-8f90f64e78dc | checklist | ASSESS-003 Hazardous Chemical/ Dangerous Goods Risk Assessment |  | ASSESS-003 Hazardous Chemical/ Dangerous Goods Risk Assessment
8111ace1-1386-5c1f-8290-3df28e3c8d3f | checkpoint | Details
22e0ef6f-ce78-59e9-b297-ec7d25cc2853 | textbox | Hazardous Chemical (product name):
b9ff6ea6-d68f-5420-95ad-2ba4d5624d14 | textbox | Hazardous Chemical Reg Item No:
ab8a41a4-fa75-5fb0-8fd3-4d803208758f | textbox | Use:
eec44df0-883b-5db0-a668-e111f5465eb4 | checkpoint | Nature of Hazard:
2dc91869-2550-5def-bf64-150280c836f9 | tickbox | Toxic (Poisonous)
57e79973-4b78-5a19-bff4-9ad758bbf832 | button | Route of Exposure: | Eyes, Skin, Inhalation, Ingestion
88a840e5-526c-5c89-872c-81fa85f07ab4 | tickbox | Carcinogenic (Cancerous)
4680c316-7669-5a9d-8683-2c956fb7628f | button | Route of Exposure: | Eyes, Skin, Inhalation, Ingestion
38ef15de-e1de-5662-a3e8-96ffa271c10d | tickbox | Teratogen (Harmful substance that could affect abnormal prenatal development)
fd4384e6-b880-5ea5-bb34-433730fb5d8f | button | Route of Exposure: | Eyes, Skin, Inhalation, Ingestion
6729409a-d9af-5e52-bfad-187d9b49c1be | tickbox | Sensitiser (Reaction to an antigen, such as pollen)
48fd11a7-a813-5130-a444-f8842212ad17 | button | Route of Exposure: | Eyes, Skin, Inhalation, Ingestion
4b286c43-eeee-5149-b9e7-6a102080ec72 | tickbox | Mutagenic (Capable of mutating DNA, such as radiation)
a27b94e6-38ec-5ba5-8aab-a5df99b14cac | button | Route of Exposure: | Eyes, Skin, Inhalation, Ingestion
33120ba3-6d89-5c97-9f68-f0397a6328e1 | tickbox | Irritant (Inflammation of the skin, eye or respiratory system)
c1618867-6f7e-539a-981c-8137a74702c1 | button | Route of Exposure: | Eyes, Skin, Inhalation, Ingestion
397765e2-da84-56a4-9e94-718dadd9677a | tickbox | Flammability (The ease of which a substance will ignite, causing fire or combustion)
c668d39b-3320-523d-a31d-6e98a9718fdc | button | Route of Exposure: | Eyes, Skin, Inhalation, Ingestion
c5299fc2-0138-5c3e-9df0-fdb6f6a23c55 | checkpoint | Risk of Injury
280b1f79-378c-5eb5-8a96-ae6737484550 | button | Risk of Acute (Short term) Injury: | High, Medium, Low
bb54da10-e4b1-5592-a6f4-d2eba7d0becd | button | Risk of Chronic (long term) Injury: | High, Medium, Low
6adca422-e108-5631-9168-8f36735799d3 | checkpoint | Controls and Requirements
b5f30664-344f-516c-a94d-67b5ebe0115b | textbox | Control Measures to reduce exposure i.e. change to a safer product, ventilate area, (P.P.E.):
98cb9a3c-86f7-5dea-a134-48d30c1c7012 | textbox | First Aid Requirements and Storage Requirements:
42c21dbd-9bff-5051-bd1f-f936237b2320 | checkpoint | Signoff
f6e6ad58-755a-5ec6-ac1a-b3db6c24bfc3 | signoff | The persons listed below have been consulted in this risk assessment, understand the hazards associated and agree to use the control measures identified above to carry out the works safely and in a manner which protects themselves, others and the environment.
7a2e19d4-a232-5ccb-9e9b-f9c2132fc0a5 | checkpoint | Assessor Signoff
d0aabc79-7a66-528f-976e-31f5a7db0456 | signoff | BY SINGING I CONFIRM I WAS RESPONSIBLE FOR CONDUCTING THIS ASSESSMENT
1d3918d1-b96c-5d85-9466-39772b5c3e6b | checklist | ASSESS-004 Plant Risk |  | ASSESS-004 Plant Risk
8111ace1-1386-5c1f-8290-3df28e3c8d3f | section | Details
5011c755-395d-598c-bc65-ea69efabb143 | checkpoint | 1. Competent Peron(s)
642f9a57-a4fd-563c-8017-5111ebdce40c | note | This familiarisation checklist should be completed by a Site Supervisor or Site Foreman to verify that the workers involved in the operation of Plant Equipment/ Mobile Elevated Work Platforms (MEWP) can demonstrate their ability to understand and operate the MEWP functions in accordance with the manufacturers operating manual. This familiarisation checklist must be verified by a competent person who holds the equivalent licence/ ticket required for the type of Plant Equipment/ MEWP to be operated (e.g. Boom lift/ Scissor lift)
b999a52f-a645-58a4-8d70-5db9f480e95d | textbox | Your Name:
a22263ed-b4d0-5804-888c-e4649b968346 | note | Your Licences / Tickets:
aa5bf004-8ddd-5f14-ae08-73972a7fdb29 | tickbox | WP High Risk
68ef03d0-70f7-5dc3-8a9f-06c9f69066c1 | tickbox | Boom Lift
e011420d-898b-5249-a126-0298d60e2bed | tickbox | Scissor Lift
6b4baf27-144a-5bdb-bd21-1e55eac5af3f | tickbox | Vertical Lift
a01a5a65-b758-5b2e-a8f4-2a79f9dfd673 | tickbox | Other
5864fa60-af4e-52c1-ad57-2859916218f0 | textbox | If 'Other" please specify:
c06fe721-a6e8-585c-ad93-6752e11d8265 | checkpoint | 2. Plant/ MEWP Details
994d5bd9-fdbf-54df-96d2-0455ac305291 | textbox | Make and Model:
fc3fe0dd-015c-5f1a-8a14-63d409cda19d | textbox | Type (e.g. BL>11m, BL<11m, SL, VL):
6b0e5610-cf37-5886-aa78-b8bc2aea3ba0 | checkpoint | 3. Employee Competency
b13720e3-fa68-5eed-a3cf-f4730b816d2c | textbox | Name:
3113df9c-3f08-5c5f-a1d3-4e63db28264e | note | Role:
4621b649-4c3d-570a-b341-c628c028ab9e | tickbox | Operator
a84137df-a861-5b18-92be-868d0c104f98 | tickbox | Spotter
8245299e-7aef-51d3-b03d-d22b8274bdf6 | note | Licences/Tickets Held:
ff58851f-3f9c-5d82-8a1c-c7677c5b56f6 | tickbox | WP High Risk
6c51f3bf-7b4a-598c-80ef-5aa3019e9eb1 | tickbox | Boom Lift
44748388-293c-57ee-8ff1-7d5f2892af19 | tickbox | Scissor Lift
0345be07-e150-56a0-978c-b4fcbcdcecec | tickbox | Vertical Lift
06ebc66d-119e-58a4-8c6d-3668b83861ad | checkpoint | 4. Employee Competency
ad489344-3cb8-5436-9524-1660c7a2b0b1 | textbox | Name:
fdf43e7e-a511-5ad5-b4df-f6d2d0037160 | note | Role:
d64f3082-6007-5bf7-9d6f-a5dd4dee88dc | tickbox | Operator
911aab0d-85c4-54d0-84e7-aa56b0cdb689 | tickbox | Spotter
d76461bf-bb7a-5ff3-9c63-b0e151b51d3d | note | Licences/Tickets Held:
9447821f-0111-52c0-8ed7-0da106bc5d46 | tickbox | WP High Risk
c5cea7d9-aa94-558d-85ad-e0662bead4dc | tickbox | Boom Lift
b82921d0-26b0-5045-b43f-d617058fa15d | tickbox | Scissor Lift
bd1f4ff6-a6d3-558f-9520-872d8e2aab60 | tickbox | Vertical Lift
3ef8e758-7384-5d13-8fa3-292a5f04a9d8 | checkpoint | 5. Employee Competency
db5e0592-fcb8-5846-ac93-0ca9146343b0 | textbox | Name:
78ae0bce-337b-5c4a-a201-b32d90decfad | note | Role:
30745a12-c816-5f95-9c80-95ac7dfa9124 | tickbox | Operator
8b8af59e-b89b-5818-9be3-d525e8caddf5 | tickbox | Spotter
3fc54ce8-6044-5d65-a977-a64b92827df4 | note | Licences/Tickets Held:
018e850c-40c9-557a-90e7-8968c3b367e3 | tickbox | WP High Risk
70f75c22-2ce6-5034-bd9e-e15d49055932 | tickbox | Boom Lift
c10357af-7e77-568d-9f22-41905e86a32f | tickbox | Scissor Lift
044c7996-ed6e-5eb3-9609-63f46dfc596b | tickbox | Vertical Lift
0db35e59-5266-54bd-bc6b-7ababdb43cef | checkpoint | 6. Declaration (to be completed by competent peron(s) noted in Section 1.
218fe4de-f3cf-52af-bd89-080f289562b3 | button | All 'Operators' hold the appropriate licence/ ticket for Plant/ MEWP | Yes, No
eeef1428-6a11-528c-995a-36882aeb0bf1 | button | All 'Operators' understand the operational controls and emergency functions | Yes, No
726feb5b-9c47-530e-a78c-1817784b07c9 | button | All 'Operators' are aware of the logbook and pre-start requirements | Yes, No
a46d561a-c056-51a1-9c3e-1fdc466efe04 | button | All Ground Support understand the emergency functions | Yes, No
c5bf15f3-19d1-5c51-99b8-b30d1635e2a6 | button | All GM Fire employees on site have participated in an emergency drill | Yes, No
f7212521-96e0-557d-a667-f54d287cccf4 | button | All GM Fire employees have signed onto applicable SWMS | Yes, No
9899d9ec-b306-5aed-bbc5-b1347ea6537c | signoff | BY SIGNING I CONFIRM I HAVE ALL PERSON(S) LISTED ARE COMPETENT TO OPERATE THE LISTED PLANT/ MEWP ON THIS SITE.
3a7eea15-0af0-5a8b-9252-a43ee66db881 | checklist | ASSESS-005 Confined Spaces Risk |  | ASSESS-005 Confined Spaces Risk
8111ace1-1386-5c1f-8290-3df28e3c8d3f | checkpoint | Details
f642bd3a-93b6-5307-84ba-8ac17a37ae38 | note | Use this form to document the risk management process for a Confined Space.
aefcbe59-67d2-53f4-99ae-82c82315ffb6 | date | Date of Assessment:
6a10f9eb-f00d-5fdc-b17b-2b864046e326 | textbox | Name of Assessor(s):
9841a384-ff41-5ba0-86b4-bba7da014bb1 | textbox | Position(s):
270f8fc3-f5f3-5606-80eb-fc2c80ae4f95 | checkpoint | Hazard Identification
970036fb-8e63-59d6-bb86-611296e78c26 | textbox | What Hazard/ Risk is associated with the task?
19119fed-a0d5-5644-939e-d1fa384cec0f | textbox | Planned control measure to remove/ minimize hazards/ risks
6b210b4a-98db-59e3-bf16-bb3aa67e0b31 | textbox | What Hazard/ Risk is associated with the task?
b3d99b4e-5a6a-5b63-b845-8b55c343a048 | textbox | Planned control measure to remove/ minimize hazards/ risks
1dbc95e8-c416-50fa-95d8-2e9aa78aefd1 | textbox | What Hazard/ Risk is associated with the task?
a24e2eb0-8fcf-5037-b603-95ffe7791740 | textbox | Planned control measure to remove/ minimize hazards/ risks
94165423-6b09-50b1-a9c9-09570b022cac | textbox | What Hazard/ Risk is associated with the task?
961960da-8888-531d-acf5-08e877368971 | textbox | Planned control measure to remove/ minimize hazards/ risks
f997c27e-2b64-5eff-bbab-763cd73852a3 | textbox | What Hazard/ Risk is associated with the task?
762939b8-e0b3-506e-9c2f-3536abbab1d1 | textbox | Planned control measure to remove/ minimize hazards/ risks
520f3973-2a3e-554c-9da3-fcd0d6905a7f | checkpoint | Review
051f0f3c-2c13-5430-8b65-cf7db80bef65 | button | Does the Risk Assessment Identify that confined space work is involved? | Yes, No
1cd1b83e-0075-5cd7-b749-189d1929a1f3 | note | If YES the Confined Space Work Permit MUST be completed
b71e5ff3-bacb-59d3-8c23-58b0471e25ef | note | NOTE: EMERGENCY & RESCUE PROCEDURE: Where an accident occurs which requires that an emergency rescue be attempted, the standby/ rescue person is to immediately contact EMERGENCY SERVICES on 000 for assistance.
7a2e19d4-a232-5ccb-9e9b-f9c2132fc0a5 | checkpoint | Assessor Signoff
ef2c80a6-3684-5688-8513-5b1de9d6eb7b | date | Scheduled review date:
946f9c2d-1950-57b6-981a-43e43c738227 | signoff | BY SINGING I CONFIRM I WAS RESPONSIBLE FOR CONDUCTING THIS ASSESSMENT.
060f713a-8df4-52be-9f49-596b47a5a859 | checklist | ASSESS-006 Job Safety |  | ASSESS-006 Job Safety
5e25be48-4354-51fa-a917-1881487cb8a0 | checkpoint | Client Details
d287a617-2879-5b32-95e6-69035ab4d1d7 | textbox | Client: i.e. Principal Contractor
36ce6c2e-810e-598a-b004-f609963bc9f5 | textbox | Client Contact Name: Responsible Person(s)
415487fb-c3de-5e51-9a95-f4912068649a | textbox | Client Contact Phone:
198af748-0694-57ea-9255-f3b0e23e148b | textbox | Client Contact Email:
bad8a559-d874-55eb-a218-4243f23c1f05 | checkpoint | Job Safety Analysis Details
c7363dde-59c9-50b5-a55a-eb0dd4ef2793 | textbox | Work Activity:
6e618c2c-f9aa-5d3f-b53d-352330057258 | textbox | Location:
fdafb1e6-3b68-5f09-909b-fe4ccf1c4005 | textbox | Who is involved in the activity?
c6801c12-770b-5a1b-801e-d9bec719ed24 | textbox | Plant and Equipment used:
452dcb6f-bc08-5372-a340-865dd5c94bd3 | textbox | Maintenance checks required:
ccf2a411-2a71-5cbd-b7e7-9dd89d7b8c16 | textbox | Tools used:
3b5c311c-7668-588b-9f71-5d00a552d789 | textbox | Materials used:
2f2d1a19-2c21-52d8-859a-22c543ed433a | textbox | PPE used:
6ba3fd9f-2f1e-509a-87ac-76a70975a065 | textbox | Certificates, permits and/approvals required:
bf689cda-da96-5e69-b85b-9888bd950c1b | textbox | Relevant legislation, codes, standard MSDs etc. applicable to this activity
f948400d-3b6d-5037-a27e-a1da8d06232a | signoff | This JSA has been authorized by:
df68f526-1e94-59d2-832e-1b4bc4eb113c | checkpoint | Job Safety Assessment
fd86d7b3-716b-5aef-94ca-58c67fe15b72 | note | Refer to the attached Risk Ratings table to complete the following..
bc5f33ca-3b4c-559e-b15a-aa4a4a041660 | textbox | Job Step Details:
d51ace86-47cd-5b73-83b8-30a224f79b22 | textbox | Potential Hazards:
dba3f86d-b828-5409-9489-89b9fcfe5452 | textbox | Name of Person(s) Responsible for work:
6ab17f0d-0018-51a6-a77b-19b49e7e5aa7 | button | Risk Rating: | Low, Moderate, High, Critical, Catastrophic
7c5df8e1-1f14-5a0b-a3ab-eb5e6e594bc1 | button | How to Control Risks: | Eliminate, Substitute, Engineering, Administrative, PPE
a7041e15-5ede-57c4-b6fc-976e1e06caa1 | textbox | Job Step Details:
78d1de29-7e12-5d88-97be-09b1797def9c | textbox | Potential Hazards:
fb2be1bb-41b4-57a5-bbb8-e611e37982fa | textbox | Name of Person(s) Responsible for work:
4362cba1-6022-5162-9ea0-157eea9f1b4d | button | Risk Rating: | Low, Moderate, High, Critical, Catastrophic
3b31946f-4e7c-54af-b3c4-138391ab8729 | button | How to Control Risks: | Eliminate, Substitute, Engineering, Administrative, PPE
fc648bd7-97cf-5258-b7e4-4530afef5d8f | textbox | Job Step Details:
658bd54e-c4b0-55fa-bed6-d9e7e39230cd | textbox | Potential Hazards:
c1b12c90-9f26-552f-ba1c-71434fed6b52 | textbox | Name of Person(s) Responsible for work:
556a3b5c-b1bb-5296-9c82-a27404df8770 | button | Risk Rating: | Low, Moderate, High, Critical, Catastrophic
3141a230-6137-513c-9a31-287554f12a21 | button | How to Control Risks: | Eliminate, Substitute, Engineering, Administrative, PPE
42c21dbd-9bff-5051-bd1f-f936237b2320 | checkpoint | Signoff
9c249912-b3c0-5116-b8ec-aba0ea058e1e | signoff | This job safety analysis has been developed through consultation with our employees and has been read, understood and signed by all employees undertaking the works:
930a3e43-5647-50d1-87f2-966cce2343da | checklist | CHECK-002 Site Inspection |  | CHECK-002 Site Inspection
7604d349-3c9d-59ec-8769-a0cfe4110d87 | section | 1. Administrative, training and risk management requirements
b646b6a2-68d2-5b04-925e-0e13a9bb914a | checkpoint | 1.1 - So far as reasonably practicable, all workers carrying out construction work on the project have been made aware of the content of the WHS management plan, including any updates, and their right to inspect the plan.
6ba63d7d-3b3f-5c31-9434-f4939b574a87 | checkpoint | 1.2 - All workers carrying out construction work have received the general construction induction training.
b9691151-2ecd-5ee2-8ec8-b533204f2fd9 | checkpoint | 1.3 - Workers have been informed of the site-specific health and safety rules.
60ac4aca-7460-564d-ba14-2d3d98bfd234 | checkpoint | 1.4 - Suitable and adequate information, training, and instruction has been provided to workers in relation to work they are carrying out.
66bab419-a393-57f6-9c97-758d79271510 | checkpoint | 1.5 - Personal protective equipment (PPE) is being worn in accordance with the projects requirements.
2ab82d7a-cc3c-56a0-a89c-ba9e4252acc3 | section | 2. Safe work method statements
c145e282-9bf0-58ac-8a85-4500302a4c6e | checkpoint | 2.1 - A safe work method statement (SWMS) has been prepared for each high risk construction work activity that is underway or about to commence.
fe929405-eae8-5ca8-8783-fd58e2de54ac | checkpoint | 2.2 - Workers have reviewed and signed off on the relevant SWMS
7934e80d-dec5-5f41-be0b-42bbfcdd01e2 | checkpoint | 2.3 - High risk construction work activities are being carried out in accordance with the relevant SWMS.
8f0ef03e-318f-5cf3-b827-93b54c1df497 | section | 3. The work environment
e6018bbf-c8f1-5f07-b149-1bf83ae3ef97 | checkpoint | 3.1 - The work environment has been maintained such that it is clean and in a safe condition.
79bdc24c-1c00-5acf-983d-ebaa5ce5fad4 | checkpoint | 3.2 - Work areas are clearly identified and separated as necessary so that work can be undertaken safely.
1825c9fa-24bb-50ad-8b3b-a1e424e13ba5 | checkpoint | 3.3 - Lighting at the workplace is sufficient to allow:
f8272eb3-01c5-5337-a307-f72286a48c32 | note | ○ Each worker to carry out work without risk to health and safety.
1be19c4f-a82e-522b-98e5-e5aa656efb60 | note | ○ People to move within the workplace without risk to health and safety.
aef67d61-2c29-5ed8-9db6-bcf3ceacb0db | note | ○ Safe evacuation in an emergency.
e6860137-88a0-51f5-bab0-d6de14d63cb6 | checkpoint | 3.4 - The workplace has sufficient ventilation to enable workers to carry out work without risk to health and safety.
4ff74d5f-cec6-5c19-bd25-e6838e8f1c56 | checkpoint | 3.5 - The entries, exits, and access ways in the workplace are kept clean and clear of materials and waste.
48066b16-7c21-5768-945d-e4a5cf766b0b | checkpoint | 3.6 - A safe system has been implemented for the collection, storage, and disposal of excess or waste materials.
0b615730-4ffb-51cd-bfb3-02fcfc4435d7 | checkpoint | 3.7 - Sufficient area has been allocated to safely store materials or plant for the construction work.
8dca0770-d2f9-575c-9e8a-bc6b57a4f871 | checkpoint | 3.8 - Protruding objects that are a hazard have been made safe (e.g. exposed nails, vertical reinforcing steel).
b201c421-5b2c-5c48-9704-05cf6113c44a | checkpoint | 3.9 - Adequate facilities have been provided for workers, including toilets, drinking water, washing facilities, and eating facilities.
c51929b0-8776-5f5d-9a2c-3ebcffee0dad | checkpoint | 3.10 - First aid equipment has been provided for the workplace and is accessible to each worker.
18a4e767-8b1d-5672-a5a5-274690a036b4 | section | 4. Confined spaces
2825d9b2-da10-596a-9ce0-b40fcc56a1cc | checkpoint | 4.1 - For each hazard associated with a confined space, a competent person completed ASSES-05 Confined Spaces Risk.
0a584ab9-a5b3-52a1-b882-f4b9709cc8db | checkpoint | 4.2 - Prior to commencing the works, FORM-003 Entry Permit Confined Spaces has been completed and approved.
89309c03-7f35-5362-a583-36791c1dba8a | checkpoint | 4.3 - Appropriate signage has been erected for all confined spaces.
d0a6d31c-65a4-5bf4-bc31-672ba9175665 | checkpoint | 4.4 - First aid procedures and rescue procedures to be followed in accordance with POLICY-006 Confined Spaces Rescue in the event of an emergency in a confined space have been developed and practiced to ensure they are efficient and effective.
ded5ed0a-e444-5b8a-bb7f-fdbe7f8fb660 | checkpoint | 4.5 - Workers required to work in or around a confined space have been provided with information, instruction, and training in relation to the:
bed85791-cdf2-5734-99e5-42eabe40f212 | note | ○ Nature of all hazards relating to a confined space
be7ccc94-3134-5b95-8b20-72fefb415b43 | note | ○ Need for, and the appropriate use of, control measures associated with those hazards
b110c5ef-6275-5bf5-a856-5a63e44d03ea | note | ○ Selection, fit, use, wearing, testing, storage, and maintenance of any personal protective equipment
1a99ce71-7f11-5eeb-a21b-b350ded8d8c3 | note | ○ Contents of any confined space entry permits that may be issued
b0c02c77-ff62-5a00-8a01-e40663b3102c | note | ○ Emergency procedures.
e81da6f2-b7fb-5d0c-920d-ac0985916342 | section | 5. Working at heights
e2a6047c-3469-57d7-a1ee-63a6d2ce1e6a | checkpoint | 5.1 - A SWMS is available for all high risk construction work that involves a risk of a person falling more than 2m that has commenced or is about to commence.
c2fb3d08-8253-53dc-a912-7762ad36b3c3 | checkpoint | 5.2 - Where a risk of fall of less than 2m exists:
15a0bb70-25a2-55ce-8391-f9705261ae79 | note | ○ Each hazard that may result in a fall or cause death or injury if a person were to fall has been identified
098e60b1-4049-5b81-9802-dc44b50477cb | note | ○ The risk of death or injury that may result because of the hazard has been assessed
d8e17ce6-5b0d-5d71-adcb-c9012baa2fa9 | note | ○ Any control measures necessary to prevent, or minimise the level of, exposure to the risk is used.
98b57a94-c6a8-50d7-bb1c-2783d46d3990 | checkpoint | 5.3 - Where a risk of fall of at least 2m exists, control measures have been used which:
df712649-e072-54fe-b908-fe63884b915b | note | ○ Prevent a person falling any distance
28993959-da47-509e-a241-bb45845a83ee | note | ○ If prevention is not practicable:
55b684af-87ab-5194-82b6-3e644dbb1a7b | note | – arrest a person’s fall
7575aa24-7d52-5200-8719-e639552c447b | note | – prevent or minimise the risk of death or injury to a person when the fall is arrested.
6a7044d6-a81e-5157-bf4a-f5cbc210f31d | checkpoint | 5.4 - Ladders are not used to support a weight greater than that for which they have been designed.
d81daed7-0057-50a6-9fe9-8aece2cab495 | checkpoint | 5.5 - Ladders are used where the:
d8458251-f7d1-554a-bcc3-372ab76e7d8a | note | ○ Bottom of the ladder is on a stable surface
c8fdd838-d4e2-5652-83e9-9bc5b3b6145b | note | ○ Rungs of the ladder are approximately level.
3f3316e4-f01d-5a03-a2af-4637d940f52b | checkpoint | 5.6 - Scaffolding has been erected by appropriately licensed workers.
e8760cac-e387-5620-9ab6-470830ad9fb6 | checkpoint | 5.7 - Scaffolding is or has been erected and/or dismantled so as to eliminate or minimise the risk of falling at least 2m to people carrying out the work, in accordance with the regulations
faed25a7-0d74-5c49-bf12-7d35d9c1c221 | checkpoint | 5.8 - Safe access to and egress from scaffold has been provided during erection, use, and dismantling.
06596e0e-a7d6-5ec1-ae87-b458bc352bec | checkpoint | 5.9 - Written confirmation from a competent person stating that the construction of a particular scaffold has been completed, has been obtained prior to the use of that particular scaffold.
a1cf7634-7b7a-503b-98b6-a44b1401c2de | checkpoint | 5.10 - REGISTER-007 Plant and Equipment is up to date and includes all mobile plant in use.
92665bac-aa8b-572e-82c0-08a5392f0bfe | checkpoint | 5.11 - CHECK-004 Pre-Start Plant and Equipment has been completed for all mobile plant in use on delivery to site.
3dd77402-8a87-529b-8183-9c072abbce8a | checkpoint | 5.12 - CHECK-005 Regular Plant and Equipment has been completed for all mobile plant prior to commencing operation of the plant that day.
26a08f78-359d-5909-8059-66675eee2c23 | checkpoint | 5.13 - Mobile plant operators hold the appropriate high risk work licence.
23b709bb-1735-5ef2-90a2-edf28c5eaf62 | checkpoint | 5.14 - Where there is a possibility of powered mobile plant colliding with pedestrians or other powered mobile plant, a warning device has been fitted.
a556791d-1316-51ef-8b5c-74f5158d5808 | section | 6. Electrical
b2dcd8ef-695d-5a07-a1c9-d7a4c42cb637 | checkpoint | 6.1 - Electrical leads are arranged to avoid damage.
d2a5d551-016e-5c24-aaed-9a6546efb65d | checkpoint | 6.2 - Electrical equipment has been inspected, testing, and tagged in accordance with AS/NZS 3012 Electrical installations – Construction and demolition sites.
a3dea501-b49e-52a0-b686-be4f3b199e32 | section | 7. Hazardous substances and dangerous goods
28f006f5-6133-536c-83c5-e5fd046e9474 | checkpoint | 7.1 - All hazardous chemicals that are used, handled, or stored at the workplace are correctly labelled.
d9654d68-e223-5e2a-a924-23ef86d304da | checkpoint | 7.2 - A safety data sheet (SDS) exists and is available for inspection for each hazardous chemical used, handled, or stored at the workplace.
569fad8c-3f02-54bb-9e8d-8a513e63a228 | checkpoint | 7.3 - A register of hazardous chemicals used, handled, or stored at the workplace has been prepared in accordance with the regulations and is kept at the workplace.
73d14d34-271c-5e50-a0cd-036c9275e063 | checkpoint | 7.4 - A spill containment system has been implemented in each part of the workplace where there is a risk from a spill or leak of a hazardous chemical.
a5f93861-409f-57a4-9892-aad365d82b0e | section | 8. Corrective actions
a3895f4e-c7f0-509b-ac43-872a6873bc7e | checkpoint | Corrective actions
fefdfa68-8ae7-5784-8f52-ff31386b2624 | section | 9. Inspection sign off
19075f73-f3d6-5581-b9a9-39135e1c7056 | checkpoint | This workplace inspection checklist has been completed by;
4b32712d-5eb5-5f21-8318-9f10d9fee1e3 | textbox | Name:
8f6f1e26-c9d1-5d5c-beb5-fb775c1e28a2 | date | Date:
75e3ab6c-26b3-5c04-9c56-ec536230e4ac | signoff | Signature
690502ea-7da5-5119-ba91-b2aa394089de | checkpoint | I hereby certify that all corrective actions as identified in the above checklist have been completed;
be7ee8f6-2fdf-5e61-aee6-adf9bbb71704 | textbox | Name:
f58dc23b-c6d5-59c2-9d2a-57694b8eff87 | date | Date:
3e494399-cc9e-5e9f-964d-deff12bc6678 | signoff | Signature
7bd28543-904f-5683-acd7-cdd9184635f4 | checklist | CHECK-003 Site Establishment |  | CHECK-003 Site Establishment
8111ace1-1386-5c1f-8290-3df28e3c8d3f | section | Details
0b4ad232-5674-51d3-9408-aef0b58a609d | checkpoint-no-value | Details:
a9f0eb07-3912-523a-be5f-a802d6ff641b | textbox | Project Number:
be704f51-8345-5d07-82ad-4691b8d46bd7 | textbox | Project Name:
55438198-cfca-5417-84b8-414b08417475 | textbox | Project Manager (PM):
cecfc96f-5250-5907-bbf1-e0562cea155d | textbox | Project Address:
71a86034-b956-5203-b873-8d6f798b33ad | textbox | QA Platforms used:
d76c3f2b-8320-5708-a9da-38fbd066c69d | checkpoint | In house, FER & Specification Numbers
62d9c92d-c1ab-5446-89b1-bf80cbc0d1a4 | date | DATE:
087bf1f2-2a91-5ac0-811b-92888709522d | checkpoint | Site visit & survey
9d598589-23f2-5739-abd1-38084d2be5a8 | date | DATE:
f40bf70e-7c03-562e-9e73-8fbcd929c861 | checkpoint | Review Drawings & print for site
767f52ec-aec3-5775-a064-7229f459323b | date | DATE:
86a71627-b83a-5fe5-827a-1173c7cec5b0 | checkpoint | Review Fire Engineering Report
0d7909f1-54e9-5c90-92e6-074eee42c7aa | date | DATE:
eb035cf3-e47b-505b-b522-f71e191c12e9 | checkpoint | Allocate labour
0a895642-a262-5e46-a17d-2bd265707331 | date | DATE:
dae330e6-ef9c-57c6-9197-103abfd54f8e | checkpoint | Review Principle Contractors (PC) proposed baseline program
1692f978-f249-5f30-958a-396ff70c258b | date | DATE:
a55f05f2-ebad-534b-8cbf-1758e22f0184 | checkpoint | Create Fire Services Proposed Programme
07f60850-c8ec-5c07-8cb3-4760f7a199c5 | date | DATE:
7a356f7b-71e1-5c53-87a9-49ac25d117b8 | checkpoint | Upload to ALL necessary QA platforms
b5b18c80-8662-5430-9ca2-81c6feb62800 | date | DATE:
e81b739e-4825-5367-841f-3db753c333bf | checkpoint | Save softcopy in GM Dropbox
c65d94ba-f3ef-5124-bde6-1efbcc2ca74a | date | DATE:
c2e6bd69-c405-5afe-b004-c8b107fec18d | checkpoint | All employees have attended Induction
f2578d06-522d-52c8-91f5-609e406fe43b | date | DATE:
2630ff26-4768-5012-85c8-d89b8e40b4dc | checkpoint | All SWMS soft copies signed & hard copy printed & filed in the ‘on site’ paper folder
ccf4434e-fcc7-5408-8a54-c9b9b3f5816e | date | DATE:
5674c7a7-848b-557d-a867-52fce0b2bfd9 | checkpoint | PM Signature:
1ec883e5-6967-525b-ae22-80125604b1fd | date | DATE:
c87607a0-8578-5433-aab2-734b6f931e89 | signoff | PM Signature
93daab84-c023-5657-95bc-3c4d78ae4e01 | checklist | CHECK-004 Prestart Plant and Equipment |  | CHECK-004 Prestart Plant and Equipment
8111ace1-1386-5c1f-8290-3df28e3c8d3f | checkpoint | Details
31b7200c-9c32-545e-a38d-96ca20e02fcf | date | Date:
6e63b5fd-dcd8-5332-b402-cad2310988a9 | textbox | Time:
136bb9ee-d728-528e-9cf1-3e309b2c8ae1 | textbox | Location:
eed49114-ac1e-51ec-9995-8e7d2c5cabe7 | textbox | Supervisor Name:
0b454d7c-2ee3-5e46-a2c9-e543b923b322 | checkpoint | Plant or Equipment
524d22de-08e4-5a4c-a4c6-f3b8467aa978 | textbox | What Plant/ Equipment is being used?
71e57a76-5530-5f40-b02a-d07e97532c87 | textbox | Person operating today:
b4e181cb-ff03-5dcb-be8f-ef9b3894114a | button | Is this person competent and licenced (if required)? | Yes, No
7b96a3e9-2ab2-5772-9dfe-029373ef2c7c | button | Is the operator under the influence of alcohol or drugs? (If 'Yes' please explain in comments and find an alternative operator) | Yes, No
a1f10b88-dda2-58f4-ae76-9ea8a476d029 | button | Is the operator tired? (If 'Yes' please explain in comments and find an alternative operator) | Yes, No
446ef14f-eba6-5c7f-a00b-f079abc6d4c3 | button | Have you added this to REGISTER-007 Plant and Equipment (located in Dropbox) for this project? | Yes, No
84ee6adc-bc53-550e-beca-8b791ed391a9 | button | Have all relevant SWMS been completed? | Yes, No
f9910de1-77f1-541c-876c-35b08d530ef7 | checkpoint | Plant and Equipment Checks
533dd4c7-0def-5c25-9d7d-e499fd48f63b | note | As per WHS Regulations 2011, s206 the person with management or control of plant must ensure the plant is used only for the purpose it was designed and ensure that all safety features and warning devices are used in accordance with instruction. Please check the following:
c48c8ee2-5452-5254-a67c-d4c0898533ed | tickbox | Electrical switches, traffic indicators, front and rear lights are working
e3184e6c-0bb4-55a4-b3a6-8bd875f7dbec | tickbox | Guarding is of solid construction, unable to be bypassed or disabled, is appropriately fixed and operates correctly (check latches/ locks and interlocks if fitted)
fc532572-edb9-5662-a509-e49b470e0f3e | tickbox | Engine, fuel and lubricating systems are as per manufacturers specifications
a834e7eb-879c-5bf6-812a-2cbc50c8369d | tickbox | Tyre pressure is as per manufacturers recommendations
76480d2c-0fca-5ea0-b9b9-0aa217639200 | tickbox | There is no risk to the plant colliding with any person or thing (i.e. workers, other vehicles or plant, energised powerlines)
ae41f1e8-9661-53bf-b305-ee4f03036afc | tickbox | There are no mechanical or other failures (e.g. hydraulic failures, release of hazardous substances)
4534011a-5cbd-5ade-9450-fbcd158fca41 | tickbox | Seatbelts are available
b9720857-20b8-5c40-878b-0faad43ceebe | tickbox | There is no damage to switch gear and controls and that controls can be locked off
61e7a480-a4e2-571b-8f1a-460273e491ee | tickbox | Emergency stop controls are marked, accessible and coloured red
34c98e4c-23f9-5a96-b767-f59504b66847 | tickbox | Warning devices are positioned to work effectively
646f749e-a84e-5845-b312-e4d2024321d7 | tickbox | There are no hazards to the operator (e.g. things that could fall on the operator)
0cf670ce-b8fb-50a3-a308-5cb9999170c3 | tickbox | There is no hazard or risk that could caused the plant to overturn
b72fb910-8b05-5bf3-9221-c784ef9ec384 | tickbox | Maintenance and inspections have been carried out
2bcc0a89-8c1f-5fe5-958d-a1f1ba7233a4 | checkpoint | General Notes
d7295a42-11dc-51c1-80d1-cf9ed24c9857 | checkpoint | Operator Signoff
c685b88b-9455-5eaa-8271-b512fa65c130 | signoff | By signing I confirm I have participated in this prestart and understand my duties. I know what PPE I am required to wear whilst operating, the load limits and I am aware that it is my responsibility to leave plant not in use in a state that does not pose risk to others.
cc546369-bca4-51b6-ab24-8e4406ba760e | checkpoint | Supervisor Signoff
411f2708-55c2-5469-af77-82675a4393a8 | signoff | By signing I confirm I have conducted this prestart with the operator (above).
ffce5932-752a-5580-b49c-af4a2b0c3c82 | checklist | CHECK-005 Site EOD |  | CHECK-005 Site EOD
8111ace1-1386-5c1f-8290-3df28e3c8d3f | section | Details
e7f3c29e-5e50-58c0-b5bc-209b95434737 | checkpoint | KPIs
fa4db146-0b35-5308-bcca-ad54bf87eead | textbox | What area did you work on today? Specify level(s)
48a997fd-f8db-5e6b-94d4-7d7992242a07 | tickbox | Detection - In Slab Conduits
96060f36-d2ff-51cb-804f-401c4d3bcb1a | tickbox | Detection - Rough In
a0d35c92-af1b-5de6-a1f7-0583a01280d6 | tickbox | Detection - Fit Off
e6e3c65e-0f4d-5310-b6a7-bfa81c780cee | tickbox | Sprinkler - Rough In
f3225d5c-2711-59b3-b140-a2e1f65f4636 | tickbox | Sprinkler - Fit Off
47cd9acd-a0ee-5458-bd65-52e4cc95d372 | tickbox | Wet Weather Stand down (List names and duration of stand down per person in comments below)
ccad0fff-c7f2-5696-88fd-b2eb321f4a00 | tickbox | Safety Stand Down (List names and duration of stand down per person in comments below)
03ceb4ba-adbb-58db-ac4c-b035e3938005 | tickbox | Industrial Action/ Techs chose to leave site (List names and what time they left in comments below)
d6aa768d-18cb-5397-9287-98d25f058d4d | checkpoint | Productivity
178ea9bc-2a02-57f5-8618-d2fe90b6222f | textbox | In terms of production, did the team meet the site goals today? | Yes, No, Partially
8490b876-e620-54ab-a20e-67374306fe22 | button | If 'No', what hindered the progress? | Time management, Lack of training, Fatigue, Equipment issues, Other
0934a786-5298-5538-937a-b73bb3d574ca | textbox | If 'Other' provide detail:
0da64418-8a08-5008-a58c-e5368b811be6 | checkpoint | Clean Up
255d61c5-d3d5-5b1d-a8b9-34fdbb45d281 | button | Is your work area tidy? | Yes, No
e44f992f-a9a4-5e30-880e-bf854b7f18a9 | button | Have Chemicals used today been returned to secure storage? | Yes, No
b7925325-ecd5-50fa-bcd2-8a8228fb6b76 | button | Have all tools been returned to toolbox? | Yes, No
312d08d3-2c79-5aa0-9ef2-b311eb83ea3e | button | Are all tools (including site iPads) charged and ready for tomorrow? | Yes, No
291034c0-16f4-532b-ad25-0139ec65b5ea | button | Have you completed all necessary QA paperwork for today? | Yes, No
f92a74db-f9aa-57b7-9768-b992adf6a1a8 | button | Are all employees aware of where they are working tomorrow? | Yes, No
9c07c4e6-a41e-5435-8511-0dc72260b2bd | note | If 'No' contact management now
d88fd463-bce2-58bd-b6fa-90986b5a7762 | button | Were there any incidents, injuries or near misses on site today? | Yes, No
6036ce80-824f-5e25-93b5-429ebe0a89ba | note | If 'Yes' complete the necessary reports
42c21dbd-9bff-5051-bd1f-f936237b2320 | checkpoint | Signoff and CLOCK OUT
5d29489d-1335-55db-945d-fe7621bce49f | signoff | This EOD has been completed in consultation with our employees and has been read, understood and signed by all employees on site at the EOD today.
47a05a8f-01d6-5308-b319-09c8bfef63a9 | checklist | CHECK-006 Daily Prestart |  | CHECK-006 Daily Prestart
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
af98ba3f-7105-4c3e-be07-e2ab6454306d | checkpoint | CLOCK IN
c58e65ab-a72b-4fed-85ca-080ec1fa3336 | signoff | Sign here to CLOCK IN to your shift
0b4ad232-5674-51d3-9408-aef0b58a609d | checkpoint | Details:
c67a5ad6-470a-5e2f-997a-f5f60b5e37f6 | date | DATE:
be60c24b-9584-50b3-85e7-c97aac850d9f | textbox | TIME:
5309490c-3518-5494-8898-6b41003721aa | textbox | SUPERVISOR NAME:
694414d8-1e1b-5f09-a0ec-7b8d590ad762 | checkpoint | Issues
29d3d625-f08c-54b1-bf3c-b22dfa3fbd75 | button | Are there any issues arriving from yesterday? If YES, detail in comments below. | Yes,No
88bc1641-daee-577f-b7e3-efc84c9a3236 | note | NOTE: If this requires a change to the SWMS then please ensure this is captured and relevant personnel inducted.
0662f670-ac3d-5439-af86-c1336a2b3861 | checkpoint | PLANNED WORK ACTIVITIES / TASKS
89e3b170-750e-51d8-a682-a426806358d3 | textbox | ACTIVITY / TASK
63009163-b71f-5d74-88ab-182d0339fbec | note | SWMS that relate to today's task/s
3217cd42-d7b4-5c06-8925-f508bd3b2eb4 | tickbox | 001 – Working with elevated work platforms
4e6ff252-595a-527a-99b7-8b0d317de7fb | tickbox | 002 – Wiring Rough In Minor
cd7e73e3-d703-52b7-9d32-c59cb15791e0 | tickbox | 003 – Fit off fire alarm system
b8ad95df-8b35-52b0-9faa-5efb930c096d | tickbox | 006 – Installation of pipe and fittings
2fc333ec-8649-5094-9bac-e7db22722260 | tickbox | 007 – Manual handling
793477a1-ebab-528d-ac0f-4cf5e41a28fa | tickbox | 009 – Pressure testing of pipework
abf682f7-668c-584c-add3-69603f01ffe9 | tickbox | 051 – Using platform ladders
aab532fe-44ab-58ce-84b2-320c641c1eca | tickbox | 060 – Inhalation of Respirable Crystalline Silica
55efd7fe-fc29-5217-af4c-3858f7a3124e | tickbox | 061 – Working in Major Area of Concern
774a66c3-3fea-5200-a769-32e4e0d72e01 | tickbox | Task-specific Safe Work Procedure
23c8da75-1795-5395-a9d2-b738a880bbe9 | checkpoint | Is a SWMS in place for ALL high-risk construction work and work procedures in place for all other works?
018251a3-fdc4-5187-821b-085ee9060fc3 | note | IF NO, STOP AND DEVELOP!
ebf4ce4a-0774-58f0-a144-522ec96b5a15 | checkpoint | Are you subcontracting out any works today and will you be interacting with other trades?
95fe8c17-73e5-5a12-84ab-0e88db6ce7aa | textbox | If YES, please list
279dbae7-8c1f-5553-98d3-d60918e8eade | checkpoint | Permits
ccbee4d0-b0fc-50f9-aba7-187627b00d3a | button | Isolation Permit | Yes, No
e9e5dd68-707a-5644-8f38-af984c59f3e6 | button | Have conditions changed since permit approval? If YES, please note changes below. | Yes, No
498988e2-fa90-543d-abe2-62bbc0b59d3d | button | Hot Works | Yes,No
49f83c80-5eec-5445-acf1-c5c9e01af072 | button | Permit to cut or drill | Yes,No
26129dde-acee-57f3-b54c-c083077e591c | button | MAC Permit | Yes,No
1d20b088-7c9c-5436-8f27-c1ecd33f79fd | note | Please list Permit numbers with description below, and upload photo/ attach file if available.
cae12b06-72bd-55e9-a701-9b47a7fdd5d7 | checkpoint | Environmental Risk
d043a4ae-8752-53fc-bcd7-920e72521388 | note | What controls are in place to manage environmental risk on site, specific for today; e.g. Wash out areas, maintenance of sediment fences and drains, monitoring of dust?
be468b16-df19-537b-854e-46bbd3df7b89 | tickbox | Clean up the general area
03b3f67c-e939-50e1-8cb2-87e19dbe9fd7 | tickbox | M-Class vacuum
054df62a-5657-559a-8159-5ed36c7947b6 | tickbox | Fit test and appropriate fit mask
3640b7ac-10ad-5ec3-ab6e-ae1284393ae1 | tickbox | Spill kit onsite
9bbc93b8-7fb5-5515-8c51-902ff1a50612 | tickbox | Other - detail below
903e1008-c734-5d92-8e65-be1215f53964 | checkpoint | Checklist for Activities
f1e2b79e-aefd-53e7-bcd3-7868bdf06e49 | number | Number of people in your Work Group
57c8c5eb-69d5-5928-bcc8-b3fe0690aa3a | button | Daily Risk Assessment Completed | Yes,No
d198e689-340f-595d-aa6c-5796b9e55eea | button | Qualifications/training of staff adequate for work activities | Yes,No
a89c730d-f0a5-5583-9141-f6861600debc | button | Plant and Equipment on/off site | Yes,No
c2abc099-5048-5862-be7e-69276e515d47 | button | Equipment safe to use | Yes,No
c35b1cc8-2353-5462-9376-b66fbffbe2eb | button | Work area inspected and safe for staff to enter and work in today | Yes,No
446e2139-b3e3-5032-b3b7-4b2ecf6682f2 | button | Appropriate and adequate PPE supplied to work teams (SWMS/SDS) | Yes,No
1297b9fc-83fc-5f03-8c96-a7ef0df8cad5 | button | Weather conditions for work to be conducted assessed | Yes,No
50775e4c-331c-5bcf-9d61-90de79b49eb6 | number | How many workers have been allocated for today’s clean up?
31b028e3-39b4-5b10-96c0-301d4210e7d4 | button | Pre-start communicated to all work teams including all trades & subcontractors | Yes,No
00d26647-1805-5512-8e68-9d14a06237f7 | button | I acknowledge that all Plans on my Dropbox shared file are up to date and I have confirmed this with management | Yes,No
f21451ba-8bea-5c8f-a381-24f716ce840c | checkpoint | Builders Briefing Notes
96ad1a92-eed7-5574-b446-3263c628aa29 | note | Attach a photo of the builders brief
2bcc0a89-8c1f-5fe5-958d-a1f1ba7233a4 | checkpoint | General Notes
3ba7bd2b-c608-4d38-bc56-aac931e41d4c | checkpoint | Mental Health Check-in
cd31bf4e-e2d5-5d58-b35c-fd75f58de3c1 | note | Prior to commencing work, ask your fellow workers: Are You OK?
0c6ae895-4776-5618-ae00-20be5d041a11 | note | Mates in Construction 1300 642 111
bd2c90e5-3cd6-5a5f-aefc-f4f34c1caf48 | note | Beyond Blue 1300 22 4636
3ecf9d4d-a367-5b79-a67e-d473daee966d | note | Gambling Help 1800 858 858
065e825a-d2be-5f52-accd-f30095264611 | note | Drinkwise 1300 858 584
462a3bfd-f982-5f3f-95bf-2a3e5632bbde | note | GM Fire Management 07 3519 7573
42c21dbd-9bff-5051-bd1f-f936237b2320 | checkpoint | Signoff
ad0d0126-8a7e-5cc0-84b3-32f1ee14e2ef | note | Remember to clock in and out of your shift.
2c27aaf3-a648-56ea-92c9-e1e22f200a26 | signoff | By signing I confirm I have have partipicated in this Prestart and I understand my roles and responsibilities today.
72662e0f-5f88-4197-9d0d-90f79a292512 | checklist | Communication (empty) |  | Communication (empty)
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
ef52a7e5-0617-4d05-b97f-e27d1af0ea1e | checkpoint | Communication
10cabfed-b40d-5608-82c0-c2c45f295b84 | note
342882e8-3155-5e74-bb97-9bd09ce24546 | checklist | FORM-001 Tool Box Talks |  | FORM-001 Tool Box Talks
0e50f726-5e25-5b32-be5e-0af50c2a4fbb | checkpoint | Tool Box Talk
e3272aff-5ad7-5584-9f05-601db13efeff | note | Project: YRC WACOL
c4982672-0b0f-5087-ad36-2079a30053d4 | textbox | Tool Box conducted by:
b862c72d-bb88-5890-9585-9eb1d66d73f3 | date | Date:
201ee0d5-9875-55e5-a6b4-cf9a175f45ee | textbox | Attendees:
272ef767-b0f9-5d40-860f-37667165b540 | checkpoint | Electrical tools Tagged & Tested
de358699-2ee1-5f01-a52d-02e78a8f5dcb | note | ACCEPTANCE CRITERIA: Completed Onsite
9031bd57-1d4e-547c-b0ec-b6fb0b1da5db | date | DATE:
605677f5-661a-5bc3-a836-02384d30df5c | checkpoint | Tools checked for wear & tear
d34b0a75-d62c-564d-93ac-a1912bd32f6b | note | ACCEPTANCE CRITERIA: Completed Onsite
8aa8c1f1-8235-59cf-9f29-b950ab07c005 | date | DATE:
acfc8acb-9e64-5733-af2a-b8ca4ea1ea81 | textbox | Items for Discussion:
eabcda0d-be6f-512a-b32a-8bddf5fcbc83 | textbox | Items for Review and discuss at next meeting:
95cb37b4-7a6f-5ffc-99b0-5d11fbc535e8 | signoff | Signatures
fb949add-50c1-5d2e-872b-1fb955255917 | checklist | FORM-002 Tool Box Talk Platform Ladders |  | FORM-002 Tool Box Talk Platform Ladders
106e79f1-1888-598d-99d2-b5a1def7ffd3 | checkpoint | Tool Box Talk - Platform Ladders
887bab57-3216-58e7-9dd5-6974b3a623f9 | note | DO NOT use platform ladder unless you are familiar in its safe use and operation.
ac68153f-7547-5f9f-b14c-f8801309e330 | note | Always complete as much work as possible at ground level before using the ladder.
3271903a-2c15-5d14-ac31-800aa151f93c | note | Make sure the platform ladder is stable before climbing.
5c4a49ee-d931-5509-bdad-bc64c1ca1617 | note | Project: YRC WACOL
00a320e9-986f-593f-bfe8-d25f2931da45 | textbox | Tool Box conducted by:
d0208122-f03a-5610-bde4-6bcb1a760f97 | textbox | Attendees:
da9865ac-d3b6-579f-bb6b-472d8b97b3d7 | date | Date:
fe834967-5fae-5142-ad41-d9de6147f88c | checkpoint | Potential Hazards
3674f2b7-e39a-58bf-b062-1209a407d5a0 | note | The folllowing potential safety hazards and risks have been explained to attendees:
5ea57c24-c9ef-5ac2-aae7-14b6543b15e5 | tickbox | Falls from height
e35ecb4b-a22f-5bcd-833f-fe852d10554a | tickbox | Falling objects
a3d70cbf-4729-5583-aee4-bcf73f29102e | tickbox | Awkward posture
016ab889-7fd8-5c55-95e3-1cf5f8ca44c5 | tickbox | Duration of task
674a0483-b78e-5388-ad6a-db7ac2554b1c | tickbox | Repetition of movement
3f4946f8-8fdd-526a-bb60-7b0d27db4098 | tickbox | Sprains/strains
a6af3874-9657-5afa-ac7b-5c30211f6885 | tickbox | Over-balancing
75d35ab2-1c77-568c-80f3-d9d45ae93ef3 | tickbox | Slip/trip/fall
4a7ce000-11b4-5942-9d59-57beec09de90 | tickbox | Electrical hazards
70790ef5-6074-57a2-b56e-987747b11967 | tickbox | Climbing with loads
1bd92719-b7cf-583c-a096-9b04e390c7ae | checkpoint | Pre-Operational Safety Checks
6ffbd377-bf17-5fba-98aa-8caef52856d1 | note | 1. Familiarise yourself with the safety instructions on the ladder.
a2ea6641-1eb7-56a0-a6e1-7e49d7e16115 | note | 2. Wear slip-resistant footwear. Never wear sandals, high heels or flip-flops. Wear appropriate clothing (e.g. no loose or flapping clothing, or clothing that restricts movement when climbing
aaf65bc0-57d6-5a03-b04a-8610a6416a50 | note | 3. Do not use if affected by a medical condition or medication.
2ba95fdc-b818-55eb-8e98-76f82b92f60b | note | 4. Keep ladder clear of live wires, electrical hazards and ceiling fans.
2c22d256-80a1-5046-8b5e-69ef43b328e9 | note | 5. When transporting your ladder check for overhead power lines, live wires, service cabling or electrical hazards.
93412ad9-195b-58ad-a5cc-688db75dd770 | note | 6. Carefully inspect your ladder to ensure there are no worn parts or damage before climbing:
ffc562ba-2d4e-5c0c-923b-aee111b51e69 | note | • joints between steps and side rails tight, all fittings secure, moving parts operate freely
639c69e6-a3c5-5051-a7d0-e2ca755bc18b | note | • rungs and platform are free of paint splatter, grit, oil and grease, welds are intact, and
5dc33034-ebb6-5e46-8386-62410b6d7321 | note | • all components of ladder intact including side rails, rungs, platform, feet, hand grip.
c1ec81fc-3779-5bbb-99e7-d74bdce4d420 | note | If any component is found to be worn or damaged, rectify any faults before use.
b6eb527a-c4c7-5a69-bb85-a66da835bc7d | checkpoint | Operational Safety Checks
df307b10-6066-5dfe-b2be-ccdabe4b711c | note | 1. Complete as much of the task at ground level as possible.
50ceb36d-3a89-51e0-a79d-8e7534c96b76 | note | 2. Ensure the ladder is placed on dry, firm, level ground/floor. Uneven footing may cause the ladder to rock. If this occurs re-position the ladder until all feet have firm contact with the floor. Always check there is no rocking movement before climbing the ladder.
2b10f449-9e31-58fa-8e70-0fe01b8c3789 | note | 3. If castors are fitted to the ladder, ensure rubber feet have firm contact with the floor when the springs are depressed.
37b91bc5-cb01-56fc-9108-0102c7c4058a | note | 4. Ensure the ladder is fully opened and the spreader bar is locked into position. Check for overhead obstructions before climbing.
7cac46ae-5fc7-5ee4-994f-75dd2980ea6f | note | 5. Only light work is to be undertaken on the ladder. Always face towards the ladder when climbing, and always maintain three points of contact with the ladder. Use a tool bag or tool belt to help to keep hands free.
64f23374-768a-5597-b8a4-9427fc451328 | note | 6. Only one person is permitted on the ladder at any time. A second person may stand alongside the ladder and help to steady it, or pass materials/tools up if required. Do not lift heavy weights that unbalance the ladder.
cea9f832-60c9-5a6a-8373-7c2c02db8309 | note | 7. Never stand or sit on the top cap or use the rails around the top as a step. It is not designed to be used as a tread/seat or step. Always stand in the centre of the platform.
c5338561-5326-55d2-8865-025c5fc7aa76 | note | 8. Do not over reach whilst using the ladder. Maintain the majority of your body weight inside the perimeter of the platform.
6a5bcd9f-5002-5193-afd2-5687e1f860a2 | note | 9. Do not ‘walk’ the ladder while on it. Always get off to shift position.
19c1d6b4-49ea-5f94-9658-6f1b832f0141 | note | 10. Before moving a ladder, take care to ensure that all tools and other items have been removed.
2d257990-358a-561e-bc89-f01924822341 | note | 11. Be mindful of your concentration and fatigue level. Avoid becoming overconfident when using ladders during repetitive tasks.
9d5b0bf0-53b6-5af8-a766-a7d78d594580 | checkpoint | Housekeeping
b7b52c7c-7b6c-5b22-8666-70b57f43c8ee | textbox | Items for Discussion
5c711e95-86eb-5f70-9f58-45404bea1e34 | textbox | Items for Review and discuss at next meeting:
0d24abf6-09a7-54db-913a-af58fcfdb176 | note | All attendees have been made aware they should:
fdb2ffa5-48c5-5b86-a475-b5e212b244b3 | tickbox | Return ladders to secure storage in a clean and in safe working order
ac8f4780-7d87-5234-98fe-0fee60585788 | tickbox | Regularly check ladder feet for excessive wear.
61838543-8502-5082-8baf-f0fa703ab465 | tickbox | Enter any maintenance in an equipment maintenance record
3015ae9e-0d1b-58a3-bfcd-57a87f411d9a | signoff | By signing I confirm I atteneded this ToolBox Talk.
20ef326e-e878-4921-96ea-783ba41928a9 | checklist | ITPS-100 Cast In and Penetration Installations |  | ITPS-100 Cast In and Penetration Installations
6cce4ad3-bd57-4076-949a-c2ff7f8d9c9c | section | Details
8f3694cd-2d94-4a37-a122-6a84cc21ed79 | checkpoint | 1. LOCATION - ENSURE
5d5bd7c3-fbb0-528a-9af4-95e439808eaf | note | CIBSE C5.2.2 Set Points
9314a049-d67d-5798-8705-3a3ecd600891 | button | Is the device setout correct and accurate as per RCP and installation plans? | Yes, No
38365bf7-1521-5905-9571-be813838722b | note | Add Photo
d3f87135-3789-4d33-84a1-4a55a8c6c504 | checkpoint | 2. CONDUIT INSTALLATION - CHECK
e47df4c2-e534-5faa-861f-02a6926deca9 | note | AS1670.1, AS1668.1, AS1670.4 and AS3000
5244b87d-4e09-542a-8399-bd9d33b8f968 | textbox | Drawing Reference and Revision Number:
a7ddf730-1251-5ab9-bcf7-c52ebf293988 | note | CIBSE C5.2.2 Set Points
4c0374b0-a0d5-511e-b560-61eab951ed66 | note | Are Conduits routes are correct as per IFC Drawings?
4a81bb11-3339-510d-81be-2214848ef500 | note | Are Conduits are joined correctly and glued using approved PVC piping and glue?
a47dc7ab-405c-5e62-8ce3-ab5ee9823be4 | button | Are Conduits are tied in properly to prevent movement and damage? | Yes, No
b5634467-065a-5f3c-bb38-e2943a31c917 | note | Add Photo
d478031a-09b2-499b-8aa0-077c842a7511 | checkpoint | 3. SLEEVES AND PENETRATIONS - CHECK
7204864a-f380-5b93-be43-046071f318ef | textbox | Drawing Reference and Revision Number:
4dbcf14a-99b5-58b7-ac1c-c6d8f1e6de79 | note | CIBSE C5.2.2 Set Points
86d181fa-7be6-5d42-9535-b3c685441ee9 | note | Are sleeves the correct type, size and quantity as per penetration drawing?
0a6731da-c8a4-5662-81f3-9ec809819b75 | note | Are sleeves routes correct as per IFC Drawings?
ccb007f7-5ae2-5a11-bfe0-2cfe5283131b | note | Are conduits joined correctly and glued using approved PVC piping and glue?
6ecda3ab-7b45-5531-aa38-346086ea0405 | button | Have sleeves been tied in properly to prevent movement and damage? | Yes, No
8725f7c6-1ff3-50d7-8a99-7742f2600308 | note | Add Photo
2fe6e91a-7d3f-44c2-bf35-73671afdf902 | checkpoint | 4. PRINCIPLE CONTRACTOR - CONFIRM
239a4667-7992-5fa9-86a5-55d2e92cd9db | note | CIBSE C5.2.2 Set Points
458cfb08-9628-5822-bc6c-de9b2706c160 | button | Is the Principle contractor's sign off required prior to pour? | Yes, No
65c73600-eb79-5c03-9052-c77cff0b5046 | note | Add Photo
0370ff29-75fd-40b0-8edd-f25d7a2715c8 | checkpoint-no-value | GM Fire Sign Off
92a462c9-9def-4231-9d33-7cfe609320f8 | signoff | GM Fire Sign Off
f0e91034-79f3-4564-ac37-2feeb8996c31 | checkpoint-no-value | Principal Contractor Sign Off
4c7b71fa-68f6-44c3-a2a3-cbccfe10ea02 | signoff | Principal Contractor Sign Off
2b2455ac-62d2-4645-8729-ac050d2e2e24 | checkpoint-no-value | Consultant Sign Off
225d98a2-ae36-4e7b-8e1f-7c8c78244c74 | signoff | Consultant Sign Off
92b56332-7996-46f7-bdf7-4dc439720850 | checklist | ITPS-101 Fire Alarm and EWIS Rough In |  | ITPS-101 Fire Alarm and EWIS Rough In
3f6578f6-3af4-4b9c-aecf-ccbc97442614 | section | Details
1b38cf8d-046c-44d1-a2a2-dffd687532d3 | checkpoint | 1. CABLE - CHECK
3ea2343e-1cab-5b35-ad42-4301882b958c | note | CIBSE C5.4.0 Wiring
c427396b-ca11-5a9c-954d-1ff5578f4f60 | note | AS1670.1, AS3000
63470cbf-e0e7-5efe-a157-4a4b469d4e9e | note | Is cable installed the correct size and type?
d6ce9c61-5e53-5db0-ac07-fc9c944ffc1a | button | Is cable secured at regular intervals? | Yes, No
5507a789-45e9-55ca-877a-1ee487894e51 | note | Add Photo
cf3aa10c-3551-5c4f-be3a-93ccaa1f5bd5 | button | Have you attached a photo of cable markings for Green Star Compliance? | Yes, No
f76dfc30-2676-53ef-b7d3-b9c1555128b3 | note | If no, stop and attach now
a04e7880-2249-419d-937c-6ecdb66d4450 | checkpoint | 2. FIRE RATED CABLE - CHECK
d3a313b8-feae-52bf-8722-ff8adf4ad400 | note | CIBSE C5.4.0 Wiring
2545cc25-1e8a-5078-8ab1-71499a29aa31 | note | AS3000, AS1760.1, AS3013, AS/CA S009
5f51567c-c7b3-57f7-9400-e68e53c010c4 | note | Have fire rated cables been secured with fire rated fixings at a minimum of every 1200mm?
2801b1fd-f3cb-5d3e-b508-4f2f1d8e75ec | note | Have compliant fire rated cable and fixings have been used for required circuits?
8ba21cb6-444b-597e-9b6c-b147650a4ce7 | button | Are fire rated cables installed as the highest circuit? | Yes, No
239bb46a-cecb-583b-b5d0-82735cefee3c | note | Add Photo
2726d425-ffc3-425d-92a6-7b6bde186582 | checkpoint | 3. CONCEALED SPACE DEVICES - CHECK
80a59c2c-e081-58d9-a982-feefa4b90cd2 | note | CIBSE C5.6.0 Sensors/Detectors
2ae1ca9e-217e-5aaf-b91e-e746be01fee8 | textbox | Drawing Reference and Revision Number:
42f6db56-497e-5370-a6b5-813c923d9ab4 | note | Have all concealed space devices been fit off?
ffa17032-7bd8-5bdb-b21a-0f3ae624c01b | button | Has remote indicator cable been left with adequate length? | Yes, No
cafb6024-5406-5abf-b457-5ef71baf299f | note | Add Photo
c5ea5222-db03-45e9-9b40-c9f91f736387 | checkpoint | 4. ROUGH IN - CHECK
67239dd9-9d98-5238-b317-c7c4a4a4f170 | note | CIBSE C5.2.5 Control Loops
800ab895-30f9-52dd-85eb-4792e8a9fb01 | textbox | Drawing Reference and Revision Number:
ea389c8d-cd7d-5c1f-b690-dd6c21c44960 | note | Have all devices been roughed in?
7cdea458-d18b-5686-9eb2-cd94567962ba | note | Is there adequate length left for fit off?
aed4c939-eb9b-5cf1-bac7-84d7ea4ee772 | note | Are device locations accurate as per the latest RCP?
19c9d689-fed7-5b4a-a24c-f6605f955560 | button | Have circuits been metered for continuity? | Yes, No
fa3116f8-ad2a-5753-89ad-c72769fb3d0b | note | Add Photo
4af7b58e-9239-48bd-b2b7-8b36876b8ba1 | checkpoint | 5. MAG DOOR HOLDERS - CHECK
4a3611f3-757f-54a2-9d87-202d52630d13 | note | C5.2.2 Set Points
111b7acb-8033-5225-b6d5-04a4e4b92840 | note | Have wall noggins have been installed?
a89f3c11-7672-5b86-81a0-841627147ec4 | button | Are cables roughed in to the correct location in wall? | Yes, No
6d5c97e3-a2e0-4e09-b49e-f8abfc78d4fd | checkpoint | 6. SEGREGATION - CHECK
2d410752-a3b4-5800-a274-6b31a4e5d750 | note | C5.2.2 Set Points
d805f318-73d6-57dd-8dda-c800e79a3823 | note | AS3000
f51da073-06d2-52cb-8d0c-285e8d0741eb | note | Is there a Minimum of 25mm from water & gas pipes?
86b3df88-1f4a-52dc-9afc-16011a0915b8 | button | Is there a Minimum 50mm between ELV & LV installation or a physical barrier? | Yes, No
fee87127-6b24-4ac0-863a-600d9fbbb9fd | checkpoint | 7. AS WIRED DRAWINGS - ENSURE
d4bb35e6-1c87-5d04-9a21-1891f37b9e67 | note | C5.4.0 Wiring
f4b08726-1d81-514e-8222-5b48cc15fb46 | textbox | Drawing Reference and Revision Number:
2de1d652-adb9-54e9-b83b-7b6e2e8c016a | note | Are As-wired drawings complete and accurate?
f4a5f54e-126c-53ec-9a9b-d58444e4b0f0 | button | Have photos been uploaded to Dropbox? (as well as below) | Yes, No
b7bf5ce9-e764-574a-98fa-dee9a1585ff8 | note | Add Photo
ed9ae082-03cc-4dfc-8f18-a6634e9beb0e | checkpoint-no-value | GM Fire Sign Off
e1993b3e-feed-40e6-b0ee-b84fc3f1d8d5 | signoff | GM Fire Sign Off
494cb100-06e3-417b-bf5a-3ca28cbc62e3 | checkpoint-no-value | Principal Contractor Sign Off
9eb01c97-4c67-41c3-a85a-b248370d6cdd | signoff | Principal Contractor Sign Off
1946ac31-398d-4a96-b9a0-886d0793c461 | checkpoint-no-value | Consultant Sign Off
60c3ab89-a956-48d7-b2aa-aba7c202b190 | signoff | Consultant Sign Off
c8a72f15-0c73-4359-8caf-9e17ed4d77cc | checklist | ITPS-102 Fire Alarm Fit Off AS1670.1 |  | ITPS-102 Fire Alarm Fit Off AS1670.1
dc945d43-8c95-40a4-b7bf-0f32a176d31c | section | Details
ae5f2caa-8f01-4480-a605-cf57a4e6e04e | checkpoint | 1. DETECTOR TYPE AND LOCATIONS ARE AS PER THE LATEST RCP
e0c60cd0-18df-5180-ba1e-9b2fb2ef8ce1 | note | CIBSE C5.6.0 Sensors/Detectors
cc4bab9d-f0ab-5635-93a0-21e75b3c6d87 | textbox | Drawing Reference and Revision Number:
a39ded39-6640-5e3e-8c05-86b356c1ca13 | note | Add Photo
3a0935e2-b8a7-41b8-b7cc-201a2c227ac4 | checkpoint | 2. DETECTOR ADDRESSES ARE MARKED ON AS BUILT DRAWINGS
b80578fe-d614-5c79-9fc3-5fb7ea5aaf61 | note | CIBSE C5.2.2 Set Points
27eafb00-82c5-5650-bdca-d8eb86cd15b9 | textbox | Drawing Reference and Revision Number:
00cc1611-ff4c-587a-8836-e6437f69a805 | note | Add Photo
fd570cc9-de0d-473a-9e1a-04d83e8f04cd | checkpoint | 3. DETECTORS MAINTAIN MINIMUM CLEARANCES FROM WALLS, PARTITIONS & AIR SUPPLY OPENINGS
0e8cba88-0c7e-5908-ba20-55451e51be0c | note | CIBSE C5.6.0 Sensors/Detectors
3f622b39-a8c7-5447-869e-5eb476c1cd0f | note | As per AS 1670.1 - 2018 - 5.1.4 & 4.1.4;
d0dfb0ca-2525-5d34-9a93-14afbf6b9d19 | note | Is there a minimum of 300mm from walls & partitions?
5f5975da-7727-5a19-986d-8d76985d2bce | button | Is there a minimum of 900mm from air supply openings for smoke detectors & 450mm for heat detectors? | Yes, No
87860d3c-1b06-5d78-8d4c-27897a4c3115 | note | Add Photo
0f527b40-02f7-45c4-a95d-59b78e8a1c7d | checkpoint | 4. DETECTORS MAINTAIN CLEAR SPACE AROUND SAMPLING POINT
ab8580e3-83e6-54d3-8d9b-2f7ee20a49c2 | note | CIBSE C5.6.0 Sensors/Detectors
c37bba88-1637-537c-b1a3-47f35b71cfd5 | note | As per AS1670.1 - 2018 - 3.27.1;
63501e55-9589-547b-b00a-45eee00d92b5 | button | Has a clear space of at least a 300mm radius and 600mm depth been maintained from the sampling point? | Yes, No
1ce1f614-6626-5ed4-a349-7402ba2d2abf | note | Add Photo
f19e13ab-b2b4-48e4-86be-d163b3ac889e | checkpoint | 5. PROTECTIVE CAPS ARE INSTALLED ON ALL DETECTORS
864bcb5c-c8a3-5774-b2c4-2bb288486257 | note | CIBSE C5.6.0 Sensors/Detectors
accfd848-8901-52c0-a5f3-3d62b52db2fb | button | Have dust caps have been installed on detectors to prevent contamination from construction work? | Yes, No
628c8b04-95b1-5510-8125-8e17f2971e46 | note | To be removed once dusty works are complete, or at commissioning.
61de2fcc-d327-50cc-bc7b-d9cb39a548fa | note | Add Photo
651dda02-5afa-429d-8b33-48e65f1f3f67 | checkpoint | 6. MANUAL CALL POINTS INSTALLED AS PER LATEST IFC DRAWING.
42e8fd5d-f452-5585-b6df-e134f83eb8d1 | note | CIBSE C5.10.0 Manual Call Points
99c1715f-cfd3-55fa-bef8-bcfdac7a6a2e | note | Have MCPs been mounted between 750mm & 1200mm above floor level?
9d7760cf-907d-5298-a43c-25be9fc61cb1 | note | Is there a clear space of 300mmm on both sides?
445235cf-4404-5c96-8d04-4eb9d0aa30b9 | button | Is there a 600mm arc directly in front of the MCP? | Yes, No
015238f2-d05c-5036-9f14-3e14edbac03b | note | Add Photo
e471ea2a-02e1-4e04-a952-bf6076f54ffd | checkpoint | 7. MANUAL CALL POINTS SPECIFIC LOCATIONS
b7c8857e-164f-5423-828e-5ec0e6578da8 | note | CIBSE C5.10.0 Manual Call Points
7559b5e9-5d56-56f7-8685-2acc87bf1e6a | note | As per AS 1670.1 - 2018 - 3.14.2;
e4efa169-c7ec-50db-b253-638ad20bddff | button | Is at least one MCP installed in a clear and readily accessible location in the circulation space of the main entrance of the building? | Yes, No
068b963d-6bcf-5b58-8031-8c2926a2852e | note | As per the NCC2022 - S20C4;
71a57d1b-b767-5647-9da3-de43845aaabf | button | If in a Class 9a building, have you ensure MCPs are located in evacuation routes so that no point on the floor is more than 30m from an MCP? | Yes, No, N/A
706c4066-07f6-5571-949b-c3eaf835a192 | note | Add Photo
1cbba782-920b-48f1-9df9-ef59bca0b610 | checkpoint | 8. FTRS
ef200662-0925-5c0a-b589-e9f86b00e74f | note | CIBSE C5.8.0 Modules Input/Output
36cba640-f654-5317-a5b6-80cb1b3dcd97 | note | Have all FTRs been installed in correct locations as per latest drawing?
57d6424a-f229-5441-92df-04698a0fc6bb | button | Have the right quantities been installed to ensure correct operation as per the fire & mechanical matrix? | Yes, No
7e60d47c-4365-53b8-bc0b-742eaf0140ce | note | Add Photo
ef57976c-d466-4e7f-9021-6e6ae873081d | checkpoint | 9. MAGS
dd6af8db-cb2d-56c1-be6a-e3b87571ccb9 | note | CIBSE C5.8.0 Modules Input/Output
2aadd93c-57c3-5f40-aa3b-846914b4505d | note | Have the mag door holders been secured properly to withstand the weight of the door?
994cf403-5ba4-51bb-9103-93f5ad15b561 | note | Have they been installed at a uniform height on each door leaf?
3d38f462-f24e-5d92-99fa-3d365d025bfb | button | Has a release switch been installed? | Yes, No
b254a4dd-edb1-5109-933e-5a7ffd79954b | note | Add Photo
87dde919-c266-43eb-a48f-4d1bda4c45d6 | checkpoint | 10. MASDS
c779a7ef-2f50-536b-9c47-ba31026ab9b2 | note | CIBSE C5.6.0 Sensors/Detectors
daaa5f10-e1da-5774-9def-cd3bba83528b | note | Has all pipework been installed in line with the Aspire calculation & design?
70dd4f78-09de-5af8-ab3c-00c15eb5ff2e | note | Has all pipework been glued?
13b83814-0c47-5e91-89ab-42fe2766cf7b | button | Is the head end unit installed in an appropriate location? | Yes, No
247ab494-30e8-599f-8556-9789b23688de | note | Add Photo
48017515-7811-4c51-ad35-63d2e89081a2 | checkpoint-no-value | GM Fire Sign Off
3d82968d-f92a-4f4c-981b-e39934d626cc | signoff | GM Fire Sign Off
b36b5a43-f11a-4dad-ac78-dbbad18a10b8 | checkpoint-no-value | Principal Contractor Sign Off
c64c8e1c-300a-450f-9d74-36e3713dd7f6 | signoff | Principal Contractor Sign Off
2f136ade-8455-42c3-ba4f-e4377b8a9bab | checkpoint-no-value | Consultant Sign Off
ee732e68-61a1-4625-8fc3-3d41f429e523 | signoff | Consultant Sign Off
1a245bf5-c738-4f9e-b4a2-5a057e2c9ef2 | checklist | ITPS-103 Ewis Fit Off AS 1670.4 |  | ITPS-103 Ewis Fit Off AS 1670.4
b73c9ef9-b412-4a05-9b33-95c01e974d6b | section | Details
61aea83e-e906-451d-b4d2-e8bba898e065 | checkpoint | 1. WIP
bd62a51e-9b70-5633-9118-31833cd61024 | note | CIBSE C6.2.8 Warden Intercom Phones
dc81adb5-6dde-54de-87fd-813592e2e897 | note | Are the Warden Intercom Phones mounted at a height of not less than 1200mm & not more than 1800mm?
a241ad8d-6003-5653-8cf2-7e45cd536253 | button | Is there one WIP per EWIS zone installed within 4m of the exit? | Yes, No
038aba17-17a7-5513-9a25-be4f61721522 | note | Add Photo
b2af2385-2964-4fa7-a7ec-64a05355f845 | checkpoint | 2. SPEAKERS
5c257b36-92fc-512c-bf99-2a25f40e4325 | note | CIBSE C5.2.2 Set Points
890458f3-7b5e-50ab-bdcd-7202e9a1fe73 | textbox | Drawing Reference and Revision Number:
658f3615-fbf9-5a25-ab10-b9f0ce663b55 | button | Have all speakers been installed to the latest RCP? | Yes, No
926a7143-05d0-58d8-a5c1-23fbd50a1c01 | note | Add Photo
ff1525ec-3015-4994-b0af-7e55b3e44056 | checkpoint | 3. STROBES
f9cea430-21e9-5778-94e6-5c46674c1fe0 | note | CIBSE C5.2.2 Set Points
2f35c913-22ea-5faf-bd15-c694a00e4fa5 | note | Have all strobes been installed to the latest RCP?
9b2c8129-bffe-5c8b-8b1d-b58d61038bbc | button | Have all strobes been labelled "EVACUATE" with 25mm lettering? | Yes, No
9d7f9b85-5a60-55a0-93d6-4e0d7bac59eb | note | Add Photo
ee51833b-e30d-4efa-be46-30e291079d87 | checkpoint-no-value | GM Fire Sign Off
e8bb78d3-4c92-4e76-85a7-8f7d89e3f31c | signoff | GM Fire Sign Off
2029fd94-f602-40e3-8403-3c098362ff66 | checkpoint-no-value | Principal Contractor Sign Off
9849285b-052e-48c5-90ce-303f0d91521f | signoff | Principal Contractor Sign Off
8dcf13c4-6fdf-4058-80a1-1d5413dcba19 | checkpoint-no-value | Consultant Sign Off
75c94825-2417-470d-8e09-d02bdda753b6 | signoff | Consultant Sign Off
d6c41e0d-136e-41bb-9fa6-ae53b2513238 | checklist | ITPS-104 Fire Alarm Cable Tray |  | ITPS-104 Fire Alarm Cable Tray
cc2b4a76-4424-496e-bdb9-68048f45fff1 | section | Details
aedd71e3-6543-464f-8a90-0f3494624bef | checkpoint | 1. LOCATION & INSTALLATION
e3c5ed3e-7cd8-59b6-9538-1f218a64e33f | note | CIBSE C5.2.2 Set Points
1475be6f-842a-5814-88eb-18225d3c3f3b | note | Is the tray as per drawings and model?
cf644446-3f20-57f4-9437-e0360236e5ca | note | Have all sharp edges have been removed to prevent injury or damage to cables?
7a79d0b9-162e-53b6-bbdf-0f65a260f0f7 | button | Is the tray supported at intervals of no more than 1m? | Yes, No
6c467741-ddb9-5905-adae-0a74b55b672d | note | Add Photo
7c134b8a-c8a9-4aa6-8802-c9d6ee1d1dfe | checkpoint | 2. FIXINGS AND FITTINGS
2f0f01d5-d622-5689-a22e-6a6f03397f9a | note | CIBSE C5.2.2 Set Points
4060e71e-58e3-5652-91cd-ef381a2ce30a | note | Have the appropriate fixings and fittings been used (for indoor/outdoor use as applicable)?
53f66582-5798-5dab-8bd9-be45c1a1fda6 | button | Are Seismic fixings as per the design documentation? | Yes, No
80f157d6-1807-56de-9211-240e09e95893 | note | Add Photo
b8a6dc99-14aa-4df7-b0a2-c69fe38aa58c | checkpoint | 3. CABLE SPACING
bc819844-fa7b-552d-8e4f-2689e8982d57 | note | CIBSE C5.2.2 Set Points
e14c85d7-6a3c-5dff-99a7-b76f1730157d | note | Generally, where possible install in the following groupings:
465b5a3a-9fbc-5b67-9d53-1e3f9c2cd9c4 | note | Detection Cabling & 24v Cabling
a6b8237b-3ff8-556a-ab7b-8caf8c9566ae | note | EWIS/OWS Cabling
d6a115fb-d998-5684-9ea1-1b976537c998 | note | WIP Cabling
8266f1c5-ac1e-5fb2-b18f-65c8a9e4207a | button | As per AS3000, 3008, and S009, is the segregation of ELV and LV cabling at least 50mm? | Yes, No
a86fd986-62e1-5cc0-ab94-175a255f1137 | note | Add Photo
b4167328-9463-4021-823a-79c7986c3baa | checkpoint | 4. SEISMIC
de8d5a43-b018-5159-ba1c-4792a8612b4a | note | CIBSE C5.2.2 Set Points
5ef8e46f-8a91-50e1-8e37-12a480d04913 | button | Has the cable tray been installed as per the seismic drawings provided? (Use of stablity strut or catenary wire may be required) | Yes, No
5a40cac5-b400-52f7-be2d-d51d69a12579 | note | Add Photo
efe81f7a-0f25-4ff3-a5a2-4f95f3e0cbd2 | checkpoint-no-value | GM Fire Sign Off
59250250-70ab-4549-8a82-bd9ddff30811 | signoff | GM Fire Sign Off
a99ba45b-ab7f-42ad-acc6-1f166fdd124c | checkpoint-no-value | Principal Contractor Sign Off
a5a1dd1b-c348-421f-9602-dcb95856a433 | signoff | Principal Contractor Sign Off
b3010da3-d124-41f1-9034-80f85db95050 | checkpoint-no-value | Consultant Sign Off
5624df8b-0b56-4f21-a163-9f48edf24673 | signoff | Consultant Sign Off
ae9ed3c9-4ed1-4d55-a93b-5451d639a7a5 | checklist | ITPS-105 Fire Indicator and EWIS Panel Installation |  | ITPS-105 Fire Indicator and EWIS Panel Installation
e070462c-d26b-478a-a253-a8a635746e35 | section | Details
2340cb88-e374-4025-ab7b-4eea6348b133 | checkpoint | 1. LOCATION
37234c03-6de7-5582-9b85-cf1b19866210 | note | CIBSE C5.2.2 Set Points
f231f056-d4c4-5625-a94c-ab0fd63d0418 | note | AS1670 (Section 3.9)
bd5b549f-bb91-55a0-8493-d21ef8a700a6 | note | Do you confirm the CIE is:
89c5671d-969b-589b-b482-971a2c65a68d | note | Not in an area used for storage of combustable material; and
be0f482d-05f2-555e-9d9c-f6ede2937dd2 | note | Not obstructing evacuation of the building; and
e36352f0-4b78-53a0-bd7e-f19ba1e885e6 | button | Not in a room containing sprinkler valves, pumps and motors? | Yes, No
7e9bf802-e6be-559b-ba0a-a554dabdf5b4 | note | Add Photo
729eb24a-d732-4b68-a98c-6a4faa9f8e98 | checkpoint | 2. LOCATION
3f85ea7e-0bfc-5e25-a418-fb242d961bda | note | CIBSE C5.2.2 Set Points
d0b197b0-327e-53e2-aef9-1615c291d294 | note | AS1670
7396d072-305b-521c-b938-7d7d09203b82 | note | Has a minimum clearance of 1m in front and 0.5m to each side been maintained?
948ea9bc-a4d5-5a0d-a457-f3a78129c145 | button | Where obstructed by a door, are the words "FIRE PANEL" in contrasting colours? | Yes, No
36270c6c-31df-53be-9036-a21b2d85314a | note | Note - Where the door reduces the sounder, an external sounder may be required.
b312cb8f-014d-5a85-936e-ba2e2083f940 | note | Add Photo
90efa20e-9c9e-4470-bbc2-ffbd7427667a | checkpoint | 3. CONTROLS AND INDICATION
4d8bb18c-b4bd-53db-91c0-b5da7047159d | note | CIBSE C6.6.0 Brigade Interface – FFCP
6ba18911-ee4a-5aff-8112-e584454fcdb8 | note | AS1670 (Section 3.9)
1a68ed6a-b58f-527a-90e5-d2241e308752 | note | Do you confirm CIE has controls that are:
f2645d9b-1bd8-5cfa-9f31-878839676809 | note | Not less than 750mm from floor level; and
c106f90f-8ef5-55c5-a570-bc564d670bb9 | note | Not more than 1850mm from floor level; and
838a5aa1-3a12-5d0b-b2af-58f5dbf08b62 | button | The access to controls is not obstructed? | Yes, No
b3d80f97-66bf-5dd6-8448-f0205e381b71 | note | Add Photo
39828cff-9f85-41f5-8e9e-8b079da3f4fc | checkpoint | 4. CLEARANCE
c8a971d3-dc06-50ed-b58e-65f2481271b9 | note | CIBSE C5.2.2 Set Point
97a02814-2d28-5b10-a5fc-12c37ae0229a | note | AS1670
8113d344-8520-57a2-a719-000fee04b0ac | button | Is there a minimum clearance of 1m in front and 0.5m to each side? | Yes, No
54d7977a-b226-598d-b819-31406db51840 | note | Add Photo
4d7d642a-017b-4c12-b0f8-e1f9cd2f8e61 | checkpoint | 5. EXTERNAL ALARM
5c58000b-d9fa-5883-a73a-1add728740ab | note | CIBSE C5.2.9 Alarm Functions
5eed5a4f-2e2c-5d47-b6aa-0e055a8275e1 | note | AS1670
29314912-d9d2-5e38-aa89-3dad3ea70fda | note | Is an external wall mounted VAD is located on the front façade no more than 10m from the DBEP?
c0f3bb99-7193-5c13-a0d4-327088259783 | button | Is it visible from at least TWO directions, and mounted with the words "FIRE"? | Yes, No
7df62d9d-36f0-5e12-a81b-81e35ae1c646 | note | Add Photo
a21783b3-857a-4d8e-a72f-c76efc077a14 | checkpoint-no-value | GM Fire Sign Off
bcd2dd4a-de08-4c87-a1ad-6a7b58e0f742 | signoff | GM Fire Sign Off
356d6c28-eaf5-4805-88f0-5123d7a932b2 | checkpoint-no-value | Principal Contractor Sign Off
ce886e81-a931-4006-a05d-cd1e2e244d5b | signoff | Principal Contractor Sign Off
49c9e6cd-3dad-4050-aa7e-763392e222c0 | checkpoint-no-value | Consultant Sign Off
04ed76ea-b40a-430a-be71-4209cda67ed2 | signoff | Consultant Sign Off
bc656407-2176-425b-bf59-8eb2dddd9cf9 | checklist | ITPS-106 Sprinkler Pipework Rough In | itp | ITPS-106 Sprinkler Pipework Rough In
52ea9496-a2f6-42e3-8e98-59159d8d4bad | section | Details
44ad7fe4-6297-4eab-a852-840dc4e974e5 | checkpoint | 1. PIPE LOCATION & HEIGHT
daa11cf3-3a90-5e40-ba03-da31719d702a | note | CIBSE W5.2 State of the System
2c0e11c0-ef05-5757-834a-5c89fe7ba3cf | note | AS2118.1-2017-Section 14.14
5ad537fc-8c8a-54ba-a26c-6e01f0a541f6 | textbox | Drawing Reference and Revision Number:
4cf55396-5329-5e50-9a60-d4a14039ef48 | button | Have you reviewed the Fabrication Cut Sheets? | Yes, No
cc510648-af32-5271-bf5d-88eb8d4fed3b | note | Is Pipework setout as per dimensioned install drawing?
72eff916-ffca-5bcf-a96e-2bbd089929d0 | note | Are Pipe heights correct?
35282b36-d82b-5177-a939-12afd39da142 | button | Have Pipework alterations been approved and recorded for as-installed records? | Yes, No
e32391cf-b80a-58c2-8780-807d89759fe5 | note | Add Photo
aa2def14-b7ad-4dbd-8e61-caf7fe9fc49d | checkpoint | 2. PIPE SUPPORTS
7073e04d-d7a5-5cd9-9983-095742537b0c | note | CIBSE W5.2 State of the System
b0e3c797-a7b3-55e6-bbc5-cc74ffe6b42f | note | AS2118.1-2017 - Section 7.8
048a63b0-742a-54e0-97a7-7f3430582ed1 | textbox | Drawing Reference and Revision Number:
865f9d64-4b89-5255-aec2-ea6d521330ec | note | Is the Pipe hanger type as per the install drawing?
2a94541e-5df3-577c-a961-3a6bfe22993b | note | Are Hanger fixings as per the install drawing?
a267dce5-5f1f-52da-bf08-f74d036900c2 | button | Are hangers spaced correctly? (not exceeding minimum spacing) | Yes, No
b33f2e93-bd30-5c78-b250-fe3a8ecb56ba | note | Add Photo
07af32e1-c101-42c6-8851-02146a090d5e | checkpoint | 3. CHECK GROOVES DEPTHS
bc784338-7908-5725-af2f-9923e6fd831b | note | CIBSE W5.2 State of the System
2803ddf5-aee5-54de-8c60-2ef2152f3951 | note | AS2118.1-2017 - Section 7.1
419e9813-43d6-5201-9c60-ff487b1e2da0 | note | Are groove depths within tolerance?
8b1be7d9-0a17-547c-8f77-cdf4efbcb18b | note | Are pipe heights are correct?
cf59cccf-edf6-5209-8f7d-113b57342713 | button | Have any pipework alterations been approved and recorded for as-instaslled records? | Yes, No
4feea553-5488-584a-ac80-dccfcbc2f9c4 | note | Add Photo
350ef3d4-cf80-41eb-bc6b-3c70d69c215d | checkpoint | HOLD POINT
1b874f0b-4135-5b1e-868f-326768ca4505 | button | Confirm Safe to Proceed | Yes, No
c2afa89c-0435-41ca-bf51-8f3745c2e9e2 | signoff | GM Fire Sign Off
f58e691f-5a9c-40ef-8285-306a544a1de0 | checkpoint | 4. VICTUALIC COUPLINGS INSTALLED
e9369a1c-c6b9-595f-a556-8ede5d35e609 | note | AS2118.1-2017 Section 7.10.2.2
c49f8cbb-2ab9-5211-89ce-89ccafdee2c6 | note | CIBSE W5.2 State of the System
acab7220-79e2-5250-97f7-122b8f58a00c | button | Have ONLY Victaulic brand couplings been used? | Yes, No
d185bee0-2eb8-5960-9764-54a1a46da42e | note | Add Photo
8905365f-0a69-4b27-b91b-e9e74e64019f | checkpoint | 5. CONCEALED SPACE SPRINKLER HEADS
91a93816-6c39-5d02-9770-dab5f7244718 | note | CIBSE W5.2 State of the System
0e44a06f-5af0-575c-be05-d1cba8c9541c | textbox | Drawing Reference and Revision Number:
6a539194-0aed-5091-8259-8b57d71b3a8e | note | Have ALL concealed space sprinklers been installed as per dimensioned install drawing?
05d43cb6-0782-5891-9ad1-c44dd1ef1485 | button | Have the correct sprinkler types and temperatures been used? | Yes, No
64a8c335-6b78-5535-ad9c-58fac6210d3b | note | Add Photo
9c9af1bb-c873-43dc-a2ed-99b42f437551 | checkpoint | 6. EXPOSED SPRINKLER HEADS
52101430-9796-5378-9c63-bf5fc0dca855 | note | CIBSE W5.2 State of the System
0be277aa-9c87-5f24-a20e-6c3dd288bb48 | note | AS2118.1-2017 - Section 5
65e45694-628a-5107-993c-af0a7ddbbed6 | textbox | Drawing Reference and Revision Number:
8c31c1b1-7d33-5b73-90bf-a76799849c16 | note | Are exposed sprinkler heads installed as per dimensioned install drawing?
492556fa-d0ca-5683-9aa2-c1d05910ad10 | note | Are sprinklers clear of obstructions?
d67fe8bb-0295-5a2c-937e-6dd34a892736 | note | Have the correct sprinkler types and temperatures been used?
bc65bd18-c491-5f8b-9957-08d3438620a3 | note | Confirm sprinklers do not exceed the maximum distance from the soffit?
c7c1bcd3-2fe6-5bf7-8dec-52534aa9f1b4 | button | Have sprinkler guards been fitted where risk of damage exists? | Yes, No
be0c330b-459d-5f0c-8a64-b2ac0076aaf1 | note | Add Photo
3ba50e2e-a217-425d-9d5b-532e264c9df5 | checkpoint | 7. FLEXIBLE DROPPERS
c55e11ce-4dfc-5618-958e-e91f6713ef15 | note | CIBSE W5.2 State of the System
e61753d6-f352-50c6-9cd4-c8f59e7b14f7 | note | AS2118.1-2017 – Section 7.6
011f95fc-fc5c-58a3-80f6-269266c5cda9 | textbox | Drawing Reference and Revision Number:
1c588d9c-9798-5855-9ad6-43420d98ce25 | note | Is flexible dropper installed in correct location?
61151a84-29a2-5eb5-a993-4d5055bb6404 | note | Correct sprinkler type and temperature?
26998a5a-d134-5109-82c4-c7e3dd724912 | button | Is there sufficient length to reach on-ceiling location? | Yes, No
7f015bd6-b860-511c-b815-f1cba39a6285 | note | Add Photo
acc47723-9c99-421c-a7d0-781c3520f48b | checkpoint | 8. SPRINKLER INTERFACES - VALVES, & MONITOR SWITCHES
8a71a0cd-ecf0-5ba2-b486-883aa93f458c | note | CIBSE W5.2 State of the System
32a6bd7a-a922-5ffb-a180-17430389a5e2 | note | AS2118.1-2017 – Section 8.13.5
2af41709-1990-57f2-a4f6-4a299c417eab | textbox | Drawing Reference and Revision Number:
54518fa8-6329-5651-b84b-748275d9dbdc | note | Have Isolate valves & flow switches been installed?
d67262b0-ae80-52a6-bd0d-4553e6587427 | button | Have labels been installed? | Yes, No
7e485fa8-c68e-5bad-bc50-5d8632899438 | note | Add Photo
2ed75e3c-0929-4842-b1e4-57b5356a2439 | checkpoint | 9. REMOTE TEST DRAIN
812a3321-47f1-5f5c-b55d-bc0906f5defc | note | CIBSE W5.2 State of the System
9dac2495-cfac-5436-bbe7-8ebad8053232 | note | AS2118.1-2017-Section 8.14
1ae87c4d-e1fa-5460-96f1-8f18209ad5f3 | textbox | Drawing Reference and Revision Number:
9385e3b2-104f-5b65-b899-f77c89590eee | note | Is the Remote test valve installed as per dimensioned install drawing?
e09f79d3-ca01-54ee-a61e-236ca6a726f7 | button | Restricted orifice installed? | Yes, No
d53baecf-076b-54bb-b2a9-1acd7a7f3bb7 | button | Have labels been installed? | Yes, No
f77518ef-c235-5a74-a9f0-afc918b7f31a | note | Add Photo
61944c53-4a04-41d1-992f-faa94145af9d | checkpoint | 10. SEISMIC
8d650e9f-cac4-5830-bb30-a42311729d44 | note | CIBSE W5.2 State of the System
9601e27c-139f-53a6-a246-4b8b8eff14b3 | note | AS1170.4-2007 (R2018), clause 5.4.6 and section 8. AS1170.0-2002, AS5216-2018 & ETAG 001 PART 6, ANNEX 1.
94beaa7d-0d3a-5f08-922c-415d48751b25 | textbox | Drawing Reference and Revision Number:
ab1b7112-5d2a-54e3-8f56-659a0a6631e8 | button | Are Seismic braces installed in accordance with Engineered drawing(s)? | Yes, No
9be48af3-7da6-514d-80d7-5e20d421ece5 | note | Add Photo
f482019d-78e0-5df3-a258-8ae327e72814 | note | CIBSE W5.2 State of the System
de6e63c7-be8b-5aeb-b0aa-8fda58e59b88 | note | AS2118.1-2017 Section 7.9.6
db824f33-6a34-5204-a8e4-b13c5b86090a | note | Has painted pipe been inspected for damage?
44035709-0aad-5c0d-b18a-a801cc22c76a | button | Have Repairs to paint been completed where required? | Yes, No
0196fc94-bf6e-5625-9741-75c3b56d20b8 | note | Add Photo
6ea5e688-6c54-48b5-a149-41826ed589fe | checkpoint-no-value | GM Fire Sign Off
6ee4cd30-5efd-446f-b3ff-8bca5e1f8113 | signoff | GM Fire Sign Off
37378bdd-b5d6-4f31-ab17-30aa2a66e837 | checkpoint-no-value | Principal Contractor Sign Off
c621c36e-bdbc-4606-8e83-5343c545742f | signoff | Principal Contractor Sign Off
36eb9bc4-7f42-4fa1-9b22-8a7411953f34 | checkpoint-no-value | Consultant Sign Off
623d3c40-0a42-4030-843e-0af0fe876144 | signoff | Consultant Sign Off
fe6cf6d2-596a-4e9f-9064-d170d15ced55 | checklist | ITPS-107 Hydrant Pipework Rough In |  | ITPS-107 Hydrant Pipework Rough In
f7db0156-0e7e-4b07-83fd-f5a15c4faae0 | section | Details
9a58ffa9-2b83-4678-8e79-1c054997917e | checkpoint | 1. PIPE LOCATION, HEIGHT & SIZE
b7805126-8514-5366-8b8f-dc7e9fff54f4 | note | CIBSE W5.2 State of the System
c3b8b51f-ebfd-559c-a20f-eabf538c8f68 | note | AS2419-2005 Section 2
25d2b91a-297a-5ab0-a2fb-3f5e94714e97 | textbox | Drawing Reference and Revision Number:
fdac9215-5890-5295-a362-03711486e6f4 | note | Is pipework setout as per dimensioned install drawing?
63b245d2-805f-5603-ab14-25959767d33b | note | Are pipe heights correct?
5545ca59-19a1-55f8-9b40-ccc339d0caa5 | button | Have pipework alterations been approved and recorded for as-installed records? | Yes, No
cd07838a-8ad4-5f48-8721-46efe4639bdd | note | Add Photo
7253f4d4-ec7d-4ed4-985f-b2b11db3ca48 | checkpoint | 2. PIPE HANGERS
163d63c4-48ef-542b-804d-d70fdcfb0b33 | note | CIBSE W5.2 State of the System
66d2fb0f-6b41-51e5-b9fd-540d65180320 | note | AS2419-2005 Section 8.7
64083392-e3dc-5e72-ac01-c0bc12903e53 | textbox | Drawing Reference and Revision Number:
43f0cbfa-e4c8-5d5b-9466-393bb7aa008b | note | Is the Pipe hanger type as per the install drawing?
5a9dc56b-6a68-5bf1-a96d-3da0eac7541a | note | Are Hanger fixings as per the install drawing?
9c3107f8-14a8-5f4e-bdf0-efffe1900c5a | button | Are hangers spaced correctly? (not exceeding minimum spacing) | Yes, No
5ed97c70-b581-514f-ad8b-36723be353ff | note | Add Photo
18768a04-e31e-4b77-baf2-99a71165ba3e | checkpoint | 3. CHECK GROOVES DEPTHS
4dcc9a47-0d6b-59b3-b6d6-513f5aecce02 | note | CIBSE W5.2 State of the System
ffa07371-2f39-5142-ac3a-df5620308dfc | note | AS2419-2005 Section 8
57945456-c051-574e-bf1b-e2f891f8874e | note | Has Victaulic Groove Tape been used?
2563f620-66e5-5b9f-ad7d-3de43b9e9ea8 | note | Are Groove depths are within tolerance?
dae3a87c-7eb9-5f82-9e6a-f7dd85a13852 | note | Are Pipe heights correct?
ed5605f0-e728-53dd-ab6d-36b3468b97db | button | Have Pipework alterations been approved and recorded for as-installed records? | Yes, No
9fcd374b-e03d-5168-b530-eeb3b5e5e732 | note | Add Photo
c1d2a725-fa63-45b2-9831-3e5642d9b9df | checkpoint | HOLD POINT
d320880e-6bd7-5ead-a69e-ca5022c7e043 | button | Confirm Safe to Proceed | Yes, No
b2fd74ea-9be7-463e-931d-fdd1dc97b898 | signoff | GM Fire Sign Off
05605cbe-fac2-4594-ba42-7ac4af12ebe9 | checkpoint | 4. VICTUALIC COUPLINGS INSTALLED
8ea700fb-2688-532e-af94-b8f13e3b4c3a | note | CIBSE W5.2 State of the System
7a7f8c4d-a26b-5bcc-80f1-436fb0b95182 | note | AS2419-2005 Section 8.3.2
5dc1c565-d29b-5c8a-8549-164714e833c2 | button | Are Victaulic brand couplings the only couplings that have been used? | Yes, No
9f5a56de-0113-5f30-9ef6-73ae2ccf5f07 | note | Add Photo
71e79d03-01c3-4a21-845b-791b1fb532d7 | checkpoint | 5. ISOLATION VALVES INSTALLED
6781ba37-adab-5bc6-a164-377c121566b0 | note | CIBSE W5.2 State of the System
d6465538-ece6-52c4-bdb8-86f7e1a7d52d | note | AS2419-2005 Section 8.5.8
dc4d67d2-f893-5749-9631-d117bc90f564 | textbox | Drawing Reference and Revision Number:
d7631f0a-6a62-5fd2-88f6-fd1ffbc279bf | button | Are Isolation valves installed as per install drawing? | Yes, No
c346aa6a-38db-5fc0-81e7-bc797d777e67 | note | Add Photo
bea5551f-bd04-402e-8164-37655f99600e | checkpoint | 6. SEISMIC
4372d234-41eb-524a-b1dc-3d36544a5d5f | note | CIBSE W5.2 State of the System
a62742c6-904d-5e5a-9e92-1fa2a803558c | note | AS1170.4-2007 (R2018), clause 5.4.6 and section 8. AS1170.0-2002, AS5216-2018 & ETAG 001 PART 6, ANNEX 1.
d8de85f5-f8ff-5ed6-a611-acb36790f079 | textbox | Drawing Reference and Revision Number:
a4326c68-8c0a-519e-910c-2bf021d9f821 | button | Are Seismic braces installed in accordance with engineered drawing? | Yes, No
583b76c5-f105-5756-b088-07ccbcb17356 | note | Add Photo
c3dc014b-2a53-43ef-9d44-6434ea1fd708 | checkpoint | 7. CLEARANCES
02748e1f-e2b7-58d7-8b2c-8fdf21e1f988 | note | CIBSE W5.2 State of the System
8338a8a7-2293-5b95-beb3-9a4bd331b74c | note | AS2419.1-2005 – Section 3.2
b0f1d95a-83c4-554f-99d3-b69668945832 | button | Is the Hydrant positioned so it does not obstruct required clearance for egress path? | Yes, No
96cf0c66-ddbf-5154-9e6c-643b5c0996a8 | note | Add Photo
a4afea40-b332-4758-8c02-b2380a5b3aaf | checkpoint | 8. LANDING VALVE FIT OFF (CLEARANCE HEIGHT/ ANGLE)
9be7cec2-a2a4-544f-998e-3fb36e875019 | note | CIBSE W5.2 State of the System
7cab0ce9-d3f2-5ae6-aaf0-eb6f93a10562 | note | AS2419-2005 Section 3.5
f196fa90-e525-582c-b2a6-4ac08ab540ce | note | Have you checked:
0279c4d7-241e-5765-b269-c4708b921ced | note | Landing valve height; and
2ee27162-b143-5b98-804b-96ea5e62ed16 | note | Landing valve is at the correct angle; and
86286408-bb3c-5aca-8113-1938da706e0b | note | Coupling angle and orientation is correct; and
46a49a8a-b7ec-5060-b9d6-46ecb6016bbb | note | Required clearance for the handwheel has been maintained; and
c79caa4f-6d71-51f8-abc7-e63df87f8b74 | button | The required clearance for the nozzle has been maintained? | Yes, No
ab09479e-cd12-5c23-9dba-e2f278148cbf | note | Add Photo
97d55d4d-d768-437a-8a57-80b68ff2018f | checkpoint-no-value | GM Fire Sign Off
073b82d6-41f9-4469-ae8c-e8c14b2e7a3f | signoff | GM Fire Sign Off
fab2da3b-b529-4d39-b83a-2259c6056673 | checkpoint-no-value | Principal Contractor Sign Off
fa694a95-dd68-4f60-bb52-c441929daa4b | signoff | Principal Contractor Sign Off
e1a920fe-49aa-4f48-9c2d-7b5d8386bafb | checkpoint-no-value | Consultant Sign Off
bd467488-bf83-4309-ba20-5b8b739e98d7 | signoff | Consultant Sign Off
5d23e067-de18-4c3d-b223-43397bc5ca3b | checklist | ITPS-108 Sprinkler Fit Off |  | ITPS-108 Sprinkler Fit Off
93c9be2f-9434-48e0-90ec-56bf34978f63 | section | Details
cd62a08a-de7a-4aca-80d9-5343516fee8a | checkpoint | 1. SPRINKLER LOCATION
d79b84b2-4199-5c2a-a587-4f8ca5847f82 | note | CIBSE W5.2 State of the System
2a21061f-85d0-5d23-99c2-77b552d80dec | note | AS2118.1-2017
487f73d9-1c2d-5c73-9034-1cff8e611670 | textbox | Drawing Reference and Revision Number:
fdf4ea11-dbaa-5195-8615-5435e5c6fb12 | note | Is the location as per dimensioned reflected on the ceiling plan/ install plan?
22249cd8-c8a8-5e2c-bda0-e49f8c5cbb94 | note | Are the Sprinkler temperatures and finishes appropriate for the environment?
8338ba18-016f-5803-aba1-8862649f2329 | note | Maximum spacing from walls is not exceeded
1f080300-1fee-5dd2-8a63-238a3fd1a90a | note | Is the wall spacing within requirements?
12e11424-471f-5b00-b7f9-045b0c5e8b9c | button | Is the spacing between sprinklers within requirements? | Yes, No
e001a646-42f5-52b4-b54d-6e1432186e78 | note | Add Photo
61277200-c428-44f0-8cec-cc6350803124 | checkpoint | 2. SOLID SPRINKLER DROPPERS
48c660a8-67d5-5e57-afd4-60dd22ae4800 | note | CIBSE W5.2 State of the System
d538dc6b-3d42-5d04-8a0c-d69c2d2acd5e | note | Is the arm piece supported by hangers?
defc31e5-50d7-5e5e-bce1-2ef4d0636298 | note | Is Dropper square?
55eb1423-d53e-5686-8cf9-7c78b4fe97db | button | Is the finished sprinkler height compliant? | Yes, No
de72c2b9-f957-5dc7-be8d-28721f6d46da | note | Add Photo
f6541102-038c-4992-a2a2-4b4c9ec825a0 | checkpoint | 3. FLEXIBLE SPRINKLER DROPPERS
24b4cd51-2546-520b-b88c-c907dd558e42 | note | CIBSE W5.2 State of the System
0e777663-8b76-5246-b99c-62204c28ce6c | textbox | AS2118.1-2017
3f79106c-f856-5894-9017-07ee28d4c9a0 | note | Has the appropriate lengthed dropper been used?
799b139e-df92-5674-98f7-bdba4fbefbf4 | note | Are Sweeping bends within tolerances?
45b291d0-817b-5d94-981a-c79e6ef359ac | note | Was the correct bracket used to secure nozzle?
20ac20cc-432d-58ed-813a-c2c431efb321 | button | Is the finished height compliant? | Yes, No
1b48abc7-c379-5d2c-84d2-4e54e50a4f14 | note | Add Photo
bc11fba4-7b14-43d1-8ec7-e2090d1d3859 | checkpoint | 4. OBSTRUCTIONS
d849ec0b-9734-5495-8889-dac5b587de8a | note | CIBSE W5.2 State of the System
910f5adc-cc9d-5866-a6bd-02d5e65d1658 | note | AS2118.1-2017
b72d12db-fc3e-5536-a3d0-0addd34f238c | note | Has minimum clearance been maintained for 'On Ceiling' obstructions?
8e22a2ed-f0aa-5971-81e3-9893252993f3 | button | Has minimum clearance from sprinkler been maintained for 'Below Ceiling' obstructions? | Yes, No
8abeb3d5-cb19-5ccf-9600-dfaaae4c9ebb | note | Add Photo
bffdb55f-1021-4f7b-a8f0-e63b0bd8928b | checkpoint | 5. ESCUTCHEON PLATES
5aede374-cc58-52b1-8960-92a7eed7b012 | note | CIBSE W5.2 State of the System
c0d794a3-95f6-546d-8399-4e77f9b58439 | note | AS2118.1-2017
1679042c-242c-53fd-a6d6-892077d401d9 | note | Have outer escutcheon plates been fitted?
bc4e7d9b-b5ca-588f-a480-c4e07a3e2048 | button | Is surrounding ceiling clean? | Yes, No
4d7193ca-97f7-5991-9626-315ea13454fd | note | Add Photo
4791507f-93d9-4b87-9bf8-cac339220db9 | checkpoint-no-value | GM Fire Sign Off
709dd7ef-465c-498a-a156-1f34455f90c2 | signoff | GM Fire Sign Off
732332fd-7218-428f-92d4-709cf9256a13 | checkpoint-no-value | Principal Contractor Sign Off
006fdd74-1606-4604-a9a5-eaa51a7349da | signoff | Principal Contractor Sign Off
fdd8c8f6-9190-43ec-8c79-394f631ba199 | checkpoint-no-value | Consultant Sign Off
f658bc14-a076-408c-a5a3-6a767fc937ea | signoff | Consultant Sign Off
3a358cee-77ac-407c-92fe-76a12853d944 | checklist | ITPS-109 Portables Fit off |  | ITPS-109 Portables Fit off
92e1aadb-af36-4085-bfb9-e0613c667981 | section | Details
48c668c9-8cfe-4aba-a4d6-0dd86edfb1d8 | checkpoint | 1. FIRE EXTINGUISHERS - GENERAL LOCATION
469efcef-b69e-519b-98a5-0356bab1c9ab | note | CIBSE C5.2.2 Set Points
bde79b9a-a824-54b0-9788-4c9b91d3533b | note | AS2444-2001 - Section 3.2 states extinguishers shall not be located in positions where access could present a hazard to the potential user.
0ebfb0db-3a9e-571f-9f8f-557e30a18eea | note | Is each extinguisher located in a conspicuous and readily accessible position?
b317e583-e39a-5940-8009-b42ebc863775 | button | Where practicable, are extinguishers located along normal paths of travel and near exits? | Yes, No
afff15ab-d023-5e44-8d0f-e2835b7d3ab2 | note | Add Photo
c8dae11c-2017-4131-8b7f-ffa743c0d458 | checkpoint | 2. FIRE EXTINGUISHERS - MOUNTING DETAILS
72f7b2a4-6627-5005-8d92-67394e280b85 | note | CIBSE C5.2.2 Set Points
fde73864-2a82-5aa8-949a-f92eb06e1b67 | note | AS2444-2001 - Figure 3.2
7dc49747-c3bc-50e4-a4c6-9a1d5d4d3fec | note | Have Location Signs been installed at a Minimum of 2000mm off the FFL?
188dee98-7cc8-5187-b683-a9c80b346ba8 | note | Are extinguishers installed at a maximum of 1200mm to the top most part of the extinguisher?
9967fc31-508f-5619-bdd5-1ee7eee65c05 | button | Are extinguishers installed at a minimum of 100mm from the FFL to the bottom most part of the extinguisher? | Yes, No
e1b1d529-072e-5c57-9c8e-928b14cc2473 | note | Add Photo
96d87139-cb77-4c8a-8581-4b3e68e3a0c7 | checkpoint | 3. FIRE EXTINGUISHERS - VISABILITY & SIGNAGE
828ade66-1e2b-5d3f-91a6-8b1f93427adf | note | CIBSE C5.2.2 Set Points
477a7d53-7318-5a1b-a6fe-b70341341fc9 | note | AS2444-2001 -Section 3.4
7e679f6d-d674-554b-905f-3340b55c0707 | note | Are extinguishers, or extinguisher location signs, visible from a distance up to 20m in all directions?
318115ef-ad8e-5fb0-ada8-d5d34a9d369a | button | Are the location and type of extinguisher signs installed as required? | Yes, No
94349fc0-5acd-5ab9-81e7-4e3bf344629d | note | Add Photo
8d204104-a7a5-4fe7-9108-e6a13bc15ace | checkpoint | 4. FIRE BLANKETS - GENERAL LOCATION
a9a0a1cb-f2f5-5c27-8d2e-0251d4125870 | note | CIBSE C5.2.2 Set Points
261e0dcc-ea6a-590e-be6d-a362b88792f3 | note | AS2444-2001 - Section 6
4438ab84-977f-5b1b-a077-65178e2a433c | button | Are Fire Blankets installed in a readily accessible position, and not in a location where access could present a hazard to the potential user? | Yes, No
0941ac53-39a0-5fe7-99a0-c225fc83379e | note | Add Photo
c24d57a8-a6dc-40c1-afdb-9ff371b733eb | checkpoint | 5. FIRE BLANKETS - MOUNTING DETAILS
242aff15-4f29-5f89-87f1-14eb87ecc5f2 | note | CIBSE C5.2.2 Set Points
085efbc3-47dd-57e5-a6ff-9adab14bddab | note | AS2444-2001 - Section 6
9076c42a-5575-5fc0-8e71-6d7c8ab23aff | note | Have Fire Blankets been mounted to withstand the loads imposed when removing the fire blanket from its container?
29045e99-892e-564d-933b-f990f8fc82a8 | button | Is there sufficient room so that fire blankets can be quickly removed without impedance from nearby obstructions? | Yes, No
481238b0-36f3-556d-93dd-195b95886c14 | note | Add Photo
9517eee6-ee4a-4b99-a55e-892fefe2e246 | checkpoint | 6. FIRE BLANKETS - SIGNAGE
7df42705-293e-56ba-a5cd-089cc352abed | note | CIBSE C5.2.2 Set Points
50c795a5-63b7-54f6-adfd-57083d34a287 | note | AS2444-2001 - Section 6
db99f0b9-3aa6-53f1-a3c6-2fad00eb247f | note | Are signs located above or adjacent to fire blankets?
db9999d6-36c3-564b-8bcf-aeeb698a612d | button | Are signs 2.0m above floor, or at a height that makes them most apparent to the average person? | Yes, No
9ca615ec-fac4-5461-82b5-ce2831b33a4a | note | Add Photo
7de96a08-9694-4922-9677-74f39728f8a1 | checkpoint-no-value | GM Fire Sign Off
c4c2547e-b0b4-4318-b7ac-4eb211c29a07 | signoff | GM Fire Sign Off
a424e5f2-9011-4f26-a5ae-fa6a23d8a1e2 | checkpoint-no-value | Principal Contractor Sign Off
77a9f7d8-bb1a-4d9b-a3e5-bd0571f90ce8 | signoff | Principal Contractor Sign Off
6ce25386-4efb-4650-90cd-caba08a379f3 | checkpoint-no-value | Consultant Sign Off
d04b5ef4-3517-4ec5-aed5-902456069650 | signoff | Consultant Sign Off
a05d5f5e-7570-47cc-b763-a8d043db61e2 | checklist | ITPS-110 Valve Set Installation & Fit Off |  | ITPS-110 Valve Set Installation & Fit Off
a5ff17a8-4dd1-4281-ab58-dd7cf92a8e02 | section | Details
c4cfb0ad-511b-434e-b0a8-92a343b216fa | checkpoint | 1. UNDERGROUND SUPPLY
5c5ecad9-03f4-5a06-b2aa-2ae2e49c88c7 | note | CIBSE W5.5.2 Flushing Procedure
ff8745cc-c9a1-5148-836b-d5e7e2c56376 | note | AS2118.1-2017 - Section 7.9.7
24fd8843-81c4-51fd-bcc3-babc89cc123c | button | Has all supply pipework has been flushed by a hydraulic contractor? | Yes, No
d57b2d4b-c1a9-5b56-a8d6-9314e26beabc | note | Add Photos
5aaa7b9b-c237-4196-a1e8-21e6d07e41ed | checkpoint | 2. CHECK GROOVES DEPTHS
ca1b5dae-1500-58a9-9139-abe2de1ba3da | note | CIBSE W5.2 State of the System
3c1f59f2-a4fb-5e61-9f3a-722f89b01fad | note | AS2118.1-2017 - SPRINKLERS: Section 7.1 | Yes, No
1de71c1e-4dbd-5cab-bf5c-e2de9b713b15 | note | Has Victaulic Groove Tape been used?
e3dff36c-8151-55f8-87ac-10db33af8599 | note | Are Groove depths are within tolerance?
ef1cdb95-2dbc-5f9b-b3df-690ec6dd3669 | note | Are Pipe heights correct?
52f6062d-606f-525b-8463-d20d47a18c47 | button | Have Pipework alterations been approved and recorded for as-installed records? | Yes, No
3ace5e7b-67fa-5f2d-a544-e3b2823718eb | note | Add Photo
280654d4-2a36-4ca0-9a6a-ae722fd3f163 | checkpoint | HOLD POINT
38be5403-6ee2-5820-9e1a-f1241ecdbf17 | button | Confirm Safe to Proceed | Yes, No
6b750928-d0f8-4e2a-821b-22bc8f93365d | signoff | GM Fire Sign Off
d004ab32-8c17-4b3f-bf11-76c0213cf100 | checkpoint | 3. VICTUALIC COUPLINGS INSTALLED
5193e508-0216-5b86-bf15-e1004d58891c | note | CIBSE W5.2 State of the System
f09f5b1a-38f5-5840-98e3-f4d4499e1ef5 | note | AS2419-2005 Section 8.3.2
fe0d0e97-5b1e-55d6-ada9-ecaee330169c | button | Are Victaulic brand couplings the only couplings that have been used? | Yes, No
ba4ebb0a-10d6-5da8-a1b7-455f6c0dd9a5 | note | Add Photo
a2cc9ffb-60c2-4aaa-a03b-3f12f85d14fe | checkpoint | 4. CONTROL VALVE ASSEMBLY
7e6bb84b-72a4-5c47-b19e-0ca8bc486bbc | note | CIBSE W5.2 State of the System
3abaf1e9-cb4d-59f2-b44a-01d872cf3de2 | note | AS2118.1-2017 - Section 8.1
298e9db4-4b58-5562-8239-52940ef41806 | textbox | Drawing Reference and Revision Number:
c93cbc29-f679-5154-b801-5b2c896483dd | button | Is the assembly is installed as per drawing? | Yes, No
a033dde7-1251-5ed6-ba66-36a3691ca4ef | note | Add Photo
2de25d59-7911-476b-af45-5c35e7184d89 | checkpoint | 5. PIPE SUPPORT
3b9498be-560b-5fd0-9c31-a50b2ba6f8cc | note | CIBSE W5.2 State of the System
207cb535-fb87-578e-9a67-1d197b5ea755 | note | AS2118.1-2017 - Section 7.8
fe93142a-9071-5cb3-8672-4cbaa8d1801b | note | Are pipework supports as per drawing?
51cec614-b370-5d32-85fa-5909c2f2f00a | note | Are the supports capable of supporting assembly weight?
dd812d9b-c618-58c6-b109-5ea3e18d6ded | button | Are the supports capable of withstanding forces during operation? | Yes, No
70032d73-6fb8-5c8b-b22f-7be96d832be3 | note | Add Photo
4df87b9d-39f1-422e-94e7-6e05719ba29f | checkpoint | 6. VALVES
20562a15-eaca-5db8-a7d2-db0a9ca77095 | note | CIBSE W5.6.2 Mechanical Checks: Automatic Control Valves
76cbaa38-4259-5c4d-afa5-cbf7038e5651 | note | AS2118.1-2017 – Section 8
4f4bab77-20be-57cd-8662-65ba12fc79bb | note | Are Valves installed as per drawing?
d1c37f2a-6686-566f-94dc-74cc48c68e96 | note | Are valves are installed in the correct orientation?
79cea958-4d94-507e-ab69-e959d40bd22a | button | Does the clearance allow for manual operation and future maintenance requirements? | Yes, No
9d66c85a-5381-54ee-bae5-2ed2493dc08c | note | Add Photo
80a87a31-f309-45c6-9bef-2d955d56aa76 | checkpoint | 7. INTERFACES
804f98aa-6745-51aa-b84e-79d24dd5267c | note | CIBSE W5.6.2 Mechanical Checks: Automatic Control Valves
2db20823-bf02-54ec-821e-e833fff2021a | note | AS2118.1-2017 – Appendix H
d3b8e6d0-d1b2-565a-a2ea-7e38d079df48 | note | Are valves/switches installed for connection by other trades?
e00166aa-a828-5cb0-9bee-d37fff6f0341 | button | Have clearances been provided for connection? | Yes, No
21d30972-955c-5cf3-a8af-9dea4c65211b | note | Add Photo
5bcede6c-42ec-4991-a705-4e4b2ac8cd3b | checkpoint | 8. PAINT / FINISH
769608c4-a077-53d9-aea7-157212dc8b48 | note | CIBSE W5.2 State of the System
2c21ae0d-d853-5c30-930a-0e08a81bd863 | note | AS2118.1-2017 Section 7.9.6
4b3dcd4c-29fa-5f2c-b333-2ea3fb668586 | note | Are exposed mild steel pipes painted gloss red (unless specified another colour or galvanised pipe)?
249d57d6-2270-5aec-99dc-2eaa3919a524 | button | Have threads been de-hemped and tidied? | Yes, No
76a6f25d-4d5f-5b92-86a5-815022ec8295 | note | Add Photo
7a1e0a29-bad7-5c4a-8d9f-df834b39ec2f | note | Add Photo
6f687353-9c80-4e27-a6ef-12ff950e25cf | checkpoint | 9. SECURING VALVES
5003337d-5da9-520f-ae51-6c2bf3dad736 | note | CIBSE W5.2 State of the System
c5de4837-54f5-5377-a5d1-ac0f1bc423ac | note | AS2118.1-2017 – Section 8
83b6fdc8-dac5-51d3-b475-0459832090a6 | note | Are valves secured by 003 locks?
617d0922-e36b-5546-8a77-50b255e7a028 | button | Have straps and chain been installed? | Yes, No
29dd550a-e1f0-5db6-a81c-44991babbd9f | note | Add Photo
5dba5bf0-1189-479c-bfcb-cd3408bf1a70 | checkpoint | 9. SECURING VALVES
8f7df1eb-a6fa-57b4-8d8a-abb87238a442 | note | CIBSE W5.2 State of the System
625bb292-9551-5db1-9a97-fd9981a1e6c8 | note | AS2118.1-2017 – Section 8
d0ccec0b-b552-5a4b-9800-9b62c812cfff | note | Are valves secured by 003 locks?
ae05bfca-557e-5d4c-94e9-32a40ed6ace3 | button | Have straps and chain been installed? | Yes, No
4b3a21e1-6719-5d2e-9226-3f13c01af87e | note | Add Photo
236f06fb-aec4-48e4-8342-e722a915daf6 | checkpoint | 10. LABELS & SIGNAGE
6e050c80-f9ff-5813-a91a-34413c49e1d5 | note | CIBSE W5.2 State of the System
04aa152b-cbc0-5686-9d9a-9a10adbd0a29 | note | AS2118.1-2017 - Section 3 (3.3.4)
eada2cb1-b7d7-55ed-bce8-74ab7e9dc477 | note | Are Equipment name labels secured?
2a792156-c34e-5a29-be47-1f8fe9310812 | note | Are Valve position labels secured (normally open / normally closed)?
a2c15a3b-bca1-570b-aa9e-8948418c9110 | note | Have "Sprinkler Stop Valve Inside" signs been fixed at the valve set enclosure entry?
0f3e5d55-70dc-5f3b-bc6e-4500340910c8 | button | Has the Sprinkler Block Plan been installed? | Yes, No
c8fb7e08-963c-53d8-9f24-eaf7b1a7990d | note | Add Photo
da66b657-5e4c-463e-a7c0-d49565c7f513 | checkpoint | 11. SPARES
d79d0460-76ba-50c2-827c-89984eff8e34 | note | CIBSE W5.2 State of the System
e946c503-47f5-5ecc-ba2d-f3fc7f50c97c | note | AS2118.1-2017 – Section 6.7
29bffe2e-b1a1-5fcc-92c3-a36376891fb5 | note | Has the correct size sprinkler spares box been installed?
524e2f8c-1975-559a-91f4-ecd8795145d0 | note | Have the correct number of sprinklers been provided?
53dcbf4a-a2e8-5444-8374-493da9b8ebfa | button | Has a sprinkler spanner been provided? | Yes, No
0d49c2c6-f9b5-5aaf-bb68-0dcde278520e | note | Add Photo
a791ad97-5e45-41e9-a09d-ceee5560c133 | checkpoint-no-value | GM Fire Sign Off
e28ca78e-293b-4b47-a92d-fb25d4b35131 | signoff | GM Fire Sign Off
9a5f026e-db15-474b-9238-2f8da25bb6c2 | checkpoint-no-value | Principal Contractor Sign Off
4268f30d-ab34-47e5-aee0-9f55de5f54ac | signoff | Principal Contractor Sign Off
c52133b7-2e37-4909-859d-b4a76c3c721b | checkpoint-no-value | Consultant Sign Off
99b818af-ee21-487e-bd2a-e68157708f73 | signoff | Consultant Sign Off
cfeff147-4fe8-4ae0-b767-213a470fd584 | checklist | ITPS-111 Tank Installation |  | ITPS-111 Tank Installation
61c85003-6e3f-472c-985c-612567bddd7d | section | Details
77851f88-63a6-438f-8178-5faa562e8e93 | checkpoint | 1. LOCATION, CLEARANCE, ELEVATIONS
1c6c1d53-2e4e-51a7-97ec-3f6b5886d22a | note | CIBSE W5.5 Pre - Commissioning
308c3a04-ba8f-5899-9ed2-070875915dfd | note | AS2304 - Water Storage Tanks
84d0ae24-86e5-5a4d-8415-f86023d527e7 | textbox | Drawing Reference and Revision Number:
0c64a47c-a294-54a1-a1a3-bd08d724d7ac | note | Are Structural Elements as per AS2304 – Section 3?
ec5a922c-3bd7-5f4c-819e-b01b804e885e | note | Is the correct Installation drawing onsite?
cb111b57-14d6-54f4-863f-961bb419726b | note | Is Ladder selection and orientation as per the submitted design drawings?
33f9252e-0ca7-51ea-8187-2aa697469dce | note | Is Nozzle selection as per submitted design drawings?
f45fa727-6df5-5b13-ba45-3f56147c39d2 | note | Has the poisition of the Tanks been confirmed with the Principal Contractor onsite?
b85d96d6-c3f6-521b-a506-459c1ac5c5ab | button | Have you check the subcontractors Competencies and Authority to work? | Yes, No
55de3519-0dc9-5093-966f-c5e500d12d4a | note | Add Photo
ed7e28d9-16af-48d5-9286-92480d5f5192 | checkpoint | 2. COMMISSIONING
c4ce1358-e56d-50ab-94e5-fc98b1938a34 | note | CIBSE W7.10 Commissioning Certification
22bd2cb2-05dc-5241-8104-9901438a91b5 | note | AS2304 - Water Storage Tanks
c2ccd13b-0e7c-5399-be34-663815b9af34 | note | RECORD, CHECK, INSPECT
240e0792-1cb5-5a8f-9f58-034d0744e1d6 | note | Structural inspection was complete prior to filling; and
b73725a0-7ae9-58f4-8c47-9794bdef73eb | note | All ladders have been inspected for conformance and clearances and position of tank accessories (AS2304); and
1d880249-063f-58bd-a407-018683eab48d | note | Hydrostatic inspection was performed after tank is filled to maximum capacity; and
159aa23f-5062-5aef-8ecc-9bc3af8906ce | note | Any defects have been recorded; and
7072c3fe-dcdd-5def-9efa-80c5dd4a9c9d | button | Have Certificates and warranty periods been submitted? | Yes, No
2727f936-01d8-54b4-89f7-c244925e6cc5 | note | Add Photo
7564bff2-1aee-463d-be2e-bec03f47139a | checkpoint-no-value | GM Fire Sign Off
e826aabd-c414-4f8b-8096-d59a59a95886 | signoff | GM Fire Sign Off
5071bdde-1c7c-4b4d-b44f-d53e25dd14db | checkpoint-no-value | Principal Contractor Sign Off
1d9f1ad8-3074-4dc8-b5c7-8ecdee7e891d | signoff | Principal Contractor Sign Off
74c0bbd2-3e03-4d99-a00e-8752c0584654 | checkpoint-no-value | Consultant Sign Off
05f3d725-08f0-449e-94e2-9e53f71c683e | signoff | Consultant Sign Off
b0b12e02-3a99-4fa6-84ed-23c98f79bfdc | checklist | ITPS-112 Deluge Rough In and Fit Off |  | ITPS-112 Deluge Rough In and Fit Off
81054a3f-cd50-4789-92e2-5c3f2cb51a31 | section | Details
e0f295a5-8c36-4fbc-ad36-b5d7ca64d721 | checkpoint | 1. LOCATION - VALVESETS
18c857d7-07ca-576b-9a8d-c386632198e8 | note | CIBSE W5.2 State of the System
76e2b728-e9bf-5d42-a7b9-b51a87ad5c60 | note | AS2118.3
07e90109-dcc2-501e-aa26-5044dab55ac9 | textbox | Drawing Reference and Revision Number:
7284876e-84ca-572e-a2d6-223293b2401a | note | CHECK:
eed7297f-7c29-5d0e-829f-a5fe657ced7e | note | Valves located outside building shall be considered protected if the external wall has a FLR of 60/60/60 or be situated at a minimum distance of 10 m from the wall.
3b4d7195-9518-5f79-933a-4be443ff2c7c | note | Valves located inside the building shall be situated at a minimum distance of 10mfrom the perimeter of the protected area.
3d3ae2a6-2aba-5de2-aaac-e7af146fa587 | note | TRANSIT TIME:
2227e5df-d382-5aec-8fff-9e5f20c3ec43 | note | Deluge valves shall be located as close as practicable to the system they are controlling. This will help ensure that the transit time to the most remote zone is no more than 30 s.
5038940a-b399-5a1e-8a51-118cfb5ede6f | note | Add Photo
aab53cbf-b363-42a3-b86e-3b8e9ab65721 | checkpoint | 2. LOCATION- DELUGE HEADS
91acebc5-0518-590a-927a-7c89738adc0b | note | CIBSE W5.2 State of the System
0d6b7eea-5f43-51c2-bdef-bfe46055e937 | textbox | Drawing Reference and Revision Number:
925e613b-44c2-56be-a558-86a36b0d1873 | note | Are Deluge heads located as per dimensioned reflected ceiling plan / install plan?
64ea6177-3629-5200-95ee-5b8afc9bc6b7 | note | Confirm sprinkler temperature and finish are appropriate for environment; and
496b4f0b-34d1-5416-af18-27d27107b6f4 | note | Maximum spacing from walls has not been exceeded; and
5f62ea42-4f55-5fc7-8d7a-9078f9d05af5 | note | Maximum spacing between sprinklers has not been exceeded; and
e30ab75b-5058-59fb-b943-f03f570bbc7a | button | All is as per manufacturers detail and FER? | Yes, No
b23c47bb-8ea6-5928-8032-bcbb47564df4 | note | Add Photo
658eb778-06ca-4aed-874c-903f5cc693f2 | checkpoint | 3. DELUGE HEADS & PIPEWORK
8233b158-b249-59d3-a92c-a777dc5b1a77 | note | CIBSE W5.2 State of the System
1e56f239-6259-57b3-bbc9-c499de7474fd | note | AS2118.3
9ab56a8a-2b2f-5fd7-ad4d-643d25075813 | note | Open sprinklers are be nominally 15 mm or 20 mm diameter, and either upright spray (SSU) or pendent spray (SSP) pattern only.
8e8a3dbd-d261-5f47-927a-9a66f6d2c8f8 | note | Deluge system pipe and fittings not normally filled with water or foam solution shall be hot-dipped galvanized.
4a1f1f54-13b2-529f-883f-ba21f248685e | textbox | Deluge Sprinkler Head Type:
997a5ca8-49e9-5b93-abb2-41d2f0cb963b | note | Add Photo
cc2b34f6-c4d6-4017-bef3-b253ddb0358d | checkpoint | 4. WHERE SPRINKLERS ARE USED AS DETECTORS - SYSTEM PARAMETRES CHECK
6a3b65ff-2ee3-54e6-a171-1ad57109ade3 | note | CIBSE W5.2 State of the System
2294ea9f-c5a3-5a35-8c09-d7d7db721628 | note | AS2118.3 Section 2.9
3ae8d679-ee64-5a60-8537-fee828825b25 | note | Where sprinklers are used as detectors, ensure the piping layout shall be designed to ensure a response time of no more than 20sec after the operation of the most remote sprinkler or manual operation.
8c6ec964-0290-5b73-9ba0-eca1a696457a | note | Manual control shall be located at each deluge valve and at a strategic point/s within each zone.
8362b9a9-c4ad-5110-8bb1-0417ea57ac2e | note | Deluge valve trim shall be in accordance with figures 2 &3 in AS2118.3.
a6340910-1770-57fe-9d05-6da354504d96 | button | Ensure a remote test drain line is installed (close piping deluge systems) | Yes, No
27f4ccf1-a665-5152-9918-3e15c7569e8b | note | Add Photo
b26d59c6-bfab-4dbd-bf28-5302ea699edd | checkpoint | 5. SOLID SPRINKLER DROPPERS
a4e42bb4-9e82-5553-9c0c-f3ca3eae7c1b | note | CIBSE W5.2 State of the System
35d9cef4-110b-50bb-b0c2-4fe930cce38a | note | Is arm piece supported by hangers?
b0c0ab00-7be6-5657-b4a1-73fbc097ae66 | note | Is the dropper square?
f7247c59-8963-5937-9285-5c8d7955a31d | button | Is the finished sprinkler height compliant? | Yes, No
a7c14a9f-e51c-5892-911b-596c556f691d | note | Add Photo
83066c0c-5fd7-4eb7-9664-8af36a507307 | checkpoint | 6. OBSTRUCTIONS
b03d4c3b-93ec-562f-afa3-7cb1c5174e65 | note | CIBSE W5.2 State of the System
5e509ca2-e8d5-5363-9860-bc721d7bb78e | note | Has minimum clearance been maintained for "On Ceiling" Obstructions?
0a5d9f7c-7840-56f5-a726-a2df7bf69903 | button | Has minimum clearance from the Sprinkler been maintained for "Below Ceiling" Obstructions? | Yes, No
c68e7778-c4e7-4b5c-a123-e9e68fd5b36c | checkpoint-no-value | GM Fire Sign Off
90dccb81-c187-4e58-bcb2-a6e774bc7adf | signoff | GM Fire Sign Off
e6d6b207-6de6-4a6e-8820-664e7b83cdbb | checkpoint-no-value | Principal Contractor Sign Off
bac4fc45-1d41-41b9-9654-a3a2db37c39f | signoff | Principal Contractor Sign Off
45f84152-f754-4153-adf0-e5690578cd1e | checkpoint-no-value | Consultant Sign Off
7375026e-c674-4b79-aca4-c5b154d54677 | signoff | Consultant Sign Off
191483b7-c577-439c-a74d-49637afc8808 | checklist | ITPS-113 In Slab Sprinkler Sleeves |  | ITPS-113 In Slab Sprinkler Sleeves
f43d1403-bd90-4f0a-b013-00eaa7f96efc | section | Details
e09d4445-9c50-409c-8435-7aa2f436c539 | checkpoint | 1. TYPE, SIZE, QUANTITY - CHECK
f7a304d8-d903-5907-b71b-567a70dc9d42 | note | CIBSE W5.2 State of the System
42145677-55fb-56e2-b504-01403df2d571 | note | AS2118.1-2017
13646846-e9fb-52de-bda0-fa2564696dd0 | button | Are sleeves the correct size, type and quantity to criteria and specified drawings? | Yes, No
852a7b1a-b2a9-5248-8f4a-88c5b6f2e81f | note | Section 9.5.2
00d727dd-a61a-5dee-8d16-87fd8b9c17e9 | note | Has pipe with a minumum DN 25 been used;
8e7c99c8-6827-56ba-85bc-8278acac810a | button | Or where a pipe supplies a single sprinkler protecting an external balcony, canopy or carport, or supplies a single exposure sprinkler, a minimum of DN 20? | Yes, No
f4169883-9744-58ec-b975-dabf3be3404d | note | Add Photo
149621e2-32d9-45e1-b934-9246f89be5e2 | checkpoint | 2. LOCATION - CHECK
ed50bde7-08f8-57f5-a8c6-621c1c134572 | note | CIBSE W5.2 State of the System
236b8b26-feab-5a64-b94e-ef987bbd7608 | button | Have sleeves been installed as per specified layout and design criteria? | Yes, No
4cfd709b-1af9-50d6-a78a-dcf9893b3e24 | note | Add Photo
6bb0d4aa-1c4a-49fb-9d47-4d881c46c5e1 | checkpoint | 3. INSTALLATION - CHECK
2be4bc6b-23b9-5076-b805-10e5124558dc | note | CIBSE W5.2 State of the System
32a08735-9e92-588a-a982-3ce0404b735e | note | Are sleeves joined correctly and tied in?
c2ce9f77-b546-5ff3-bc9a-7d532204da6f | note | Have sleeves been checked for damaged?
4f468963-b276-5a5b-aa59-50d05e687aaa | button | Have you ensured sleeves are not resting on form work? | Yes, No
6b9d8b4d-4530-5d27-9272-541757398e7e | note | Add Photo
d557c139-27c9-47bc-8a96-cad9625018d3 | checkpoint-no-value | GM Fire Sign Off
2c7fde5a-7264-4da6-90ce-2b9978b3a29d | signoff | GM Fire Sign Off
b32e28cb-28b0-4d6a-b039-2d16c03fe424 | checkpoint-no-value | Principal Contractor Sign Off
b1be3441-17ad-43ef-9e34-82e5a9f2dd3d | signoff | Principal Contractor Sign Off
91435715-3249-4a0d-baaf-c064e855d163 | checkpoint-no-value | Consultant Sign Off
dcd0e66f-4625-4f9f-b54d-35150b59fda0 | signoff | Consultant Sign Off
302ce8ae-416b-44ae-9956-165b82f97d7a | checklist | ITPS-114 ASD Rough In |  | ITPS-114 ASD Rough In
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
301ce4de-3b22-4dce-a04d-6a11d70d79dc | checkpoint | 1. LOCATION
6fa65a68-09fe-5060-ac85-cb759782ed22 | note | C5.2.2 Set Points
ce161d24-a612-5c65-afc5-4502bb0ade24 | note | AS1670.1
5bc7906c-5f04-511e-a168-e87f53c86838 | note | Have you check that the ASD device does not cover an area great than 2000m2?
ed1500bd-f282-5d1d-aa1c-60ed97bf8833 | note | Is the ASD unit in an accessible location with no obstructions?
98acba65-4e0c-5c2e-9b29-e0a01adc3e3c | button | Is the ASD unit free from damage? | Yes, No
fcdd088e-5124-5800-819a-e4ab36ed5634 | note | Add Photo
2b0b7938-d334-4a65-8f47-4fce09527687 | checkpoint | 2. SAMPLING POINTS
7d44a5b6-63e1-5828-97cb-6f0845a97c8e | note | C5.6.0 Sensors/Detectors
7fa4f0c3-935f-5659-8bca-143991662fae | note | AS1670.1
c55bcfda-a688-59fb-ab63-4d4fba632868 | note | Are ASD points unobstructed, unpainted and free of burrs?
93c92f60-3f61-5e9f-8bb3-628eccad1dda | note | Have ASD points been labelled and identified as required?
b01ed9f3-dc1b-5097-a1a2-103f1a273589 | note | Are ASD points installed in accordance with spacings of point type detectors?
dba4225d-9013-5b0b-bf6c-c95284d7a2dc | button | Have you confirmed ASD points are no more than 600mm below ceiling? | Yes, No
0df551a4-107a-563e-b611-e49566186504 | note | Add Photo
00c5bc27-8495-4283-953b-5d790eb5e1e6 | checkpoint | 3. EXHAUST
c0cf56ab-ff79-570a-9818-3fc1690abb63 | note | C5.6.0 Sensors/Detectors
5fcfa6c1-7a12-5407-a64c-0a76fcbd5cb0 | note | AS1670.1
9efd09bc-f50c-5a31-ae78-ee41a5af7c63 | note | If the ASD is mounted outside the protected area and the potential for pressure differentials can occur between the sampled and exhausted air:
9c2af89d-4026-54e1-95af-a5102e516cb3 | button | Are the exhaust outlets returning back to the protected area, or as per system design? | Yes, No, N/A
96e0a5da-9652-58d4-afb3-3fae6fcff62c | note | Add Photo
bb3cdd27-af1b-4b3e-be2a-db4a7c0d4c3e | checkpoint | 4. OTHER INSTALLATION REQUIREMENTS
22da179a-fae4-5528-8aa1-21dcdd2092f3 | note | C5.2.2 Set Points
4ef1208c-da47-5669-b69f-4ef66cb41088 | note | AS3000, AS1670.1, AS3013, AS/CA S009
be07cfa6-cba9-5254-bae0-0062a98e8c50 | note | Are all sampling points AND capillaries red in colour OR have visible red stripes at least 2mm wide at intervals no more than 2m?
690cd884-25cc-51f1-8bc5-b8ccb7c1d7c9 | button | Is the pipe orientated to ensure identification of markings is visible? | Yes, No
5a59f277-8941-56a3-9950-b49b4e0c3967 | note | Add Photo
439bf4fc-3ed1-4e15-b5fc-ac58b85aea88 | checkpoint | 5. CABLING
3095f6fd-b7e8-54ac-949d-86636c7e5808 | note | C5.4.0 Wiring
01430a79-c746-509d-9d6d-4a28a6f57269 | note | AS1670.1, AS3000
10020ec7-2e77-52c4-838a-4944cf9d4983 | note | Is the cable installed the correct size & type?
f5a0dc8b-8f30-5216-b748-c6982b690fe4 | note | Has cable been secured at regular intervals?
b9efd4f2-94a6-5cff-b145-4c63cb049a97 | note | Has 24v cabling been installed where required?
1755f4e0-35f1-56c2-9d3b-68f9a4c6f34e | button | Is the power supply in accordance with AS1670.1 Cl 3.15? | Yes, No
2341a751-35d3-53fc-b488-5858e8ea64e3 | note | Add Photo
972f4453-adab-4f2e-8bc4-4d1e8f3a61d0 | checkpoint | 6. PIPE LAYOUT
fa5c217f-1c27-545a-91f8-ed4be2e5469a | note | C5.2.2 Set Points
302d20e9-4def-573e-b9e5-f831de78c48e | note | AS1670.1
f952d26b-c395-5b9d-94e1-38a286190d8f | textbox | Drawing Reference and Revision Number:
e38e11d4-48ce-56f8-b864-40cc050a4f29 | note | Is the ASD pipework as per Aspires or Calculations?
d98ab9d1-900e-5216-b13f-ab6fa41417f2 | button | Have you confirmed the pipework layout with measurements? | Yes, No
eea8d151-4c1c-5a12-83e2-469fab82f5db | textbox | PROVIDE measurements:
105efcfa-4722-5811-9904-7eeb75385be9 | note | Add Photo
95708427-0952-4309-9871-1b906f20976a | checkpoint-no-value | GM Fire Sign Off
4a4fbbfc-ee67-44ef-b078-bd0f463d16d0 | signoff | GM Fire Sign Off
87d69699-1f3e-4199-9431-bfea03c5d109 | checkpoint-no-value | Principal Contractor Sign Off
05765fa0-d499-458b-8f98-07a02fcb8672 | signoff | Principal Contractor Sign Off
e468e92d-6971-4f14-9f05-e446d358790f | checkpoint-no-value | Consultant Sign Off
569b162a-c8d8-4518-b379-179872db4827 | signoff | Consultant Sign Off
c80f2080-d38c-498f-b223-3e3fbfaf0583 | checklist | ITPS-200 Fire Detection and Alarm Commissioning |  | ITPS-200 Fire Detection and Alarm Commissioning
e3d7bc46-de20-43a3-b0bc-d6639655ad65 | section | Details
c8a199d9-0e7e-4b38-84f7-3182825b14ed | checkpoint | 1. CONDUCT 100% TESTING OF ZONING
b3010eda-ada1-5485-b57d-562095970bc2 | note | CIBSE C5.2 Dry Fire Commissioning – Automatic Controls
e00145a8-e327-510c-b43a-9f0139baee30 | note | CIBSE C5.2.9 Alarm Functions
1280853b-3789-5c7c-bda4-6a539d85ca9d | note | CIBSE C5.6.0 Sensors/Detectors
976c2a7c-4190-584c-aa00-f491ed1c4c66 | note | AS1670.1-2018
587f6e3f-b588-5b6f-96e7-c2d73de3c672 | note | Are Detectors activated when tested?
d81ee4b9-0cb0-5f63-af6a-7127c9e6ac86 | note | Do indicators function correctly on Detectors and FDCI?
9ab740a8-0b5b-5a44-828d-6c495e16e115 | button | Has "GMF-COMRPT-001 Fire Detection Zone Commissioning" been completed? | Yes, No
8625b676-6aa8-5c10-947d-43ab527b6c09 | note | Attach relevant photos and a copy of GMF-COMRPT-001 below:
7985037f-4671-4126-a84a-7f0f48e79d14 | checkpoint | 2. CONDUCT 100% TESTING OF SMOKE AND THERMALS
dbf83b67-182d-5230-bf77-460887fe2317 | note | CIBSE C5.2 Dry Fire Commissioning – Automatic Controls
38c865af-247c-5eba-8f0f-aa7a6c02cde4 | note | CIBSE C5.2.9 Alarm Functions
bbc07c8a-25d2-5007-a776-e5459a22e64f | note | CIBSE C5.6.0 Sensors/Detectors
32fdba80-72ce-5915-8b13-b9cab08b7b40 | note | AS1670.1-2018: Ensure Detectors are activated when tested and correctly indicates on the detectors and at the FDCI
413ce12c-dc79-5aa5-a9f9-039aa703244b | note | Are Detectors activated when tested?
01ec3f06-72ad-5a88-b8c2-4acf5cd251ea | note | Have all dust covers have been removed from detectors?
51845bbc-b7f3-559d-be8b-f98808298075 | note | Do indicators function correctly on Detectors and FDCI?
1009d030-fdcb-5ddb-a985-588d063c20a0 | button | Has "GMF-COMRPT-002 Fire Detection and Alarms (Smokes, Thermals, Duct Probes)" been completed? | Yes, No
ae0ec55b-82f1-51f4-9d9e-7edbe39ad66e | note | Attach relevant photos and a copy of GMF-COMRPT-002 below:
dbfb6fb8-cfea-4c79-b85d-319fefaff816 | checkpoint | 3. CONDUCT 100% TESTING OF MCPS
7c4b3e31-0399-52d1-973d-5f593993c951 | note | C5.2 Dry Fire Commissioning – Automatic Controls
448806e3-15cf-5934-beed-e9e1c750062f | note | C5.2.9 Alarm Functions
edc41c40-dcfb-5786-a9a0-be3a4cf00879 | note | C5.10.0 Manual Call Points
4ad51f0f-39a8-5d9b-9c19-f8b48da64eac | note | AS1670.1-2018
1aad918a-bc07-5358-a922-80ebaa28e3fd | note | Have you checked:
88c2bdaf-9b13-57e5-8e6d-a776c0717831 | note | The correct operation of each manual call point; and
5beef3f9-849f-5062-b9a2-dbb37a56c272 | note | That the activation of manual call points on the same circuit as other actuating devices does not cause existing detector alarm indications to be extinguished; and
0b7409d0-04d6-58ac-8887-d5d5c68e4210 | note | That manual call points are not subjected to alarm dependency; and
1f8f39dc-60e2-5151-898f-1ab9a5437874 | button | Has "GMF-COMRPT-003 Manual Call Points" been completed? | Yes, No
56839b10-cb22-5f2b-b24a-d81ec8dd6722 | note | Attach relevant photos and a copy of GMF-COMRPT-003 below:
8b5462a2-5c77-47f5-b85e-c400ccb8b7e1 | checkpoint | 4. CONDUCT 100% TESTING OF DOOR DEVICES
60107918-74d6-57ea-bdcc-f2ff4519808f | note | C5.2 Dry Fire Commissioning – Automatic Controls
cca80ad0-47ea-5348-8995-758db85b99e0 | note | C5.2.9 Alarm Functions
15d37c82-55cd-5587-9727-ba8d61d265f4 | note | C5.8.0 Modules Input/Output
ed2b17a7-f25b-5da2-9ab3-4e22ac0e17a2 | note | AS1670.1-2018
1fc26cd9-6c65-5d17-8fd0-737483871acc | note | Has the operation of each device/door release been checked after install?
962164fc-0e96-5f6d-a6b3-221adcf0267f | button | Has "GMF-COMRPT-004 M.D.H / Auto Door Commissioning" been completed? | Yes, No
a6cc3434-4537-5260-821a-558c439f15c9 | note | Attach relevant photos and a copy of GMF-COMRPT-004 below:
41d92fec-87bd-48d7-ac05-0df22e7134e9 | checkpoint | 5. CONDUCT 100% TESTING SPEAKERS AND ZONES
f592b00b-7e28-5c5f-b340-f9d5e3c10ff3 | note | C5.2 Dry Fire Commissioning – Automatic Controls
6d4d338f-00a0-5ae8-b1e8-7f5653110f72 | note | C5.2.9 Alarm Functions
a175e3d8-62a3-52d7-aa71-cc291cb3f56c | note | AS1670.4-2018
b8e2a05f-22f4-5c8d-9423-23d67e89e4dd | note | Have the audible signals, visual and tactile signals been checked? (automatic operation)
9576e5ec-4b63-5be9-bc79-6e0830047eb0 | button | Has "GMF-COMRPT-006 Emergency Warning Commissioning" been completed? | Yes, No
f257a094-568b-5162-a2bd-ce274ae75d16 | note | Attach relevant photos and a copy of GMF-COMRPT-006 below:
8ce2ebed-7260-4cca-90e8-35032e803453 | checkpoint | 6. CONDUCT 100% TESTING WARDEN INTERCOM PHONES
15df73ff-1408-5eee-abdc-144f6c2a217d | note | C5.2 Dry Fire Commissioning – Automatic Controls
88114e3a-a181-5a18-b107-737a77cb02e6 | note | C6.2.8 Warden Intercom Phones
1f2072cd-7248-596f-b8ae-afb87210fd1d | note | AS1670.4-2018
49d72edd-8a1b-571a-a52f-479a441871c7 | note | The WIP audible call signal shall have a SPL of not less than 80 dB(A) when measured at a distance of 1 m from the WIP.
32af80b7-ac2c-5af3-a7a9-04b5223e539a | note | The SPL of the WIP handset audible call signal shall also be met when the WIP handset is mounted within a security enclosure.
b6779ac7-423f-5a05-909c-785886c67fd2 | button | Has "GMF-COMRPT-007 Warden Intercom Point" been completed? | Yes, No
e7c12f54-b74e-55c9-a5f0-595159b338e9 | note | Attach relevant photos and a copy of GMF-COMRPT-007 below:
2ff962d1-95bd-45ed-8024-a1f02c328866 | checkpoint | 7. CONDUCT 100% TESTING CASCADE AND EWIS ZONING
63dd8a66-e1e6-518f-b147-bf674ddecbb6 | note | C5.2 Dry Fire Commissioning – Automatic Controls
08a0c0c2-0ed1-5d90-9697-cf41b21ac522 | note | C6.2.5 Cascade Sequence
a6cd3044-1b9a-5d94-96bd-fa6117565f51 | note | AS1670.4-2018
b52ca689-b99d-5583-8726-0f6be6d0ac9f | note | Have the audible signals, visual and tactile signals been checked? (automatic operation)
1238f2c1-9a80-5978-aa67-3cdb7993f5eb | button | Has "GMF-COMRPT-005 Emergency Warning Cascade and Matrix" been completed? | Yes, No
d9282c3a-d4a1-5c39-a3a2-f7eda6196afc | note | Attach relevant photos and a copy of GMF-COMRPT-005 below:
73504873-2294-4b2c-a70a-c5888d5e9d14 | checkpoint | 8. CONDUCT 100% SPEECH INTELLIGABILITY TESTING
124bb6b4-6ea1-593e-8740-9ec0cb13f9f4 | note | C5.2 Dry Fire Commissioning – Automatic Controls
d0967ee9-8591-51f2-8e4d-8f4df7f0d51c | note | C6.2.5 Cascade Sequence
3f26af8f-ed31-53b5-933a-b9f9c4caef73 | note | AS1670.4-2018
0d17a728-da2a-53fc-9113-33594d176501 | note | Have the audible signals, visual and tactile signals been checked? (automatic operation)
603e2b45-7e05-5b03-8234-0ea980777aa1 | button | Has "GMF-COMRPT-008 Speech Intellegability Readings" been completed? | Yes, No
e9201255-1758-518d-bed8-51a0e91adbc8 | note | Attach relevant photos and a copy of GMF-COMRPT-008 below:
2e3f4212-382d-4351-913c-24320ad7e006 | checkpoint-no-value | GM Fire Sign Off
0c71a6e1-00dd-4668-b137-9e304b049a15 | signoff | GM Fire Sign Off
122baa9c-98d7-4dae-a683-715c4e693dc6 | checkpoint-no-value | Principal Contractor Sign Off
d3243c5c-4f17-4740-b247-fcafe6af4c65 | signoff | Principal Contractor Sign Off
f5a57e08-f8ad-4f4b-814b-65628fee64f9 | checkpoint-no-value | Consultant Sign Off
e9e947cb-1bd9-40f7-9e1a-7a4f17185e8e | signoff | Consultant Sign Off
9f22b016-06cc-44cc-805a-5755a599836e | checklist | ITPS-201 Interface Commissioning | itp | ITPS-201 Interface Commissioning
9915b3be-0e3d-4cda-a432-2dc886426ee3 | section | Details
38cf9c21-3019-43ba-9c21-9621aa9ee0ba | checkpoint | 1. CONDUCT FIRE MATRIX TESTING
40bd102c-a3e7-5f64-ab22-6a947e6a1f61 | note | CIBSE C6.2.4 Fire Matrix
498fa96d-dde8-574f-a8ac-aab8077368c8 | note | AS1670.1-2018
362f91b0-aaf3-5aa5-a704-ab57d7a9ed02 | note | The ‘end-to-end’ test should include the activation of associated detection devices to confirm that all required functions operate correctly in accordance with the system interface matrix.
58db238f-6af0-518d-9971-fc5d09531cad | button | Has "GMF-COMRPT-009 Systems Interface Matrix" been completed? | Yes, No
2151908e-6609-5ca3-836f-e694a90084ad | note | Attach a copy of GMF-COMRPT-009 below:
95c20ed3-5bfb-4f56-ab81-a91f863b48b9 | checkpoint | 2. CONDUCT FIRE FAN CONTROL PANEL AND BRIGADE INTERFACE TESTING
ce6ce7b8-8301-5fe3-8dd1-55e14b58f797 | note | CIBSE C6.6.0 Brigade Interface – FFCP
aafdb741-40bd-527c-a817-c9743c886323 | note | AS1670.1-2018 Appendix A
80d8d410-41cd-5bfa-ab56-0637cf74127a | note | Check Fan Control Operation as per Matrix.
ed737a31-bcd0-5619-8156-09f1261265ea | button | Has "GMF-COMRPT-010 Fan Control Matrix Testing" been completed? | Yes, No
4ba636df-87f9-58f6-a4a2-ec18af7239df | button | Has "GMF-COMRPT-011 Fan Control Overrride Controls" been completed? | Yes, No
18bc6286-b179-521b-bfbc-031d5756a129 | note | Attach a copy of GMF-COMRPT-010 and GMF-COMRPT-011 below:
84befc27-4f57-48fd-a31f-2ee7be2b351d | checkpoint | 3. SPRINKLER INTERFACES FITTED OFF
1694c3c0-ed67-55e0-b2e6-24f950ae2f35 | note | CIBSE C5.8.0 Modules Input/Output
8ad227e8-16db-5a89-9e7f-ff67867cff5c | note | CIBSE C5.2.9 Alarm Functions
aaaa844a-e470-59c0-9235-58c6ac40c1aa | note | AS1670.1-2015
67e03542-7190-5bd5-8413-44e244675dfa | note | Prior to any interface testing, have you checked all systems listed in the system interface schedule are complete and operable?
7066b362-c0bc-56bf-9336-0568f798aa33 | note | Have you checked all systems interfaces to the FDAS?
bfe6e191-110a-51bc-9381-019c38f59093 | note | Has "GMF-COMRPT-020 Sprinkler Zone Commissioning" been completed?
20d2bb4d-f865-5d05-b3ef-0711e2862eb0 | button | Has "GMF-COMRPT-021 Pump and Tank Indication" been completed? | Yes, No
96c92af2-f474-54bb-a0fb-8509718a0eda | note | Attach a copy of GMF-COMRPT-020 and GMF-COMRPT-021 below:
db0f9264-6627-4f37-8b84-23393d38cfd8 | checkpoint-no-value | GM Fire Sign Off
722f10e7-3075-4349-9bf0-4b8a9077f757 | signoff | GM Fire Sign Off
ce5e2f84-8777-4c77-976b-2bc8eb9e8319 | checkpoint-no-value | Principal Contractor Sign Off
673660d0-eded-4043-8c9e-2628cd8ff4af | signoff | Principal Contractor Sign Off
f771caa7-51d7-454f-83ef-84dfd6fb0f04 | checkpoint-no-value | Consultant Sign Off
c149992a-a0c0-41fb-9786-419df10208bc | signoff | Consultant Sign Off
7745dbbf-e2ca-489e-afa5-4dd8136f537a | checklist | ITPS-202 ASDS Commissioning |  | ITPS-202 ASDS Commissioning
4fef7ba2-4e44-43b5-9345-5b3f463c75ed | section | Details
9c5443e6-560d-47da-904f-7d56a33bfe72 | checkpoint | 1. VISUAL INSPECTION
67087ca9-1119-5291-91be-4c2a472e838f | note | CIBSE C5.6.0 Sensors/Detectors
113fe462-4362-5e56-bb13-f06742bb3f7e | note | AS1670.1-2018 Appendix A
3038fbf0-28aa-59bf-8508-dd69a4ddb5db | button | Have you visually inspected every sampling point to ensure it is not obstructed? | Yes, No
4b4741f2-06c8-519a-af55-73ec29ff2793 | note | Add Photo
6b1eae3f-01f9-4bd7-a5f1-ebce9221f2b5 | checkpoint | 2. ALARM TESTING AND TRANSPORT TIMES
f1445477-65e4-5163-b3ac-4930be8f1a4e | note | CIBSE C5.6.0 Sensors/Detectors
2502b5de-7528-524b-8717-c2dde85daf4f | note | AS1670.1-2018 Appendix A
5ca6f8b3-14ef-5931-95aa-b038111a1940 | note | CHECK AND RECORD
c301afb1-2188-5359-b562-5176f839a4e7 | textbox | The response of all capillary sampling points using a test medium placed at each sampling point:
04546c62-2444-5270-8b75-3b1f67b2ecd1 | textbox | Measure and record transport time (TT) from the EACH sampling point:
e701f1d2-7596-524a-96c8-efadf9d1af41 | button | Has "GMF-COMRPT-012-ASD Commissioning" been completed? | Yes, No
53d9d8cc-8ddd-5b9d-b48b-d7507c9d4b57 | note | Attach a copy of GMF-COMRPT-012 below:
f7b47c3f-98bf-4f7a-a4a8-d68ee4a73dd6 | checkpoint | 3. OPERATION - ALARM, FAULT AND ISOLATE
936f0e9b-0cbe-5550-a4c2-eaff51271bc1 | note | CIBSE C5.2.9 Alarm Functions
565d0752-722d-593d-872d-8cac52dc492b | note | AS1670.1-2018 Appendix A
dc74731e-6cfe-59d6-9ca9-866dbd6d3ca1 | note | Have you checked:
ace61e8c-7ef9-578d-aa2a-6e9d3a751df6 | note | The operation of remote indication of alarm and fault signalst; and
67edba48-d813-542e-97a2-2ea2b0711db1 | note | The operation of airflow failure indicators; and
5f42a9f4-3770-5492-a810-71317caaa834 | note | The operation of the system failure indicators; and
6615b77d-1b25-5de9-90c6-f3cb795413ac | note | The isolate and reset functions; and
3db6e1a1-0ee0-59c5-ab64-050875f05e58 | button | The fault and alarm test facilities (where provided)? | Yes, No
b423a370-f897-4f09-9578-d8e49606905c | checkpoint | 4. ASD MATRIX (If Applicable) - Including Thershold Testing
956a3654-8f11-5f33-8297-19912cad2419 | note | CIBSE C5.2.9 Alarm Functions
310f43ac-4f1f-5c7b-8d92-802ee0146fcd | note | AS1670.1-2018 Appendix A
5ee58141-1583-5d17-a12a-892cda6c0d3a | button | Has "GMF-COMRPT-013 Double Knock Testing" been completed? | Yes, No
8f3e40fb-426d-5bc9-8067-702528412c76 | note | Attach a copy of GMF-COMRPT-013 below:
1bba08d3-4fe8-4f84-a3bf-6501bdd64c1b | checkpoint-no-value | GM Fire Sign Off
094e9277-6081-403a-85f4-fac8d82869b8 | signoff | GM Fire Sign Off
41a5534c-eca9-4196-bf47-c758b252389e | checkpoint-no-value | Principal Contractor Sign Off
11be37f0-98c1-42b9-bc42-33a0d84aaf19 | signoff | Principal Contractor Sign Off
f6170dba-e177-49c3-9862-30e4c09d393c | checkpoint-no-value | Consultant Sign Off
02ccebdf-f9d2-49f9-a78f-c2f50af1bee7 | signoff | Consultant Sign Off
5c073136-2cfd-44c9-8156-d2501891f071 | checklist | ITPS-203 Pipework Pressure Testing |  | ITPS-203 Pipework Pressure Testing
9a251254-abd1-4b33-8296-9abee28cf2d2 | section | Details
f06b5816-45e5-40e5-a1d4-b4c67aef391d | checkpoint | 1. SCHEDULED TEST IS APPROVED - CONFIRM
8d4bd424-8073-5ca0-9026-db08b1b90064 | note | CIBSE W5.5 Pre - Commissioning
1ce34504-78c8-5178-8471-70bf0cb24948 | note | Have you received Approval for test time and location?
a3aadf31-955d-5a4a-8a6c-957990972613 | button | Has the site been notified? | Yes, No
60242b4b-e978-51cf-b4d6-2eded5e9bfce | note | Add Photo
bef8c2f5-9a98-44fc-a8e4-9776c9ace3b1 | checkpoint | 2. EXCLUSION ZONE - CHECK
04599bb3-57e5-5781-a1b0-a764fed12039 | note | CIBSE W5.6 System Checks
ffaf229e-dfca-51d2-89e7-af03e7ffb84d | note | Has an Exclusion zone been set-up?
617f7e9a-3ad4-5d81-aa0e-31e056c8393d | note | Have you erected appropriate barriers and signage?
61d94625-3065-59c5-921b-65269b6de3da | button | Have all workers/occupants been notified and have they exited the area? | Yes, No
4398ea4b-71a9-5a3f-9771-1f7b77746a38 | note | Add Photo
903f23de-6feb-4637-ad90-16aeee209c91 | checkpoint | 3. VISUAL INSPECTION - CHECK
d31782a2-e147-5333-8c81-c38aacc00fcc | note | CIBSE W5.3 Check before Filling
bbc1871d-f6a5-5347-a252-0a62bac2ad78 | textbox | Drawing Reference and Revision number:
d88f0679-0fee-523a-a50f-fb2fbab2c37c | note | Is Installation complete?
d64c2ec9-d687-5bb6-95ae-d32da5a2c73b | note | Have End Caps been fitted with lockable ball valves? (BLANK END CAPS MUST NOT BE USED)
068f57e3-a4ec-5384-a719-4209f3809360 | button | Are all outlets sealed? | Yes, No
95dfdcf8-d345-5ef1-aa8b-0f115579fc2c | note | Add Photo
3350e986-6996-476e-9dbb-069bd1972c9f | checkpoint | 4. FIT TEST PUMP AND CALIBRATED GAUGE - INSTALL
8a323d69-1639-51e4-9873-9a57eb913958 | note | CIBSE W5.3 Check before Filling
96b6b423-7926-5034-ac01-7bc4e2c583d8 | note | AS2118.1-2017
5c5b5964-d871-511b-98e8-b88b5050f4fc | note | Is the Pump installed in a safe location?
61e0b36d-8be3-56a6-9981-6045ebd42f2d | note | Is the Callibrated gauge in visible location, and accessible to photograph?
e7211b2b-ba7d-5bcc-8864-4d15111b698f | button | Have the Pump and Callibrated gauge been tested? | Yes, No
729db6ab-bc08-5c2d-b919-8f3b30659cea | note | Add Photo
ca03e4d9-506e-48f5-aabc-8407ada43aac | checkpoint | 5. CONDUCT BREATH / LUNG TEST
00c85ce9-09e3-595f-85cf-a024df4a6bd7 | note | CIBSE W5.3 Check before Filling
7852975c-b31a-556d-9e66-3d9b753a27d0 | note | AS2118.1-2017
2426e8ca-97aa-5d01-b95d-87ca7e6a27eb | note | Perform Lung/Breath test where possible;
3590aac0-1f8d-57e5-ac86-9a0945b6ccdd | button | Is the system sealed? | Yes, No
4d80c60e-4f0e-5c9a-af95-f60f875a811b | note | Add Photo
28c361c6-6356-4504-a82d-0f4f9b80743a | checkpoint | 6. FILL SYSTEM - STATIC PRESSURE ONLY (OR AIR PRESSURE)
f38b3146-d9fd-5c64-bbb3-318ce86f2998 | note | CIBSE W5.4 System Filling and Venting
4e7cc020-63e4-5ba7-aaf9-82c801718adc | note | Prime system to towns main pressure OR 300kPa (depending on test);
39565de2-0e30-5073-9b58-56494d11058f | button | Are there any leaks in the test area? | Yes, No
8baaa640-6a32-518b-9b7d-2afe1c841e4e | note | Add Photo
6686a94a-4f87-443d-9ff0-228dcc572502 | checkpoint | 7. START PRESSURE TEST - CHECK
aaea9636-9222-54e8-8aea-9364377672af | note | CIBSE W5.4.1 Pressure Testing
8a89f96e-4572-50e1-8857-874f68145747 | note | Increased pressure to 600kpa start pressure;
8a4c6678-777e-5a7f-9d81-d4ae813a5e22 | button | Are there any leaks in the test area? | Yes, No
9427c58d-f690-5099-9c95-c532c8113391 | note | Add Photo
1c239eb8-62b3-4712-8bc8-940297e86c83 | checkpoint | 8. INCREASE PRESSURE
3bb1da06-4d75-576b-88bd-2dcb1ad99f54 | note | CIBSE W5.4.1 Pressure Testing
85558429-670c-503b-a4a2-ec80bf888ad7 | note | Progressively increase pressure in 100kPa incraments; and
5b1c82d4-31e3-537e-bdfe-8703be1a4643 | note | Inpect test area for leaks at each increase; and
578fa24b-bd15-52bd-85f2-18120cd2d07b | note | Repeat until pressure reaches 1600kPa;
7f3f239a-d65f-5006-b315-6541dfc67281 | button | Were there any leaks in the test area? | Yes, No
772b2a01-d869-52e5-9a02-5de06390279d | note | Add Photo
88dcc15d-bc28-458e-b544-c307a82ad091 | checkpoint | 9. HOLD PRESSURE
349e88bd-e7f4-54ce-a844-d8306e0c5f06 | note | CIBSE W5.4.1 Pressure Testing
335e9994-3527-5f82-b581-a7e2af6934ce | textbox | Record Start Time and Photograph Guage:
7de8b81a-a68a-53d2-ba5a-b715a42d32b4 | note | Hold pressure for 120 minutes.
6d274b54-a6ed-5096-adf1-33579c6f6700 | button | Was there any pressure loss? | Yes, No
01568e27-549c-55da-a5ee-d7583a8e527b | textbox | Record Finish Time and Photograph Guage:
b0f2f9c7-ac92-56f5-a236-fbef182c0694 | note | Add Photos
bb235d56-c9b1-4f44-b72c-23b0cfb92804 | checkpoint | 10. DE-PRESSURIZE SYSTEM
184d1ff9-b9a4-510e-92be-b2c3d38afea3 | note | W5.4.1 Pressure Testing
265b46fc-f325-50c9-b1e0-159838333cdd | note | Release test pressure from system.
97ac622c-3772-5406-907d-579aa0c1130b | note | System remains primed with towns main pressure.
865c2fc3-db07-5cb3-8a54-82f49b06a0fc | note | Add Photo
ebb96ef2-8c59-47fd-928c-08adbbf2a13b | checkpoint-no-value | GM Fire Sign Off
8e876c92-9a46-4c02-bbce-a8d727441a67 | signoff | GM Fire Sign Off
176a9883-5b5e-4177-96da-a089994b7c4a | checkpoint-no-value | Principal Contractor Sign Off
bd414725-a1aa-4262-80ba-7f81d7eae333 | signoff | Principal Contractor Sign Off
520fed88-c105-4e3c-b521-8b061893b85e | checkpoint-no-value | Consultant Sign Off
545a65c0-3336-4d53-9d4a-d06b08aaafd6 | signoff | Consultant Sign Off
0e57bead-5512-43c0-9c00-94d314376f3f | checklist | ITPS-204 Electric Fire Pumpset Installation and Commissioning |  | ITPS-204 Electric Fire Pumpset Installation and Commissioning
e1630d90-bb45-4d0a-bac4-3a8e1295ae8e | section | Details
03485932-8526-4076-8938-853cc76b10e9 | checkpoint | 1. CHECK AND CONFIRM - LOCATION
697ea067-2291-5db5-af14-f952299db91a | note | CIBSE W5.2 State of the System
4d2e37a0-cdab-5bcb-827e-350055380401 | note | AS2941.1-2013 – Section 11
6ae3ff46-8be6-5b8f-878c-28d14646f2f5 | button | Has the Installation Pump been installed in a position that is protected from falling debris, and vehicular and mechanical damage? | Yes, No
a15ab15b-07eb-5afe-aa39-2f60f4b42bef | note | Add Photo
de8cf7b0-f059-4aa0-8822-09db02096fde | checkpoint | 2. CHECK AND CONFIRM - CLEARANCE
2924d238-5566-5d14-a24d-54eb0787233a | note | CIBSE W5.2 State of the System
a856ce91-1fb6-5594-a932-36a69b27c605 | note | AS2941.1-2013 – Section 11
79739424-091b-5169-9c04-3d52536741c6 | note | Is there at least 1.0m of clearance around the perimeter of the complete pump setup; and/ or
145d6f71-6dee-50cf-b3f1-b9331c2205a9 | button | for multiple pumpset installations, there is a clearance of atleast 600mm between each of the installed pumps? | Yes, No
92f02873-6e1f-5d15-afb3-e07c1e4ebd81 | note | Add Photo
520d8c82-c1a0-45ea-b9fb-d8c1709944b4 | checkpoint | 3. CHECK AND CONFIRM - ELEVATIONS
f54ee4c4-d1c6-5685-9572-9ea6d58ff5bc | note | CIBSE W5.2 State of the System
b31f3343-c0e1-5e71-96aa-e79ec2e37020 | note | AS2941.1-2013 – Section 11
e991b964-695d-5443-a16c-8225e48fc9ce | note | Have pumpsets been installed with the centre-line of all suction pipes at the same elevation; and/ or
8a0e5715-f65e-5d25-b002-4b0303feb317 | note | if the pumps have been installed at different elevations, the elevated pump is installed on a properly constructed mezzanine floor; and
c27bfbb0-7710-5fd9-80d7-9dd675071b09 | button | with head clearance of minimum 2.1 m to the underside on both levels? | Yes, No
813d2d6c-3941-5e5a-98ab-bbd75ba8c906 | note | Add Photo
0482e3df-ff6b-4179-ab00-a8421cdbebbd | checkpoint | 4. CHECK AND CONFIRM - PLINTH
e0a9277d-19b8-5540-8047-09fabc7757e4 | note | CIBSE W5.2 State of the System
d48fea15-57aa-5db1-9904-0a49a66e6a96 | note | CIBSE W5.6 System Checks
d9b02db9-65c5-5ac3-959e-df625830344d | note | AS2941.1-2013 – Section 11
94f9eb37-7ea8-55a8-800e-2b0316eb8bab | note | Have pumpset baseplates been mounted on concrete plinths with a height not less than 150 mm above the floor?
aa3e1e49-8eaf-55d1-ab4d-b0e25f554262 | button | For fixing purposes, does the concrete plinth extend 150 mm past the edge of the baseplate on all four sides? | Yes, No
f6e33f90-c9e8-53ef-852a-7230d70510fa | note | Add Photo
f4cb0b14-be0e-4117-a8ba-ab577614f759 | checkpoint | 5. PRECOMMISSIONING CHECKLIST - CHECK
8586b7b2-49e8-574e-b7c2-b8d0d61947b8 | note | CIBSE W5.5 Pre - Commissioning
2aeac3d2-edae-5731-9735-b1dbf205d6fe | note | CIBSE W5.4 System Filling and Venting
398e0fa0-b2eb-548c-8d0d-5e2bff2b1218 | note | AS2941.1-2013 – Section 12
4a93d2eb-3182-5f84-bb0d-669faf3f32c5 | note | Have you checked the coupling alignment to ensure that the unit is aligned within the manufacturer’s specified tolerance?
3f7c1173-cbad-58ea-b33c-af5f34ce7bd9 | note | Have you confirmed the direction of rotation?
602f8a43-cfa2-5079-a812-5b279de404b1 | button | Has the battery electrolyte level, and the battery leads and connections been checked? | Yes, No
48f9be51-99d0-5d81-9887-87e4dd1cacb1 | note | Add Photo
2ae374e9-8bc2-4bf8-8370-2b8c6aba4f30 | checkpoint | 6. PRECOMMISSIONING CHECKLIST - ENSURE
c796e7c9-7258-58b8-9ddd-9e28dc485592 | note | CIBSE W5.5 Pre - Commissioning
9bf485e1-3aef-50e2-ad32-f25985cec157 | note | CIBSE W5.4 System Filling and Venting
31664f45-9673-5cd2-b576-006aed9983ff | note | Is the delivery from the pump under test the only supply to the measuring device?
2fd372c1-e893-57b2-bda9-109fd7b23832 | note | Does all flow from the pump passes through the device?
d09fd9ce-d86c-50cd-b18d-6127e22ece84 | note | Is the pump primed and lines are clear; and
350e1508-2e8b-580d-be46-f87df21a7a62 | note | valves are correctly set (open, closed or adjusted to required pressure); and
663c0730-b0b9-550a-8f24-54e169df5453 | button | is water available? | Yes, No
9268a9ff-200d-56b0-8032-62f15f1c1385 | note | Add Photo
2e492c0d-10fb-4fbf-b1c6-41c02289e7a0 | checkpoint | 7. PRECOMMISSIONING CHECKLIST - ISOLATE
386f45ec-f0fc-55c6-8d61-71d847ab3e00 | note | CIBSE W5.3 Check before Filling
b2272a05-1be8-5667-a257-6d0c64758cf7 | note | CIBSE W5.4 System Filling and Venting
567a7fd4-0186-54fe-be1c-47e82296877d | note | AS2941.1-2013 – Section 12
e41690d0-9bea-5f1b-bf48-55e22021cbab | button | Have you isolated all other water supplies to the fire protection systems, such as the automatic pressure maintenance pump and any other compression-ignition engine driven pumps in the system? | Yes, No
743f38c2-daa3-55e2-96a0-6d1939530b8c | note | Add Photo
cd7d22cf-83d2-4ad5-998d-15e3d1707107 | checkpoint | 8. PRECOMMISSIONING CHECKLIST - REPORT
3ad669f0-b1db-5ee8-82d4-ff256c1abe4e | note | CIBSE W5.5 Pre - Commissioning
877f7eab-d5b3-5d72-ac09-818598d44ddf | note | AS2941.1-2013 – Section 12
189a2b2c-19a4-5140-818d-5240dda60a7f | textbox | Pump plate details:
1fd5498c-2276-57d5-b6f3-b93be04803a7 | note | Add Photo
0db5cd59-90a6-4f5e-9e98-0441a58324ab | checkpoint | 9. COMMISSIONING CHECKLIST - RECORD
24dfc587-c9d5-55be-ba18-e064c467bdf3 | note | CIBSE W7.10 Commissioning Certification
f0535636-0a66-5fa0-bb66-8e78b3cb93ff | note | CIBSE W7.2 Flow Rate Measurement Tolerances
f48b67cc-3d35-527c-820d-0f130f879036 | note | AS2941.1-2013 – Section 12
aded069c-7e2a-51f3-8a5f-a7a186942bcb | textbox | What is the pressure in the system at which the pump starts automatically?
40d0795d-1b8f-5e0d-91c8-f4c0d6fb8812 | textbox | Pump shutoff pressure:
2a3c1d86-1856-5e9c-97a4-d016c5f0e304 | textbox | Motor shut off pressure:
d6a17090-3527-593f-b669-404d1ec3ca4e | textbox | Delivery pressure at maximum flow:
f87ec8f5-63f3-5c0e-b833-19bfd07b932a | note | Add Photo
c97e545e-db18-462a-bba5-ba0d4c4014df | checkpoint | 10. COMMISSIONING CHECKLIST - RECORD
c5c50b10-195a-59ec-b5ef-985d2d416e3d | note | CIBSE W7.10 Commissioning Certification
425a4ad8-26f2-5ecd-886e-9158175e0d37 | note | CIBSE W7.5 Preliminary Flow Rate Check
93166a74-9b26-5fec-91a9-76960e7ac048 | note | AS2941.1-2013 – Section 12
b95daa92-0ec6-5947-b2bb-1d5018d24bc2 | textbox | Record the pressure on discharge gauge and motor current at three other flow rates between shutoff and maximum flow, one of which should be at the duty flow rate:
46f3c0aa-cbb4-5b18-b1fa-d432845f6738 | note | Add Photo
54beb0fb-8e88-4329-83c7-bf1897811848 | checkpoint | 11. COMMISSIONING CHECKLIST - RUN AND RECORD
8f611f38-51a0-5c1f-a7b4-436817ff2211 | note | CIBSE W7.10 Commissioning Certification
5026fb19-e26b-5af7-9d87-d2d235375eda | note | CIBSE W5.7 Static Completion Records
023b5c25-a54a-5f2b-b68e-051a843c87c2 | note | AS2941.1-2013 – Section 12
acb4ec1e-9c37-5976-9801-a35fb1356607 | note | DURING OPERATION:
8cc6e1bc-dbba-52a3-bd07-06c9ae5931e9 | note | Have you checked the temperature of the bearings and stuffing box leakage and noted any abnormality?
7e5aae05-7e9b-5d07-a429-dbb2289acd48 | note | Have you checked that all alarms and indicators, both visual and aural, have been activated; and
9b481df1-5ac6-5c2c-a96f-2f3a8bea9944 | button | Alarms and indicators, both visual and aural, revert to normal stand-by status when pump is stopped? | Yes, No
c7974807-07de-54d9-aed1-5bdd76b0d184 | note | Add Photo
339f6696-4670-48bd-a156-c8c04955fb5a | checkpoint | 12. COMMISSIONING CHECKLIST - RUN AND REPORT
bb505ee5-b93b-5550-843c-fa49427dd6bc | note | CIBSE W7.10 Commissioning Certification
9e375c00-00c4-5f71-8533-c7fd5be62da0 | note | AS2941.1-2013 – Section 12
9161ec0a-e551-51a4-bfbd-d131300143db | note | RUN AND REPORT:
bbfef1ae-ecd3-5a51-9eae-702925cfee42 | note | Is the electric pumpset, together with its associated control gear and ancillary equipment, functioning correctly?
0658bdc6-b332-5535-9b31-ae584d45523d | button | Does the pumpset satisfy the intended performance conditions? | Yes, No
2caa95c7-e6d0-55d7-af97-f750b07d2f0b | button | Are there any operational abnormalities? If Yes, detail below. | Yes, No
2987e4cf-2c49-50c7-8e27-d5b9c023f554 | note | Add Photo
dce8b662-763e-4e1d-9dba-7a7c48ac1126 | checkpoint-no-value | GM Fire Sign Off
787d0478-c694-4b14-8d9e-6b6cc626fa5e | signoff | GM Fire Sign Off
a64150e6-a204-4913-b884-5fd74546b22f | checkpoint-no-value | Principal Contractor Sign Off
a3fd66ea-d11a-4573-867b-498cf7371f7f | signoff | Principal Contractor Sign Off
535cc038-91dd-401c-aa7c-b170bc23da94 | checkpoint-no-value | Consultant Sign Off
a2a1358f-f2e6-4839-97d3-29626accfe9d | signoff | Consultant Sign Off
6aa25247-d4e7-495c-b7f7-bbe09a53e0d4 | checklist | ITPS-205 Diesel Fire Pumpset Installation and Commissioning |  | ITPS-205 Diesel Fire Pumpset Installation and Commissioning
01bb393c-207b-403a-bccd-c75750a8e586 | section | Details
39b71a3b-2478-4ba1-a921-563d9b2a7de3 | checkpoint | 1. LOCATION
f1cc6053-c105-5065-82a3-3b3f7aca63b8 | note | CIBSE W5.2 State of the System
a7f11aa0-aa2e-511a-a546-03ddd5f11c0f | note | AS2941.1-2013 – Section 11
e2b16caf-31d7-5538-ba71-b5d20308578f | button | Is the Installation Pump installed in a position that is protected from falling debris, and vehicular and mechanical damage? | Yes, No
53b440e5-3e9b-5a05-a7d8-73532bcbced6 | note | Add Photo
c4cbe03d-7db6-46b1-9215-9a518d581634 | checkpoint | 2. CLEARANCE
b0850926-4d2e-5791-9cf4-15cdd1409e96 | note | CIBSE W5.2 State of the System
23d502c2-1458-5e74-abec-e10625582e2d | note | AS2941.1-2013 – Section 11
3c4289ca-0dac-51b1-a0c8-f59e8e28f669 | note | Is there at least 1.0m of clearance around the perimeter of the complete pump setup; and/ or
fc2188f9-fd21-5561-a8c6-cc5612311de3 | button | for multiple pumpset installations, there is a clearance of atleast 600mm between each of the installed pumps? | Yes, No
797ca03a-766c-5435-84b0-a3fc10ea6f54 | note | Add Photo
d6558c3a-9388-44c3-b8f1-9f596289fb21 | checkpoint | 3. ELEVATIONS
74757e19-b2e9-5bb9-a7a3-2204601488d2 | note | CIBSE W5.2 State of the System
f95b0de6-57d6-5e4c-9796-7ed37763505a | note | AS2941.1-2013 – Section 11
2ba5e6ec-1c61-5d94-a976-e9e879477979 | note | Have pumpsets been installed with the centre-line of all suction pipes at the same elevation; and/ or
efef9b61-457a-50bd-8660-4a9a8f090844 | note | if the pumps have been installed at different elevations, the elevated pump is installed on a properly constructed mezzanine floor; and
3aeb5b98-defb-5988-9d4f-e4f1c949970b | button | with head clearance of minimum 2.1 m to the underside on both levels? | Yes, No
7bc37864-6de3-5f83-87e1-26131613bbef | note | Add Photo
7a1bb20b-d33d-4a9a-96de-ffa24187949e | checkpoint | 4. PLINTH
8d5c7909-b9ed-51e3-a52a-71b7e7faa3da | note | CIBSE W5.2 State of the System
97a5f656-470f-548e-9339-53dc070d2f05 | note | AS2941.1-2013 – Section 11
890519c9-9833-5302-b1f7-51f87550c6b3 | note | Have pumpset baseplates been mounted on concrete plinths with a height not less than 150 mm above the floor?
1d769877-c6a0-50f3-b084-23a99e4e2e61 | button | For fixing purposes, does the concrete plinth extend 150 mm past the edge of the baseplate on all four sides? | Yes, No
7242f26b-b309-5a41-af62-5c8cedb87bd6 | note | Add Photo
39794e38-5ebf-4dd3-8fdc-153d8512c79e | checkpoint | 5. PRECOMMISSIONING CHECKLIST - CHECK
e64d7b75-fe83-584d-b6e1-aaf9fd557fd4 | note | CIBSE W5.5 Pre - Commissioning
091ce54c-a93c-5b19-96a2-a1ecf9c8fa7a | note | CIBSE W5.6 System Checks
ed1126ec-f7bc-5f91-b78b-c6ce2338e73f | note | AS2941.1-2013 – Section 12
0709455d-1f91-5e54-af2a-890c4577f447 | note | Have you checked;
10a174f7-8918-5e57-aef7-7dc8627f93b4 | note | The cooling supply system; and
4e89b6a0-f2a5-5f41-b2e1-e6ca58c42a8a | note | Engine fuel supply; and
f9751610-7ba3-5927-99fb-509ed61a3019 | note | The coupling alignment to ensure that the unit is aligned within the manufacturer’s specified tolerance; and
6da28edf-ce55-5122-98fd-f4025b6d2a3f | note | The direction of rotation; and
2e5f69be-6dbf-5f9b-8087-39e818047ace | note | That the engine lubricating oil is at the correct level; and
0ae57e4d-dd66-5618-a295-aefd50ed1eb7 | note | The battery electrolyte level and the battery leads and connections; and
e6691867-5f9a-5edc-a0ab-9d9dd5d5ce67 | button | That the exhaust system is intact? | Yes, No
47cb6512-2c1b-5fb0-a5b0-6ce729d5a269 | note | Add Photo
edafcd73-4662-4c8e-a6dc-176ec064d447 | checkpoint | 6. PRECOMMISSIONING CHECKLIST - ENSURE
461b86ea-edf5-5804-ab2e-6d5a1a16f946 | note | CIBSE W5.5 Pre - Commissioning
4a11466a-16d7-550e-bc4c-b1c04c8acde6 | note | CIBSE W5.4 System Filling and Venting
8de801ec-5e7c-5380-8817-80e7119322d2 | note | AS2941.1-2013 – Section 12
043580d8-09a8-5b97-81b8-55efc5a971d0 | note | Is the pump primed and lines are clear; and
ecdc6988-77a7-5131-b2c3-3b929c99538f | note | valves are correctly set (open, closed or adjusted to required pressure); and
5a6d0e1d-5c53-5db0-9c7a-2400f61f3b2f | button | is water available? | Yes, No
d0becf51-f79d-5941-9b7f-95758a141cdd | note | Add Photo
1cdcec83-646c-408b-b6f9-cdd925fc1e3b | checkpoint | 7. PRECOMMISSIONING CHECKLIST - ISOLATE
0d6ddeb6-98ed-507d-9819-9baca324745f | note | CIBSE W5.3 Check before Filling
7611c3bd-6458-5312-975b-148a62120932 | note | CIBSE W5.6.2 Mechanical Checks: Automatic Control Valves
901616eb-1a7e-5f28-8cb2-8a8076682961 | note | AS2941.1-2013 – Section 12
3ab636ca-7133-519f-b352-9dc8cb736919 | button | Have you isolated all other water supplies to the fire protection systems, such as the automatic pressure maintenance pump and any other compression-ignition engine driven pumps in the system? | Yes, No
d745feaa-d2c4-5322-8926-ef96fce625d0 | note | Add Photo
bbc4b98d-961a-49b7-a8ba-273d035ca3f7 | checkpoint | 8. PRECOMMISSIONING CHECKLIST - REPORT
1c1af41a-4f9c-5351-bc8f-cd7a909575ea | note | CIBSE W5.5 Pre - Commissioning
e76cfb0b-6db2-59b6-8a2a-0acfdcf1af3e | note | AS2941.1-2013 – Section 12
c5ddad7b-0596-50c3-90dc-0bc418811168 | textbox | Pump plate details:
37a8f953-57e4-5927-aa20-627ca5ed45e1 | note | Add Photo
00f5d6d3-72ae-478d-9973-2391bc4abcff | checkpoint | 9. COMMISSIONING CHECKLIST - RECORD
8ea45551-3388-5bcd-8e30-c1a4261b7b26 | note | CIBSE W7.10 Commissioning Certification
a4b21b36-4452-580b-98d5-13926751cdd5 | note | CIBSE W7.2 W5.7 Static Completion Records
686e4279-bbea-5fda-b99a-60520ae0737c | note | AS2941.1-2013 – Section 12
667f0488-711e-5fb7-a47f-172c41209af7 | textbox | What is the pressure in the system at which the pump starts automatically?
58a8bd82-f139-59be-a12a-3a52c32303b1 | textbox | Engine oil pressure:
4377b84f-3fb3-5aca-82f9-567b05bfb36b | textbox | Pump shutoff pressure:
e70ac930-c9f0-5524-bfcb-f1a0a2570089 | note | Is the Coolant flow correct; and
e73baa5b-e2e7-59cf-8e02-56c648cae812 | button | Are the fan belts rotating and intact? | Yes, No
b778b1a3-f938-574f-a4e0-c64399a38267 | note | Add Photo
a07402b6-e961-4f83-82fc-ffcb95fdb0cb | checkpoint | 10. COMMISSIONING CHECKLIST - ISOLATE
bd93aed5-7de7-51ee-b4ac-b36bdc1fb4c0 | note | CIBSE W7.10 Commissioning Certification
e101bf81-1041-565e-b60e-07e4682130df | note | AS2941.1-2013 – Section 12
0fc13d24-384a-54d0-acea-370243c2d46a | note | ISOLATE the flow meter, partially open the test valve, and flush to remove any debris or foreign matter;
48d08d52-a240-53dd-8dc4-3494d44d2d6f | textbox | open any meter-isolating valves, open the test valve, and record pump delivery gauge pressure when approximately full load flow is indicated on the flow meter:
568e5920-cec2-5dd5-85e8-a471e6d72925 | note | Add Photo
7b768bfc-8bf3-44c5-b5ad-81888a887340 | checkpoint | 11. COMMISSIONING CHECKLIST - RUN AND RECORD
d17e9d8d-a639-53bd-8e15-79328ea45bd8 | note | CIBSE W7.10 Commissioning Certification
0be7edce-8eb8-5dc0-8808-7a81e895f61f | note | CIBSE W5.7 Static Completion Records
731c2f8f-bdad-5e82-8276-637a06ec63aa | note | AS2941.1-2013 – Section 12
df4c0145-f135-5fae-82b0-4e9c3dd85946 | note | RUN the pump for 30 min at maximum flow and record.
94a9020b-cd48-5438-83e5-4df3bbd5864b | textbox | Suction and delivery pressures:
4ef0fd50-f5a2-55a6-8843-68ef7a1096d2 | textbox | Engine running temperature:
571df837-8024-5bff-8023-ed56465d0a0a | textbox | Engine oil pressure (within the engine manufacturer’s limits):
30ca195f-a73a-5fcc-b6be-d20713c9a87b | textbox | Air temperature at pumpset:
f62497d4-4d43-52de-875f-b8829dc3749a | note | Hold the engine shutdown mechanism closed and simulating an automatic start signal until the engine has attempted to start for five automatic starting cycles.
dce2b08a-f00d-58ef-a4a1-dd888541ba8b | button | On the sixth starting cycle, return the engine shutdown mechanism to its normal starting position. Does the engine start immediately? (Clause 9.3.6.2) | Yes, No
ca4652c4-ff95-599b-a349-2de047d28df9 | note | Add Photo
10079e24-56f5-4da0-80dc-e75e3fd2819a | checkpoint | 12. COMMISSIONING CHECKLIST - RUN AND RECORD
8a37ae93-bda4-5760-9b05-53503f29a35f | note | CIBSE W7.5 Preliminary Flow Rate Check
1ced5256-f58e-54a5-b9e2-e936ac628d17 | note | CIBSE W7.2 Flow Rate Measurement Tolerances
2bf304d5-bbaa-5998-bc38-26319da7c3b3 | note | AS2941.1-2013 – Section 12
ebb1af9a-7864-52b8-8a2e-6e59ae111b59 | note | RUN the pump for 30 min at maximum flow; then
e9f057dc-145c-5583-b579-a236563a001a | textbox | Discharge pressure at three other flow rates between shut-off and maximum flow, one of which shall be at the duty flow rate:
cd609e42-ffce-58d3-b6bc-fec1e9e2e514 | note | Add Photo
e2719013-7a63-4b5d-8775-811aee2f706d | checkpoint | 13. COMMISSIONING CHECKLIST - RUN AND RECORD
831b8481-6c90-54bf-bdcc-aef7d630a205 | note | CIBSE W7.10 Commissioning Certification
7ba50586-fceb-5abb-b01b-b006b3853a68 | note | CIBSE W5.7 Static Completion Records
72fbda3f-be15-5016-b195-2708079e238e | note | AS2941.1-2013 – Section 12
19c493de-bf4d-576c-84c7-faa838720be4 | note | DURING OPERATION:
eb55f48c-e188-5c7b-b162-8891f4456105 | note | Have you checked the temperature of the bearings and stuffing box leakage and noted any abnormality?
9b55f487-8fab-5a1a-893b-2e89b584decd | note | Have you checked that all alarms and indicators, both visual and aural, have been activated; and
617a3363-bd4f-59e6-a68a-4e311dfe045a | button | Alarms and indicators, both visual and aural, revert to normal stand-by status when pump is stopped? | Yes, No
d8768bbc-6754-585e-a66a-b3324797ea19 | note | Add Photo
4e6c90a0-141c-4a09-b979-0c7fc8b02365 | checkpoint-no-value | GM Fire Sign Off
8aa433dd-8ae0-484a-b1dc-36b20df0b930 | signoff | GM Fire Sign Off
4c492b6a-343a-4deb-bd9e-a188457aa37e | checkpoint-no-value | Principal Contractor Sign Off
e26bda14-6101-4787-964b-26b6d330d0b3 | signoff | Principal Contractor Sign Off
f6077b97-2876-454c-ac5c-13ebd1d78f2e | checkpoint-no-value | Consultant Sign Off
78869c26-ad24-4769-9cab-3fc3e3ac0714 | signoff | Consultant Sign Off
14d2a939-eaf1-454a-b978-5b326ba854ee | checklist | ITPS-206 Sprinkler Commissioning |  | ITPS-206 Sprinkler Commissioning
f67da234-fbdf-4dda-a8d8-b7ceead7b71b | section | Details
7e3bb81e-b712-45fe-a505-8cfd0521d01a | checkpoint | 1. CONFIRM WATER SUPPLY & PUMPS PREVIOUSLY COMMISSIONED
5df11c6f-9760-5033-82bc-3a0086fc11ec | note | CIBSE W5.2 State of the System
3a228639-065a-5149-a975-8fb14b9971de | note | AS2118.1-2017 - Section 14.9
5dcb27cd-6a4b-5758-88ad-87817e41ee20 | note | Water Supply & Booster Pumps have been commissioned
4783792e-ac0f-5d93-8a40-4a3c9ab546df | button | Are all Valves in the correct position? | Yes, No
7f54093b-860d-43d1-ae85-087f54aa4c5a | checkpoint | HOLD POINT
3f90e2e9-9262-58e3-92b9-e138f07593ae | note | There is a risk of damage to pumps if system is not ready for sprinkler commissioning . Refer ITPS-204 and ITPS-205.
b52114b9-ba18-4fae-a77e-0cf2dbc11280 | signoff | GM Fire Sign Off
ce591833-db45-40e8-bd9d-e84df6bd4885 | checkpoint | 2. CONDUCT FLOW TESTING TO PROVE SYSTEM PERFORMANCE
dd4417ca-9e12-544f-aefb-24ea0e72a95d | note | CIBSE W7.5 Preliminary Flow Rate Check
a84c4d43-7c5e-5cbd-92c5-4d218621b7d1 | note | AS2118.1-2017 - section 4.2.2.
86b47a8f-9bbc-5a37-a204-85a7eb5dc966 | note | Test
e3432612-c8c8-563d-8f49-7fead2381dbe | note | 1) Confirm flow & pressure requirement
9293bbda-79ee-5319-a200-723b4a035782 | note | 2) Secure flow meter to annubar test line
2950125a-c413-5f75-8137-702e8b0b6e19 | note | 3) Manually start booster pump 1
22beb0f9-cf74-52ca-9de6-34168acc0f1a | note | 4) Incrementally open annubar test valve
be567796-8bbe-5af2-a664-bf5a3db5ec8a | textbox | 5) Record test flow & pressure at each stage:
a87cd63a-11f5-5234-a33e-6397b4075171 | textbox | 6) Record pump data at each stage:
bd84b414-8019-5132-8da5-3be54cf79d55 | note | 7) Confirm system achieves pass result
6788adf4-8cf1-5a4f-b02f-a4167b291f21 | note | 8) Close annubar test valve
db465b5e-1eab-540e-b809-0061cdd5eebe | note | 9) Stop pump
acd88c12-a419-5b21-839f-32d402ad6839 | note
36f7da66-8677-59fa-a42e-dbb47e571db7 | note | Has the Sprinkler Block Plan been completed?
5315f7ad-06c7-5f4a-b982-59d2992565c1 | button | Have you recorded this on the Pressure Gauge Schedule? | Yes, No
526ff0aa-bcd1-5494-b51f-f37253ac8b26 | note | Add Photos
34968e5f-984a-4305-85af-76d60204d993 | checkpoint | 3. CHECK OPERATION OF DBA PRESSURE SWITCHES
a8e0fcfa-094b-57cd-a85a-3d1527449be9 | note | CIBSE W5.6 System Checks
cf58abfa-2e4a-5241-9ab4-bcceeb4d42c5 | note | AS2118.1-2017 - Appendix H4
7f007be6-5fdf-53ac-90f4-38453e1bd3ec | button | Does the pressure switch change state when system is activated (Rise in pressure switch)? | Yes, No
0dc4945a-18f9-55d0-b208-8c024c9b0060 | note | Add Photo
8894d702-ade6-4c1f-bdd7-f3e29ff8f890 | checkpoint | 4. CHECK OPERATION OF PUMP START PRESSURE SWITCHES
6eb4f353-45d2-5463-909d-e9025a104b35 | note | CIBSE W5.6 System Checks
89701280-8f6c-5fa6-a3c8-ee3467ec010f | note | AS2118.1-2017 - Appendix H5.4
7edb5ec3-c0e9-5203-8ce0-30a74246eca3 | note | Are the pump start pressure switch settings in accordance with pressure gauge schedule?
3dd90b78-c637-50c5-851c-4e18f7ba47f9 | button | Have you checked the operation of All pressure switches individually? | Yes, No
65f2977b-daa5-58eb-a196-352e34c04c7b | note | Add Photo of Pressure Gauge Schedule
1fafc345-856c-41b2-b833-57fd385a37ce | checkpoint | 5. CHECK OPERATION OF DRY FIRE INTERFACES
525da64c-2a79-560d-9a68-907e0399e675 | note | CIBSE W5.6 System Checks
ba5c790c-415c-5d45-9a83-7147ead9e7fd | note | AS2118.1-2017 - Appendix H6
9765a0dd-50bb-5917-9cca-bd252e950253 | note | Activation of ancillary Pressure Switch (Rise in pressure switch) registers at FIP
c2117379-c1d6-508d-ba30-baa6d15768ac | note | Activation of flow switches register at FIP | Yes, No
a62a24a9-22ac-50da-87f3-ca08a4a7eaea | note | Change in valve state/position register at FIP
51fd5727-af57-544b-bdb8-279498791e99 | note | Attach the valve list
c6048cf3-0b65-4851-b883-eec8dadba51a | checkpoint | 6. COMPLETE FORM 71 & ALL TEST RECORDS
177bad4e-9212-593c-a906-78a10fe2bd89 | note | W7.10 Commissioning Certification
6ae6653d-5711-56e0-89b1-c6ad1c1897f5 | note | NCC 2019, AS2118
490b67be-99ba-58ea-b9f9-0e362f46b858 | note | Flow test pass result on Form 71*
5724eff1-bf0a-5478-adc5-e409fac4cb0c | note | Record the pump start pressure switch set points:
928c810a-a023-5b80-b0ae-d3c225ae074c | button | Record the dry fire interface test results: | Yes, No
c79b9982-9f20-5af1-85cc-f61518c10b79 | note | *Form 71 - Fire Hydrant and Sprinkler System Commissioning This form is to be used for the purposes of commissioning water based fire safety installations, as required by the Queensland Development Code – Mandatory Part (MP) 6.1, which is a building assessment provision under the Building Act 1975, section 30.
4429f79a-7bf7-521c-8748-a1e1d505b3bb | note | Add Photo
70fcf860-b02a-4c23-baf6-de05f137cd2a | checkpoint-no-value | GM Fire Sign Off
f755ead7-dd1b-474b-8aea-3413a7b67d8a | signoff | GM Fire Sign Off
500b93e6-f7fa-42a0-8242-206e5b7cb10e | checkpoint-no-value | Principal Contractor Sign Off
a9fa8403-1669-4ac8-a7cc-64f64421be7f | signoff | Principal Contractor Sign Off
93122f56-1e6c-4dd5-b340-919089a3eb2f | checkpoint-no-value | Consultant Sign Off
e16b56a6-9f71-4c59-893c-58d1dcff950f | signoff | Consultant Sign Off
c24a4479-d050-47e5-8f8e-3fbe53c5c36e | checklist | ITPS-207 Hydrant Commissioning |  | ITPS-207 Hydrant Commissioning
686e521d-a466-43b7-a855-6e2ef40caa6c | section | Details
9b0e2ea6-b814-406c-9935-fca79681d131 | checkpoint | 1. CONFIRM WATER SUPPLY AND PUMPS PREVIOUSLY COMMISSIONED
3c102f89-32d7-53ef-8160-0e68888bfb18 | note | CIBSE W5.2 State of the System
fca9a80d-c224-5f7c-a1dd-97bf95d873a4 | note | AS2419.1-2005 - Section 4 - To comply with Part 4.2
2ae196b8-b893-51f3-ab07-ed8216fa792b | note | Have the Water Supply and Booster Pumps been commissioned?
c9f23bca-7c46-560d-8ce4-ea5706bcda58 | button | Are ALL Valves in the correct position? | Yes, No
4ee9822a-3f99-496d-8af2-060228d2c1aa | checkpoint | HOLD POINT
4b2c5bbb-6fcd-52dc-b3b0-a164273344d4 | note | There is a risk of damage to pumps if system is not ready for sprinkler commissioning . Refer ITPS-204 and ITPS-205.
9ffac547-f891-402c-b28f-6efa6726a586 | signoff | GM Fire Sign Off
2a57da7d-70e8-49ce-920d-56c16536ab29 | checkpoint | 2. CONDUCT FLOW TESTING TO PROVE SYSTEM PERFORMANCE
23112ad1-8ad7-5d8e-9c89-6e750cfed644 | note | CIBSE W5.2 W7.5 Preliminary Flow Rate Check
c3d2de9c-8583-535e-9005-0ee1f0eb8bcc | note | AS2419.1-2005 - Section 2
49de3448-8654-56f5-9bc3-a80bc503858f | note | 1) Confirm flow and pressure requirement
4b1438e1-3cf0-51b0-9892-f4c8a8287857 | note | 2) Secure micrometre and calibrated gauge to hydrant outlet
ffd4cf00-1507-5369-9dd4-1ba9b5ec2a5e | note | 3) Manually start booster pump 1
b7101965-49ac-53ba-ab30-f68f634adcab | note | 4) Open hydrant valve to required flow rate
75aaf898-04cd-59d9-89c0-08a300e89d12 | textbox | 5) Record residual pressure at required flow rate:
9fd1228b-0f43-5f78-8e8a-6e6d4a369922 | textbox | 6) Record pump data:
650fe6f0-a54c-534e-b2ce-bb389130e1bd | note | 7) Confirm system achieves pass result
e528d2b7-b3ec-57b4-ae6f-9b6fb3ae9304 | note | 8) Close hydrant
32281e71-82dd-5709-9c5b-f7b81ea8db5f | note | 9) Stop pump
bcebc9de-8fb7-5d4a-b87e-6a6ea00b0d97 | note | Attach Hydrant Block Plan and Pressure Guage Schedule
7344eedd-2b18-42c3-817e-349b0cd7a4f1 | checkpoint | 3. CHECK OPERATION OF PUMP START PRESSURE SWITCHES
9a01f929-3658-51e7-b61e-2864a5234b3a | note | CIBSE W5.6 System Checks
18dfbbdb-e496-528a-a4f4-2fa7500f2424 | note | AS2118.1-2017 – Appendix H5.4
0e0aa008-4be6-5dcb-9f48-6e0a409498ec | note | Is the pump start pressure switch settings in accordance with pressure gauge schedule?
5584b0ce-888f-5035-87d8-fe664223b29a | button | Have you checked the operation of all switches individually? | Yes, No
2a017dab-cf0a-5863-8274-e0cc6e2a2305 | note | Attach Pressure Guage Schedule
923fbb6e-b5b7-4699-a761-f8dd27eb847c | checkpoint | 4. CHECK OPERATION OF DRY FIRE INTERFACES
464277a3-b816-57a2-ae91-7e35b5173a2f | note | CIBSE W5.6 System Checks
be87ce7d-cd8c-571a-8339-e79fa22a63c3 | note | AS2118.1-2017 Appendix H6
96edc218-67c9-5d6a-867d-ff185c1315a2 | button | Change in valve state/position register at FIP | Yes, No
fd877fe6-fc10-5637-8469-39f8bd59a723 | note | Attach Valve List
9b9fe0e8-b732-486d-aeab-cd099352f045 | checkpoint | 5. COMPLETE FORM 71 & ALL TEST RECORDS
263b9a35-b996-5169-9d47-cae0b8a1e33e | note | W7.10 Commissioning Certification
aa0a026f-06b2-5d2e-82f6-e0d65e009c4d | note | NCC 2019, AS2118
c3c17d56-d6f2-58cd-8e8a-981913986c8e | note | Flow test pass result on Form 71*
da9908e8-43ee-517b-9d31-2002af02213a | note | Record the pump start pressure switch set points:
81b6727a-4859-5ed6-9026-589f61712b20 | button | Record the dry fire interface test results: | Yes, No
431e21f7-0371-5c3b-a160-8a834f7627a2 | note | *Form 71 - Fire Hydrant and Sprinkler System Commissioning This form is to be used for the purposes of commissioning water based fire safety installations, as required by the Queensland Development Code – Mandatory Part (MP) 6.1, which is a building assessment provision under the Building Act 1975, section 30.
f9306c60-f406-5130-bb0a-2f2a934db91c | note | Add Photo
4aa62756-97d9-49f2-8436-190ab54ca721 | checkpoint-no-value | GM Fire Sign Off
c7ee08a4-205f-40f3-9c83-dd43e26f97fc | signoff | GM Fire Sign Off
84792006-d3a0-4ba0-aa57-2296518a8ddd | checkpoint-no-value | Principal Contractor Sign Off
69ba7d58-e616-45ba-ad5f-b4c5955c937e | signoff | Principal Contractor Sign Off
3bb5d85c-dffc-4816-be28-9da24be2bc71 | checkpoint-no-value | Consultant Sign Off
a4888d35-193d-4056-a6d8-a121dd99f3b7 | signoff | Consultant Sign Off
95e11fea-a076-4cd7-85ce-9995fa9b1c7c | checklist | ITPS-400 Temporary Fire Strategy |  | ITPS-400 Temporary Fire Strategy
6cb86481-fcf9-46f8-9841-0da8b555bea0 | section | Details
639ed363-b32d-4cec-b8a0-c7e8406015ee | checkpoint | 1. INSTALL AND CHECK PORTABLE FIRE EXITINGUISHERS INSTALLED AT FIRE EXITS
5c3e7aa7-fa76-4f23-9651-462141f1aa83 | checkpoint | 2. INSTALL AND CHECK HYDRANT BOOSTER INSTALLED, BLOCK PLANS, LABELS
b567c5a9-df03-45f1-a853-bffba600754c | checkpoint | 3. CHECK EXTERNAL ATTACK HYDRANT IS WITHIN 20M OF BOOSTER
ae31c060-18a6-4504-b821-a30e07389bac | checkpoint | 4. INSTALL AND CHECK SYSTEM IS PRIMED WITH WATER (TOWNS MAINS)
361d4753-9a85-4f41-b351-51cea458862c | checkpoint | 5. INSTALL AND CHECK HYDRANTS INSTALLED PRIOR TO JUMP
98446794-2f3f-450c-bfb7-97fe465e26b8 | checkpoint | 6. CONDUCT WATER PRESSURE TEST OF HYDRANTS
8117d1de-59e7-464e-90f5-f7f2e73fe54e | checkpoint | 7. HOLD POINT DETAILS
cb19ec5a-ac11-5235-8330-4b6093af7b16 | button | Hold Point Required: | Yes, No
2cfbc421-03a4-4fc5-b035-ce8d4cacb17f | checkpoint-no-value | GM Fire Sign Off
45c0df11-1755-43c6-825f-735260021fdf | signoff | GM Fire Sign Off
083149ee-0a71-4276-bd77-62c52bf41bdb | checkpoint-no-value | Principal Contractor Sign Off
8b86cd00-c15b-49ae-a239-c86dc7f4aa6c | signoff | Principal Contractor Sign Off
5fab6021-cfb7-4e21-8a78-5e96a240cc47 | checkpoint-no-value | Consultant Sign Off
e044d65f-3f47-4dcd-8bd5-3596aaa4e611 | signoff | Consultant Sign Off
e13a4ab5-f340-44a0-afab-9415821eaceb | checklist | ITPS-401 Site Temp Asset Lists Extinguishers |  | ITPS-401 Site Temp Asset Lists Extinguishers
8eaa84db-684f-4bd9-8238-faa24fac9db6 | section | Details
d1cf28bb-e4bc-4cec-9c93-dc5b70a708fd | checkpoint | 1. ASSETS 1 TO 10
00cccc45-2dc3-50b1-b72d-56a8c0fc889b | note | Add Photos and Numbers Below:
b20db316-0f08-449f-8960-38e50ad23345 | checkpoint | 2. ASSETS 11 TO 20
bf9d46e1-cab5-58ba-89a7-2cd966e31e85 | note | Add Photos and Numbers Below:
fb94fc8e-430d-4079-a811-51b0ddbf5bf1 | checkpoint | 3. ASSETS 21 TO 30
8dfa41bf-c675-5be7-baa3-9870ed0d8f02 | note | Add Photos and Numbers Below:
3a560dba-a8b6-4d66-9970-ea3a325a9a0d | checkpoint | 4. ASSETS 31 TO 40
83c31cf5-8dc7-5967-ba60-165e5bb4a9b2 | note | Add Photos and Numbers Below:
8f3937fd-b18f-4984-a0d1-0483687249a0 | checkpoint | 5. ASSETS 41 TO 50
34a6c12a-2886-5613-882a-11f9b93615c0 | note | Add Photos and Numbers Below:
9d2857bc-4100-476e-8c75-89db3f91b09d | checkpoint | 6. ASSETS 51 TO 60
307c12e2-9bbb-5149-a8aa-512a4e5752cd | note | Add Photos and Numbers Below:
59df53fe-16f9-4b14-ab08-41c5a88438fc | checkpoint-no-value | GM Fire Sign Off
acef4e6c-d6d2-4311-b626-2a6a32ceb9ac | signoff | GM Fire Sign Off
d750a1e1-2e58-48e1-ae56-070c8fb735fc | checkpoint-no-value | Principal Contractor Sign Off
952afc0b-3e42-402a-84bd-f9e17be45401 | signoff | Principal Contractor Sign Off
8fa83fe7-fe2b-456d-aff6-434ab589550d | checkpoint-no-value | Consultant Sign Off
919f5857-64b0-43d9-a17c-4f86ff20fa4d | signoff | Consultant Sign Off
1e70382a-cd84-5ae1-8862-c1c058edde43 | checklist | Lendlease Contractor Schedule H Checklist |  | Lendlease Contractor Schedule H Checklist
7a748d55-533f-527b-b0f9-60e8fa293f5f | section | Incident Reporting
7c933c97-88e7-4d19-8439-4b61e6d6f3c9 | checkpoint | Incident Reporting
b5b35a37-7382-54ba-8bfb-811dbf4572bf | button | Any incidents were immediately verbally communicated to Lendlease | Yes,No
6801e20c-e2f1-5a7f-a0d5-fe47c4fd717b | button | A copy of Incident Notification Form was submitted within 4 hours | Yes,No
66e9a4c6-0421-5ef0-8732-cd78bca8e3a8 | note | Detail any incidents from the past month below and attach relevant forms below.
826609b4-fc54-5a39-ad75-e1293f234680 | section | Workers compensation first, progress and final medical certificates and Return to Work Plans
0c9492a0-811a-544b-b5bc-2fc846063034 | checkpoint | Injuries and Illnesses
e20f96b2-5ee3-56b2-b5c5-912388171f1b | note | The following have been provided;
5492c177-794d-5136-81c9-8f8430e1d1c8 | button | First Medical | Yes,No
823e0dc6-15b2-594f-962a-261c0a26bf92 | button | Progress Medical | Yes,No
09fd6dbb-22b0-55d9-bec1-c657d23b526c | button | Final Medical Certificate | Yes,No
d36edd68-abcb-576d-b8fc-6978886ed6b8 | button | Return to Work Plans | Yes,No
a20041b8-0ee5-5f04-a4e5-2f9b0b26598b | button | I have submitted any necessary Injuries and Illness forms within 2 hours. | Yes,No
b9e71c13-fb0c-5796-9a4d-1f3ce13a3ae0 | section | Reporting
e2cefbe1-7b4c-58cb-9296-52013acd2aff | checkpoint | A copy of any regulatory notices has been submitted to Lendlease via email immediately following receipt from regulator.
4094ba7a-5738-5658-93bd-78c5dff3acda | checkpoint | Daily Pre-Starts have been delivered to the office by 9am each morning.
4fb06383-4684-5418-9d3a-cc9f4daa39dd | checkpoint | I have submitted a copy of Toolbox Talks to Lendlease weekly, including records of attendance.
67b6449c-0fcb-586a-8ebf-2addf988ee69 | checkpoint | I have conducted a miniumum of 1 EHS inspection per day and a copy of EHS inspections for the month have been submitted.
2c6854ff-7dce-52fd-90e9-e611023a913b | checkpoint | Labour Statistics and Man Hours
c45fef96-b2bf-597b-b3ce-585cf62a4bdb | note | Contractor Labour Statistics:
3961a981-e885-5a9c-877f-050b8d38419c | button | Has been completed weekly? | Yes,No
2fcfc2ff-fc1b-5978-9631-1633f919466f | button | Has been submitted before the 26th day of each month? | Yes,No
506b1288-bedf-5659-a27b-52efdb96cd11 | button | Is attached below? | Yes,No
c5929b96-f03b-5652-94b3-156328f9754d | checkpoint | SWMS
1bfaab1b-8e49-53ee-9e9e-873030346dbc | button | Copies of updated SWMS have been submitted to Lendlease | Yes,No
e4104c40-5765-5a71-b723-f81d0bcfb590 | button | Contractor SWMS review register has been submitted to Lendlease | Yes,No
1adcbe56-3cdc-5f92-af30-4e947fc6e60f | button | Updated copies of signed SWMS have been submitted after onboarding each worker | Yes,No
d064d5c0-d0e0-5fe2-a4de-7727e0a3ff4a | checkpoint | Workers are trained and competent
973bcb55-6152-5f6d-a2b0-4d5902cff6f6 | button | Copy of current training register has been submitted | Yes,No
58d3b39a-17b8-56a7-9770-52ce522e2ef8 | button | Copies of licences, qualifications, training records for any courses attended during the month | Yes,No
3495576f-5639-59ab-a767-a607784a3cf2 | button | VOC (Lendlease Template) for concrete saw/angle grinders and Plant to be submitted for all workers before operation | Yes,No
aef74d7b-d587-5e34-9266-884de37191d4 | checkpoint | I have submitted copies of daily pre-start inspection records for the month
d77f5e32-8a3c-5a96-97b8-96e1ee4e803b | checkpoint | I have attached a copy of the up-to-date Plant & Equipment Register
863d56e4-a279-57b2-a68e-d4b15f9c5577 | checkpoint | Copy of current and up to date Electrical Register has been submitted ( 3 monthly unless new tools added)
1c11da09-d5b8-50be-807f-7a10f77c3645 | checkpoint | I have attached a copy of the Fall Prevention Register
f73063a9-6e9f-572b-981e-bc4461355341 | checkpoint | Lifting gear to be inspected, tested and tagged
e9a421ee-a73c-5e73-8691-a5ecb3c66c99 | button | I have submitted to Lendlease and attached below a copy of lifting equipment quaretly testing register | Yes,No
92bd2845-9677-5a10-9f62-2f292143cd1c | button | I have submitted annual inspection certificates to Lendlease | Yes,No
d8e7b937-09da-531f-a96c-18f76041589f | button | Monthly inspection register has been sent to Lendlease as per Lendlease Lifting and Slinging Guideline | Yes,No
ae92f7c6-9451-56f7-ae90-9960f5122f4b | checkpoint | I have attached copy of Hazardous Substances Register highlighting any chemicals brought on site this reporting period.
a02a0ab0-ff4d-53ee-8a92-1c3a98928fa7 | note | NOTE: Subcontractors are required to use Chemwatch to log all chemicals utilised
ba1f906f-1a0c-5a9f-a883-1abf31d17b82 | checkpoint | A copy of the Ladder register has been submitted this month
3d903859-b52d-52dd-aabf-1957c83c9f42 | checkpoint | I have attached a copy of Safety Data sheets for chemicals brought onto site within this reporting period (this month)
23484093-b5c0-5552-a60d-8d92e054fe12 | checkpoint | Temporary Works Design Register
75720ec4-cb43-5a56-a617-c22bb12e8de3 | note | NOTE Temporary Works Design Register must be submitted prior to mobilisation capturing of all Temporary works to be implemented by the trade
fcd4c867-242a-5081-80f1-6d415a64ea0b | button | I have attached the updated Temporary Works Design Register | Yes,No
5d21287a-0bce-5c38-a159-cd6673bf2998 | button | I have attached Evidence of Engineering Certification | Yes,No
d80834eb-8560-5715-b772-28441493f097 | button | I have attached Evidence of 3rd Party review of engineering | Yes,No
92ddcd9e-8e9b-5040-844d-c86a13562740 | signoff | Signatures
5f39f63b-4f38-5279-b8a3-5d9522726ee4 | checklist | POLICY-005 Safe Work Procedure |  | POLICY-005 Safe Work Procedure
90e555f1-b7db-5342-8f6e-ab9bb0160482 | checkpoint | Task Details
5fc57c12-5477-5737-99fc-084691513b3c | note | Use this form to record your safe work procedure after analysing a particular task in your workplace.
54e2bd4c-94eb-5209-bbf6-64e830f80521 | textbox | Work Area:
9345d407-83d5-53e1-ae76-961efef6fbc7 | textbox | Task:
8c2a2f79-7fb1-547f-9a76-c4ff8879c69f | textbox | Safety Risk: e.g. electricity, moving parts, noise
73bf96f4-9e1e-51a1-a557-4789936e6b2d | checkpoint | Personal Protective Equipment (PPE)
a90d62f1-4ee9-5c2d-b7df-76b97030b23e | note | The following PPE must be worn, and precautions taken, when doing this task:
022fa3f2-9ec3-551f-818a-9c4229ce102e | tickbox | Work Gloves
52b6e6d4-f5fd-5247-9a5e-5fad9cd8d0f5 | tickbox | Safety Glasses
d9b21827-bffa-5c64-9e91-aa8761441fa2 | tickbox | Steel Cap Boots
4cfe66fa-6182-5fd6-a77e-838eead415da | tickbox | Ear Protection
b4497feb-45d9-5b69-991e-167ba3c02e54 | tickbox | High Visibility Vest
7deef65f-a665-55a5-b5f7-28ac247ea135 | tickbox | Head Protection
1b2d413d-c2a0-5534-9415-abc526c07534 | tickbox | Respiratory Mask
7ecd5c2e-1ed2-5ef3-82f1-e7eab5e88ed4 | tickbox | Face Mask
e41d6c28-3b8f-5973-9144-7fd4a73ccd3d | tickbox | Protective Clothing
6789b585-de74-5794-bb90-7fa121ba3daf | tickbox | Wash your Hands
cc546369-bca4-51b6-ab24-8e4406ba760e | checkpoint | Supervisor Signoff
4570fb2e-7310-5ac1-a58f-8ade9076d7c2 | signoff | BY SIGNING I CONFIRM I HAVE APPROVED THIS SAFE WORK PROCEDURE
377dad0f-aa24-54c0-8934-eb50d7085b59 | checklist | REPORT-002 Hazard |  | REPORT-002 Hazard
8111ace1-1386-5c1f-8290-3df28e3c8d3f | section | Details
7016619e-d9e9-575d-a598-04fc8176f882 | checkpoint | Hazard Report
d6fac993-3afc-5a0a-bf59-46b1183a40b6 | note | GM Fire employees shall complete a Hazard Report in the event they identify a hazard that may result in injury or incidents to person(s), property/plant, the public or the environment.
421c3000-183a-573f-b675-9b67446b28c9 | note | The principal contractor will be informed immediately and provided with a copy of this report.
423d5ed9-def2-5985-8cad-6c2afa7e0d08 | checkpoint | Hazard
779b2823-ead7-57ba-8973-50e213a956d0 | textbox | What is the hazard?
e23dd611-f6df-5b35-a2ee-6c2f1af58ca8 | checkpoint | Contributing factor
7c1617a6-9bc4-58c7-83e0-4ac6b7a8929a | note | What are the contributing factors?
b909e342-13da-5c75-9a16-d2eae827b982 | tickbox | Environment such as noise, slip or trip
e92993f8-77fa-505e-9226-c869f455e1a5 | tickbox | Equipment/ materials i.e. wrong or inadequate
2cfcadef-9ac4-5c49-93aa-1fdd30bbd5d7 | tickbox | Work Systems i.e. inadequate training
17cf5a44-4765-558d-8bd9-fee7cc14ca70 | tickbox | People i.e. production pressures, lack of communication, lack of procedures
757fde40-c494-50a2-9a89-759f08992678 | tickbox | Other
3da07c87-9fae-5160-ac16-7bf3713d8f42 | textbox | If 'Other' please specify:
5b8936dd-da50-5d1e-a2b4-e9a5b6b57cc3 | checkpoint | Corrective Action
8dca55e3-584a-57b5-abad-6128a4fe8381 | textbox | What are we going to do to fix the problem?
befb55ad-6428-58d3-a1ba-0824cc511374 | textbox | Who
f0f32da2-4b10-5043-b9ce-081e5d91b042 | textbox | When
09c0367c-9df2-5a1e-b57f-ce79d5be231a | checkpoint | Completed By
e8cad4f8-a779-54c4-8306-b65b38b7a52b | signoff | Signature
0f56543f-1fcf-5a12-adea-9042b0f34b4f | checklist | REPORT-003 Chemicals Review |  | REPORT-003 Chemicals Review
8111ace1-1386-5c1f-8290-3df28e3c8d3f | section | Details
0d8a6e98-b471-43b6-9650-ee939445ff56 | checkpoint | Details
4ac30089-4533-51d3-8dd6-b8ec501373cc | date | Date:
5b3e37b6-74a8-5e8c-b6a9-a683396c7f2c | textbox | Time:
eefd7d21-c3a8-5249-9155-dcea38b4b61b | checkpoint | Existing Register
9e02aff2-7ea5-54e7-b974-6a6404e755dd | date | Last Revised on (date):
6af00759-a4c9-5d98-85a8-b72324ad2647 | note | Upload a photo of the "Register-006 Hazardous Chemicals" as it is on site today.
586de132-0677-5158-8fb0-c38150ef6201 | checkpoint | Chemicals on Site
42470866-3263-593f-9713-37c9caf4f5e4 | textbox | Location where Chemicals are being stored:
fcda37d6-585e-580c-bc1c-56bd76552ff0 | note | Upload a photo of each Chemical on site
8cbd2a0e-3c28-53bd-b9da-5a65540b2443 | checkpoint | SDS
9b415998-7708-5a04-af3e-41003c551b91 | button | Have any of the SDS sheets expired? | Yes, No
a9baba90-4203-5977-a3a8-af1696798675 | note | If 'yes', cease use of Chemical and contact GM Fire Management immediately.
978423bf-2d61-5f1a-b9bc-9c8eda763c61 | note | Upload a photo of ALL Safety Data Sheets (SDS) on site.
58bfb4fd-b3d4-5f94-a67a-e067a225bcd0 | checkpoint | Declaration
35bca062-fb37-51e9-bb3e-34407159ee52 | button | All Chemicals on site have been approved for use by the Principal Contractor | Yes, No
e87c1613-1aa2-5321-a6a6-4edc69e06b32 | button | All Chemicals are stored securely | Yes, No
e256eab2-8cdc-58b4-aa1a-b65ff3187f43 | button | Any Chemicals that are no longer required on site have been removed and or disposed of as per WHSE guidelines | Yes, No
0da0ee29-0ac0-5051-ad4a-3e439a9e4b19 | signoff | BY SIGNING I CONFIRM I AM THE REPSONSIBLE PERSON FOR HAZARDOUS CHEMICALS ON THIS SITE, AND THAT ALL INFORMATION I HAVE PROVIDED IN THIS REPORT IS CURRENT AND TRUE.
42c7df9a-ccb8-5d7f-9abf-a956b1f84163 | checklist | REPORT-006 Incident Investigation |  | REPORT-006 Incident Investigation
8111ace1-1386-5c1f-8290-3df28e3c8d3f | section | Details
6412ac75-35b3-555b-a89e-87d89553cfa8 | checkpoint-no-value | Incident Investigation Report
26c7a877-82ff-5d4d-9964-4e831bec896a | note | GM Fire shall complete an Incident Investigation Report in the event of any injury involving medical attention or off site treatment or in the event of any incidents involving a near miss, property/plant damage or injury to the public or the environment.
c7009061-5139-5526-a062-83adc69dbabf | note | The principal contractor will be informed immediately in the event of the above. Following discussions with the principal contractor, a decision will be made as to who will conduct the incident investigation. The principal contractor will be provided with a copy of the completed Incident Investigation Report.
0bb42031-c4a8-5bcf-80ff-6fc5304ee4f4 | checkpoint | Class of Incident
319b1c6b-9f44-55ea-b16c-b1a07631b0a3 | tickbox | Injury
0adde8bb-4f35-5400-993c-c7d0180c2af2 | tickbox | Property/Plant Damage
621668cf-7542-5404-a731-45e940e7d4ee | tickbox | Near Miss
95d75d3d-669b-5354-b3b0-96b4a129a1c0 | tickbox | Environmental
67776edd-303c-58ed-b6a4-4c93c3ad56de | tickbox | Other
c5515547-5acf-5223-adaf-ff810432bbba | textbox | If Other - Please explain
e433ee97-85b5-52fa-97a9-25ca60ea13bc | button | Reported to Princpal Contractor | Yes,No
857bb4fc-18cf-5306-a76e-802c247b752f | textbox | Details:
e1d07f73-ecd2-514f-8842-5a2e0effd57f | button | Further Action Required | Report to Authorities,Other
820f14d5-50a0-5c15-96c5-71e6e32d06c6 | textbox | If Other - Please explain
bc36afa9-00da-5f53-99b5-0b99d61a7935 | checkpoint | Details of Incident
92284681-efd2-53d4-8e0b-d46de0d7e437 | date | Date of Incident
673f8d24-ff72-5e07-b453-93880d52a9f4 | textbox | Time of Incident
325ed646-43a2-5fc3-9425-0bef6e03fe7f | button | am/pm | am,pm
4b70799d-acc0-5966-a907-0ef28ba3f126 | textbox | Witness Name
541505a5-4428-5a09-a1c7-efa380a6cf43 | textbox | Witness Contact
fdfff4a4-8f76-588d-97bd-e1944521b0f4 | textbox | Nature of Incident
725a55af-18c7-57c8-afe2-bfa092de1b6a | textbox | Location of Incident
3f3be10a-9abd-53e3-82f0-2667d7e71aa8 | textbox | Description of Incident
b482344c-2e6d-577b-9ddb-70e3d053f88b | textbox | Details of damage to equipment/property?
5acc9a29-5ef8-55dc-93ab-9320efe0254e | checkpoint | Injured Person/s (if applicable)
24e6a102-3cb8-5740-9562-2f6fcc5871ca | textbox | Name
c68b8d90-60e8-5111-8e35-d7857559c628 | textbox | Address
e678a59a-6b1f-5756-b6cf-2d17da084cb1 | date | Date of Birth
66d64f8b-744b-59a5-8649-41a77a1b3902 | textbox | Occupation
f3631539-86a5-543a-ad2e-dad8be5e4b52 | textbox | Employer
df6586a3-039d-5599-8263-333b90fa2c9b | textbox | Referred/transferred to
2653d5b4-f6f4-5d10-b061-5710923ec319 | section | What factors contributed to the incident?
673b3686-24cc-52e8-a200-da491c74d4d4 | checkpoint | Environment:
5bebb027-96f0-5460-890a-132a143a47e3 | tickbox | Noise
5e04e3c6-c511-54d9-855b-61b79ba33d83 | tickbox | Layout / design
be7367f6-b65c-5e31-9806-b57e064484b1 | tickbox | Lighting
b344a257-3875-58bf-9242-ae1b70d9c52a | tickbox | Dust / fume
c1b98094-8764-57ae-8d8f-23524f9f5e83 | tickbox | Vibration
c6079cb7-cfed-539d-a3de-4ffe5242c1a5 | tickbox | Slip / trip hazard
85c76db0-7b13-5e0b-b320-9a0f6543aa2d | tickbox | Damaged / unstable floor
1e95cef6-f5ed-5510-89c5-ba7214c48c16 | tickbox | Other
7af769cf-fdc6-5763-a34f-36b7668432b1 | textbox | Other (if applicable):
da263eea-7753-5dda-9253-36aae5136ab1 | checkpoint | Equipment/materials:
fe1e78dd-509e-5b53-8078-3c13e8d0020a | tickbox | Wrong equipment for the job
48449b5b-94f5-56fd-aa68-28179f2a1234 | tickbox | Equipment failure
34dbaa91-66eb-5b35-86e6-12b7080c0add | tickbox | Inadequate maintenance
340c7cf0-23ea-5aaf-be3e-08341656325a | tickbox | Material / equipment too heavy / awkward
d44177e4-2535-597e-9309-931a3a8d12ee | tickbox | Inadequate guarding
3d7d49b4-0c2b-5d53-bfdc-aa67787549d7 | tickbox | Inadequate training provided
000690e7-a449-5a80-a869-a79c71c27c48 | tickbox | Other
e2a3d872-b06f-56d7-868a-7dfc157a60c7 | textbox | Other (if applicable):
29bb93fe-1a56-5a6a-a4d8-caafbdc08848 | checkpoint | Work systems:
5dd9bf85-df05-50a5-9d39-ba8c92524aee | tickbox | Hazard not identified
2fbf68fc-22c1-530f-9cb2-b87b25344ca7 | tickbox | No / inadequate risk assessment conducted
0387a054-0cba-5d62-97d1-4479ebe8b41d | tickbox | No / inadequate safe work procedure
d37a698b-994a-54ae-81f2-b04aa7a1df63 | tickbox | No / inadequate controls implemented
c6ba7810-1a06-5766-8b22-30f4fdc6cfd1 | tickbox | Hazard not reported
8f15171b-ea63-518f-a1d3-40a0cdb8bb86 | tickbox | Inadequate training / supervision
22ddaef3-e684-5031-82f2-eabc39055e20 | tickbox | Other
df7a8e40-28bc-528b-b28a-0b6efe49c3d3 | textbox | Other (if applicable):
13eb0e36-06f7-5153-ba71-5b36d7104644 | checkpoint | People:
68c29607-73a8-59a9-918a-e8a1a7758f3b | tickbox | Procedure not followed / no procedure exists
f49a9eb6-f469-5486-a041-424512d20bb0 | tickbox | Drugs / alcohol
315224a4-528b-59d0-b752-048abb08d4dc | tickbox | Fatigue
2ed0f27c-86d8-5e84-a4f2-361debecd863 | tickbox | Time / production pressures
1cf8af67-af67-5409-bca2-d1a6cdab08ea | tickbox | Change of routine
91dc8070-c2b8-5f0c-bd24-be694c6f87a7 | tickbox | Distraction / personal issues / stress
06712e9c-8051-58f7-8676-16be7955cabe | tickbox | Lack of communication
feefc030-bfe5-5354-a12e-104f9508da2b | tickbox | Other
c3685b47-7234-5973-bc9c-d337e162b8f6 | textbox | Other (if applicable):
1c21ef12-b1aa-5192-a53b-a50ba28212cd | section | Corrective actions:
e23dd611-f6df-5b35-a2ee-6c2f1af58ca8 | checkpoint | Contributing factor
34fb92e3-cc81-5b39-9cc4-3570d31ea806 | textbox | (from above list)
73874509-bac9-555d-8853-d738436ac006 | textbox | What are we going to do to fix the problem?
da26fb44-6d60-52fb-870e-90b8c5ffd716 | textbox | Who
f5d8b083-01e8-5841-aea1-53e16258b921 | textbox | When
585d5a57-d317-5a2c-8c86-399f10c406d3 | date | Completion date
09c0367c-9df2-5a1e-b57f-ce79d5be231a | checkpoint | Completed By
11f31f0b-4a44-5a8b-8133-2e07b430d536 | textbox | Name
9346513a-1500-5fae-b25b-d6e769dd31d7 | textbox | Position
40b6d092-dcdd-58fd-840d-c4a54e7f5c2d | date | Date
e8cad4f8-a779-54c4-8306-b65b38b7a52b | signoff | Signature
502881c9-67c5-5efc-ab28-0fe458372e1f | checklist | REPORT-010 Request Corrective Action |  | REPORT-010 Request Corrective Action
8111ace1-1386-5c1f-8290-3df28e3c8d3f | checkpoint | Details
9810d1bc-258e-56f0-9bc6-452940de7206 | date | Date:
894e936a-16aa-5a12-8dd3-a2e86d12abb3 | textbox | Time:
f4900617-e6c9-5013-9f0f-3deea28445cb | textbox | Location:
0aba8aa2-3911-5c0e-a663-489ce7c5bf16 | textbox | Supervisor Name:
d5aaa5eb-093f-5332-af20-a8b65033877e | checkpoint | Corrective Action Report
70dc6985-b82b-5059-b0e6-8c6051173d6b | textbox | Principal Investigator
82a58a69-0265-5f1b-94f6-eedb3ba93de4 | note | Non-Conformance is:
c318a2db-478b-5c04-a64b-b2793ada7182 | tickbox | Minor
dec3fec8-de3e-5688-8012-e311fd468226 | tickbox | Major
c2aaa82a-4b9a-5ee8-8cff-c4245e5693ea | tickbox | Critical
89423c53-f35f-5f23-b881-00eeec89d495 | textbox | Details of Non-Conformity Identified
c3366d33-37f4-5ff7-89b8-1e481ab4e76f | button | What is the likelihood of Fatality? | Very likely, Likely, Unlikely, Highly Unlikely
5681d23a-0e11-5cb7-9255-8d253cf73465 | button | What is the likelihood of Major Injuries? | Very likely, Likely, Unlikely, Highly Unlikely
0d067ecb-4237-5446-b218-148a310a5b4e | button | What is the likelihood of Minor Injuries? | Very likely, Likely, Unlikely, Highly Unlikely
159d61ec-bd9e-5e62-a7ae-68339204b43a | button | What is the likelihood of Negligble Injuries? | Very likely, Likely, Unlikely, Highly Unlikely
405f5810-c9c4-5474-bbd5-b6e1aa9b4940 | note | Add photo evidence if applicable.
5d294295-86ae-51e1-92b2-e35eee764d2a | checkpoint | Corrective Action Plan
de007f46-3b5d-5c71-bc9e-d42dd29a0b9c | textbox | Describe corrective action
9929de41-ded9-5d69-903e-87a87d518821 | textbox | Is this plan permanent or temporary? | Pernament, Temporary
b6278eed-edba-5296-9de3-eb2587d0c304 | date | What is the proposed completion date?
42c21dbd-9bff-5051-bd1f-f936237b2320 | checkpoint | Signoff
2923664c-ab55-5c48-87d4-1901f7c5ef27 | signoff | BY SIGNING I CONFIRM I HAVE COMPLETED THIS REPORT TO THE BEST OF MY KNOWLEDGE