## Master List Templates
Id | Type | Name | Values | Prompting Name
87dbf723-3c96-462d-bf66-e455fedf5f06 | checklist | ITPS-209 Deluge Commissioning |  | ITPS-209 Deluge Commissioning
8eea13d2-6902-4b58-986a-3c9ed55875f7 | section | Details
7817e386-1f03-4300-b563-044adf24669d | checkpoint | 1. AREAS PROTECTED
0f26962a-7b53-515d-b6b3-22f5c1ae0bbc | note | CIBSE W5.2 State of the System
f6c8df84-0587-588f-a3c6-5fb3d4f3a162 | note | AS2118.3
579b67c5-1d15-5b2f-bfaa-4893198ed8bd | button | Have you ensured areas protected do not exceed 300m/sq per valveset? | Yes, No
69a0a452-eee7-5400-b4c3-1d18d8f626f5 | note | Add Photo
e13b2f41-965d-47fe-b293-b669ac827608 | checkpoint | 2. PRESSURE TEST
b77b8a3d-9734-5cad-b586-4c6c8f11065c | note | CIBSE W5.4.1 Pressure Testing
b5dd3634-0e61-5e2b-a53d-78f9fd902b38 | note | AS2118.1
088ba1e8-65f5-5bab-b519-e8d61450a0f6 | button | Have you completed a pressure test as per ITPS-203 for each deluge system? Note: Where open sprinklers are used ensure all heads are plugged prior to pressure testing. | Yes, No
b4e01887-62fb-5ccb-9378-5e7c57b095e0 | note | Add Photo
1ae11dd8-82e8-4a6a-9c03-a5c7b3ce35dc | checkpoint | 3. EQUIPMENT TESTS - SYSTEM FLUSH
728f2aca-b05d-5e3e-89ac-d818871303ea | note | CIBSE W5.5.2 Flushing Procedure
0851b159-f1c6-5973-977a-cb3586eb9363 | note | AS2118.1
543b63ae-49e1-55ad-b2ff-593c4e0fb7af | note | Complete the following PER valveset and open sprinkler head:
ec26301e-47b5-50d4-972e-b4d24505bd78 | note | 1) Flushing of each open sprinkler head to ensure debris is removed.
9c12745e-e70d-59ce-abb7-ac762de00e99 | note | 2) Setup filtration mesh and water bin at each open head off each system (is there are a large number of heads then separate system by plugging each head).
1903c679-9e94-5e4a-8788-0686e90ca55f | note | 3) Let water flow through pipework onto filtration mesh
29b7d2ca-0540-5357-b85d-d2214726c8f2 | note | 4) Once water is clear from debris shut off water and return system to normal.
79de03cd-4a66-53e9-a70f-2b83859bb91b | note | Take photo per deluge head and record deluge head/s location:
c62db6fb-5360-49e9-b201-c73c7170ea52 | checkpoint | 4. TRANSIT TIME TESTING
c61592c5-2057-5eaf-873e-fdc3c8791cd9 | note | CIBSE W5.6.2 Mechanical Checks: Automatic Control Valves
655f698f-f7f9-5633-8f34-22bd130f6610 | note | AS2118.3 Cl 2.9.1
dca9d2ad-e275-576e-b1fe-5f22044bf59a | note | Complete transit time testing
24da5ecf-6c2c-59bf-886c-e935fd082ba3 | note | Test of the deluge valve to ensure the transit time does not exceed 30s from the valveset to the remote deluge head.
ca7a5928-1b84-55d6-9e89-7a1559ca7660 | note | Add photo of results of transit time.
3a04b841-ac9a-4574-b21d-5e715db680a8 | checkpoint | 5. RETURN TO NORMAL OPERATION
0a93862e-2b51-5279-931c-3b3f60087f9c | note | CIBSE W5.6.2 Mechanical Checks: Automatic Control Valves
83d068c2-f166-5a5a-950f-7dba0ba9b53f | note | Are all open sprinkler heads re-installed where previously plugged?
eb006e7b-ed6a-56f8-8e5a-e7b3b4e19414 | note | Have system valvesets been returned to normal condition (or approved condition where construction still occurring)?
b0c22b87-45d6-5de6-a6c7-d46ea7ff4bc3 | button | Have water filled bins been emptied as per principle contractors requirements? | Yes, No
e3e5c507-051b-5c83-9f98-b95a7e82ef8d | note | Add Photo
f4e4ad9b-dd6e-4b4c-9955-2e35567b6483 | checkpoint-no-value | GM Fire Sign Off
8b042243-f6a4-4082-8826-804c333eb1ce | signoff | GM Fire Sign Off
44ef14c4-0907-4701-b770-28081a0f23f3 | checkpoint-no-value | Principal Contractor Sign Off
85d7a163-ece4-4347-b7b8-2cd6e059e22b | signoff | Principal Contractor Sign Off
287159ad-2b09-44b6-9445-76962cf3474e | checkpoint-no-value | Consultant Sign Off
0531c335-d3e4-4752-a6dc-20e7e02a75ed | signoff | Consultant Sign Off

## Project Checklist Templates
Id | Type | Name | Values | Prompting Name
c5dc7d7c-df99-5ec2-a589-b436df406a75 | checklist | 010SAF_08 SWMS |  | 010SAF_08 SWMS
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
a1c9d02b-1fdf-5e00-bcb7-56aeec761826 | checkpoint | 1. INDUCTION - Attach your signature to confirm you have completed the Principle Contractor's Induction.
d39621b2-57eb-545c-b19b-913b988ebada | signoff | By signing I confirm I have completed the Principal Contractors induction.
93e7a6a9-2417-5a63-a628-5bbbe7c40d86 | checkpoint | 2. ALL STAFF
cbaa5304-d926-5145-abea-643403fc7075 | note | 003G Using Platform Ladders
4c0dcfe7-d8a0-5008-bd8b-d7bc54f1ac2a | note | 004G Inhalation of Respirable Crystalline Silica
1117a6d0-9a4c-5b98-b403-d22a7b5ad3a6 | note | 005G Working at Heights
68979298-f5d8-548e-baec-8741d208ed87 | note | 006G Working at Heights Rescue Plan
1e1b9f0c-d012-59f5-9748-6f1fbc413551 | signoff | By signing I confirm I have read and understood ALL the SWMS documents listed above. I have reviewed these documents onsite with my supervisor and I have signed the hard copy.
d3e29984-ceb2-515c-9230-7a6de1161462 | checkpoint | 3. WET FIRE TECHNICIANS
b4e0d11c-383a-5193-a4d8-06886c652d7b | note | 019T Pressure Testing of Pipework
543f3f86-57b8-5b16-b786-9b1a07dba3bc | note | 020T Sprinkler System and Associated Pump Test
e8307916-4807-52bf-87e5-102669e43c3f | note | 021T Hydrostatic and Flow Testing of Pipework
b9ed5514-0cad-5767-9bc2-787d09c4b91b | note | 022T Fire Rating
3eda0a35-e17c-5ffa-8f13-550cbe45fa28 | note | 023T Fire Alarm and Emergency Warning Systems Testing
6a966737-d7b0-592b-adaf-4fd6c5c1ce28 | note | 024T Commissioning and Testing of Hydrant System and Booster Area
ec96f917-5f59-57b4-b51e-789fed1bc3e7 | signoff | BY SIGNING I CONFIRM I HAVE READ AND UNDERSTOOD ALL THE SWMS DOCUMENTS LISTED ABOVE. I HAVE REVIEWED THESE DOCUMENTS ONSITE WITH MY SUPERVISOR AND I HAVE SIGNED THE HARD COPY.
cb6326be-0982-5008-a0f6-df63d2b7f5a8 | checkpoint | 4. SWMS - DRY FIRE TECHNICIANS
5d11d398-a985-5a6c-aeb6-18ee293dc7c2 | note | 008I Removal of Existing Fire Alarm Systems and Devices
92d6eeb4-8277-5022-83a0-fc89644f8bed | note | 009I Removal of Pipework Fittings
52103321-2daf-5ff5-83c8-2ade86fd2490 | note | 010I Fire Alarm and Warning System Rough-in
8205c84e-07ea-575b-bae8-d3015acb0b02 | note | 011I Fire Alarm and Warning System Fit-off and Installation
884a1c0d-249f-5a69-b8f2-2e03f9760652 | note | 012I Installation of Fire Alarm and Warning System Cabling
61c0ba51-1491-512b-936c-ac2c0f143740 | note | 013I Installation of Pipework and Fittings
c29e79e2-249c-55ba-b869-187073053c35 | note | 014I Installation of Fire Control Panel & Emergency Warning Systems
12c89be3-5c80-51bc-be0f-9f94b3c520b4 | signoff | BY SIGNING I CONFIRM I HAVE READ AND UNDERSTOOD ALL THE SWMS DOCUMENTS LISTED ABOVE. I HAVE REVIEWED THESE DOCUMENTS ONSITE WITH MY SUPERVISOR AND I HAVE SIGNED THE HARD COPY.
8b3b509a-75aa-5bb4-bf99-8e6b8d8e597b | checklist | 010SAF_08 SWMS - AIDP Ripley |  | 010SAF_08 SWMS - AIDP Ripley
8111ace1-1386-5c1f-8290-3df28e3c8d3f | section | Details
a1c9d02b-1fdf-5e00-bcb7-56aeec761826 | checkpoint | 1. INDUCTION - Attach your signature to confirm you have completed the Principle Contractor's Induction.
d39621b2-57eb-545c-b19b-913b988ebada | signoff | By signing I confirm I have completed the Principal Contractors induction.
93e7a6a9-2417-5a63-a628-5bbbe7c40d86 | checkpoint | 2. ALL STAFF
e10de068-098a-54e4-9ca5-367664a0021d | note | GM FIRE 001 Working with Elevated Work Platforms
15671497-ad54-5d32-afa4-04d3f3c4b7b8 | note | GM FIRE 007 Manual Handling
520f9407-d01a-5995-b868-f3de1b60147e | note | GM FIRE 008 Working at Heights
fd6856ce-5fcf-5581-a5f9-83f42ae44906 | note | GM FIRE 051 Using Platform Ladders
98e081c0-c0f2-5647-a6e5-e314220d57ab | note | GM FIRE 060 Inhalation of Respirable Crystalline Silica
1e1b9f0c-d012-59f5-9748-6f1fbc413551 | signoff | By signing I confirm I have read and understood ALL the SWMS documents listed above. I have reviewed these documents onsite with my supervisor and I have signed the hard copy.
d3e29984-ceb2-515c-9230-7a6de1161462 | checkpoint | 3. WET FIRE TECHNICIANS
12aa4e47-69ce-583a-99b5-9ec6063e0430 | note | GM FIRE 009 Pressure Testing of Pipework
68ec500e-a59b-5b0b-b97e-769b3dde3619 | note | GM FIRE 031 Sprinkler System and Associated Pump Test
f9b74e32-e4b3-583e-91f9-e7b3e7f28716 | note | GM FIRE 032 Hydrostatic and Flow Testing of Pipework
ec96f917-5f59-57b4-b51e-789fed1bc3e7 | signoff | BY SIGNING I CONFIRM I HAVE READ AND UNDERSTOOD ALL THE SWMS DOCUMENTS LISTED ABOVE. I HAVE REVIEWED THESE DOCUMENTS ONSITE WITH MY SUPERVISOR AND I HAVE SIGNED THE HARD COPY.
cb6326be-0982-5008-a0f6-df63d2b7f5a8 | checkpoint | 4. SWMS - DRY FIRE TECHNICIANS
96e187af-4508-5796-814d-edf71d430753 | note | GM FIRE 002 Wiring Rough In Minor
edf53965-a075-57b6-9e59-ee1f53c5eea8 | note | GM FIRE 003 Fit Off Fire Alarm System
6d09c463-be7a-5e4e-bf48-f312657a39db | note | GM FIRE 006 Installation of Pipe and Fittings
12c89be3-5c80-51bc-be0f-9f94b3c520b4 | signoff | BY SIGNING I CONFIRM I HAVE READ AND UNDERSTOOD ALL THE SWMS DOCUMENTS LISTED ABOVE. I HAVE REVIEWED THESE DOCUMENTS ONSITE WITH MY SUPERVISOR AND I HAVE SIGNED THE HARD COPY.
9e0279ff-7609-525d-9686-c77d8964a06d | checklist | 010SAF_08 SWMS - ODYSSEY |  | 010SAF_08 SWMS - ODYSSEY
8111ace1-1386-5c1f-8290-3df28e3c8d3f | section | Details
a1c9d02b-1fdf-5e00-bcb7-56aeec761826 | checkpoint | 1. INDUCTION - Attach your signature to confirm you have completed the Principle Contractor's Induction.
d39621b2-57eb-545c-b19b-913b988ebada | signoff | By signing I confirm I have completed the Principal Contractors induction.
93e7a6a9-2417-5a63-a628-5bbbe7c40d86 | checkpoint | 2. ALL STAFF
92bb9af3-0b3c-58d5-af01-dcaa3f0b56f9 | note | GM FIRE 001 Working with Elevated Work Platforms
16ddb0bd-0fc5-58c9-8947-d15f08b642d0 | note | GM FIRE 007 Manual Handling
5ed13011-b997-5fb6-859a-409c9dfd8397 | note | GM FIRE 008 Working at Heights
f233adc5-9ce8-5fa1-ae06-8bb9ae69b156 | note | GM FIRE 049 Working At Heights Rescue Plan
aa74eefc-fb81-571a-bef1-13ae5835d8a4 | note | GM FIRE 051 Using Platform Ladders
5194bef9-5c15-5d9f-861a-2f5c3e600e75 | note | GM FIRE 060 Inhalation of Respirable Crystalline Silica
1e1b9f0c-d012-59f5-9748-6f1fbc413551 | signoff | By signing I confirm I have read and understood ALL the SWMS documents listed above. I have reviewed these documents onsite with my supervisor and I have signed the hard copy.
d3e29984-ceb2-515c-9230-7a6de1161462 | checkpoint | 3. WET FIRE TECHNICIANS
c78fac4a-5239-5f18-9a7a-73a9ec3e70e6 | note | GM FIRE 009 Pressure Testing of Pipework
9f860354-0af2-5f62-ad21-86c78c194f74 | note | GM FIRE 031 Sprinkler System and Associated Pump Test
4fc9cf05-94c2-5778-94c6-e190eb249ca1 | note | GM FIRE 032 Hydrostatic and Flow Testing of Pipework
ec96f917-5f59-57b4-b51e-789fed1bc3e7 | signoff | BY SIGNING I CONFIRM I HAVE READ AND UNDERSTOOD ALL THE SWMS DOCUMENTS LISTED ABOVE. I HAVE REVIEWED THESE DOCUMENTS ONSITE WITH MY SUPERVISOR AND I HAVE SIGNED THE HARD COPY.
cb6326be-0982-5008-a0f6-df63d2b7f5a8 | checkpoint | 4. SWMS - DRY FIRE TECHNICIANS
de972ceb-44c7-57f4-b5da-0399766270af | note | GM FIRE 002 Wiring Rough In Minor
d9228552-ac2e-5900-8cc2-e99ea5a3530a | note | GM FIRE 003 Fit Off Fire Alarm System
9ba02a88-ad12-53e3-98b8-aa4b8159636c | note | GM FIRE 006 Installation of Pipe and Fittings
12c89be3-5c80-51bc-be0f-9f94b3c520b4 | signoff | BY SIGNING I CONFIRM I HAVE READ AND UNDERSTOOD ALL THE SWMS DOCUMENTS LISTED ABOVE. I HAVE REVIEWED THESE DOCUMENTS ONSITE WITH MY SUPERVISOR AND I HAVE SIGNED THE HARD COPY.
02820854-2b26-5b84-8a78-37944efc42b3 | checklist | 010SAF_08 SWMS - Wacol |  | 010SAF_08 SWMS - Wacol
8111ace1-1386-5c1f-8290-3df28e3c8d3f | section | Details
a1c9d02b-1fdf-5e00-bcb7-56aeec761826 | checkpoint | 1. INDUCTION - Attach your signature to confirm you have completed the Principle Contractor's Induction.
d39621b2-57eb-545c-b19b-913b988ebada | signoff | By signing I confirm I have completed the Principal Contractors induction.
93e7a6a9-2417-5a63-a628-5bbbe7c40d86 | checkpoint | 2. ALL STAFF
e5f4983c-79f9-5d2c-aa86-19628d97bca4 | note | GM FIRE 001 Working with Elevated Work Platforms
cb97e826-81ed-5498-a1ce-8026ccaa34ad | note | GM FIRE 007 Manual Handling
3b53ae2d-a214-5919-8837-5ff53a686f11 | note | GM FIRE 008 Working at Heights
ad6ae2e0-0d48-5ac4-ab38-827dbaaad25f | note | GM FIRE 049 Working at Heights Rescue Plan
addf5555-e97e-5e0f-a3ae-e0bdc7cb00d5 | note | GM FIRE 051 Using Platform Ladders
29dc9e88-4534-5045-931b-379ccf48318e | note | GM FIRE 060 Inhalation of Respirable Crystalline Silica
1e1b9f0c-d012-59f5-9748-6f1fbc413551 | signoff | By signing I confirm I have read and understood ALL the SWMS documents listed above. I have reviewed these documents onsite with my supervisor and I have signed the hard copy.
d3e29984-ceb2-515c-9230-7a6de1161462 | checkpoint | 3. WET FIRE TECHNICIANS
f1b0bb87-0310-5266-aeba-e3557c2bc226 | note | GM FIRE 009 Pressure Testing of Pipework
aeb50cbd-b592-59f9-889d-b43dcaf721bd | note | GM FIRE 031 Sprinkler System and Associated Pump Test
afab2c86-7bc8-5186-b3b3-7364105642c4 | note | GM FIRE 032 Hydrostatic and Flow Testing of Pipework
ec96f917-5f59-57b4-b51e-789fed1bc3e7 | signoff | BY SIGNING I CONFIRM I HAVE READ AND UNDERSTOOD ALL THE SWMS DOCUMENTS LISTED ABOVE. I HAVE REVIEWED THESE DOCUMENTS ONSITE WITH MY SUPERVISOR AND I HAVE SIGNED THE HARD COPY.
cb6326be-0982-5008-a0f6-df63d2b7f5a8 | checkpoint | 4. SWMS - DRY FIRE TECHNICIANS
c22eb604-a543-55e8-a9bc-009aa41cad12 | note | GM FIRE 002 Wiring Rough In Minor
f0a3092c-62a3-588f-ae43-2a09e0cbbfe5 | note | GM FIRE 003 Fit Off Fire Alarm System
666707d9-d1a3-5bb1-800c-46a33c145d82 | note | GM FIRE 006 Installation of Pipe and Fittings
12c89be3-5c80-51bc-be0f-9f94b3c520b4 | signoff | BY SIGNING I CONFIRM I HAVE READ AND UNDERSTOOD ALL THE SWMS DOCUMENTS LISTED ABOVE. I HAVE REVIEWED THESE DOCUMENTS ONSITE WITH MY SUPERVISOR AND I HAVE SIGNED THE HARD COPY.
b2707511-d95d-5bd8-9fe5-d7b1aeb787fc | checklist | ASSESS-001 Risk |  | ASSESS-001 Risk
8111ace1-1386-5c1f-8290-3df28e3c8d3f | section | Details
1c657631-910b-56b0-9af0-2d9a539b2537 | checkpoint | Assessment Details
2737dda7-0da8-5350-a990-3c75e95a2887 | note | Use this form to document the risk management process for a single generic hazard.
289128ce-f3c7-536a-8723-4c70cd69bfce | textbox | Work Area:
ae1c42b6-c657-5e4d-9209-2bad75870138 | date | Date of Assessment:
8a53b641-9f68-5989-8d44-4cf1ba1926bb | textbox | Name of Assessor(s):
caa8797b-e08d-52e2-8736-115154cf3705 | textbox | Position(s):
f6ba4789-5bd0-5594-9b1c-010bc61db611 | textbox | Incident Ref. No:
270f8fc3-f5f3-5606-80eb-fc2c80ae4f95 | checkpoint | Hazard Identification
68274c54-05ce-5ce6-86e9-ca232bb22a04 | textbox | Describe the Hazard:
bfd5195d-87aa-5c40-ac91-f0b3a6ea86bc | checkpoint | Risk Assessment
8a96e579-e757-52cd-aac7-c2595bbe497f | textbox | What harm could the hazard cause?
403ab9f6-98ce-5c66-868e-2679ce633da0 | textbox | What is the likelihood of this happening?
5bd4779e-96af-50dd-9f6a-99a1d0cdff0d | textbox | Persons at risk:
e51e81a4-bb38-5350-a32e-178abbc64320 | textbox | Existing control measure:
711cba2d-b126-5349-aaf1-f13b90a0bfe9 | textbox | Consequence:
df1c1362-d4be-51c7-97a0-196760254788 | textbox | Likelihood:
43c9bc56-3d31-5b6b-88d9-be99de6d3ef5 | textbox | Outcome:
32563b01-0feb-5e94-999f-2bc4f92e2c20 | checkpoint | Control Measures
26bc5138-30eb-58e0-9a12-54885a1212d4 | textbox | Elimination:
dc594457-3299-539f-8a27-727188b7aaf7 | textbox | Substitution:
809c790a-705f-5659-94a9-63c4e630e13d | textbox | Isolation:
a9c2b50c-045f-5fd6-bab9-52e76acc984a | textbox | Engineering:
fb6bc54d-9c0a-5f84-8964-f0f46bfd349a | textbox | Administrative or PPE:
e4d91219-de55-500e-ae36-937ccddb4ff0 | textbox | Preferred control option:
71245745-e635-5d28-b0f1-51a28405fcc8 | checkpoint | Implementation
ad41fa7a-48fb-500a-9607-b49a60e29f86 | textbox | Associated activities:
4534f779-9710-5858-94f9-d6ce7fef84be | textbox | Resources Required:
9ea6d005-499c-56f7-974b-aa0ef858cb30 | textbox | Person(s) Responsible:
52b2f865-6543-582a-bf9f-e8a527fb4846 | date | Scheduled Review Date:
7717528b-ba68-53aa-a357-393c48e0a282 | signoff | Signature
367c214b-499a-50a2-88bd-3efe1f2b2b50 | checklist | ASSESS-002 Manual Tasks Risk |  | ASSESS-002 Manual Tasks Risk
8111ace1-1386-5c1f-8290-3df28e3c8d3f | section | Details
1c657631-910b-56b0-9af0-2d9a539b2537 | checkpoint | Assessment Details
490c172b-529e-535d-95e8-e5ad2fb72267 | note | This assessment identifies how to manage the risks associated with hazardous manual tasks and control the risks of workers being affected by musculoskeletal disorders as per the code of practice under section 274 of the Work Health and Safety Act 2011 (the WHS Act). Use this form to help identify and manage risks of hazardous manual tasks.
ab900e56-77e5-5805-9997-0d1dfe555ee7 | date | Date of Assessment:
2aec5e0b-8872-5011-9421-48854f44e051 | textbox | Name of Assessor(s):
5e55219b-583f-56f3-bfdd-5dea292dd57c | textbox | Position(s):
e9a03c42-ce41-510c-81f9-6726eabba5a7 | textbox | Incident Ref. No:
58267725-2c6f-55fe-83b6-0579eb36ea4e | checkpoint | STEP 1 What is the Manual Task?
d8a88177-159b-582e-9b31-2a129c8d8287 | textbox | Relevant worker(s) to consult:
e232891b-c7c3-5c4f-8710-9e25a80167ba | textbox | Name of task or activity:
037244fe-8b0c-5516-b956-b112323b670e | textbox | Location where task occurs:
7ad89bb6-a5b4-5328-a0e3-bc256710943c | textbox | Who performs the task:
d3180965-d2b6-5838-8138-4fd1533da7f7 | textbox | General Description:
bf2b5766-0a58-58a5-9304-cb818f3230f5 | checkpoint | STEP 2 Is the Manual Task hazardous?
aab5e53a-b884-5772-9678-39989f5669f7 | note | Hazardous manual tasks can result in musculoskeletal disorders (MSDs) such as sprains or strains. Work through the following to determine which postures, movements and forces of the task pose a risk.
aea3be1b-890b-5d5c-a299-8bddf9f945cf | note | 1. Does the task involve any of the following risk factors?
2f77bbb9-7a7b-580a-810e-83fa27e840a9 | button | Repetitive movement | Yes, No
74ead498-3c45-5e04-ad4b-502bba13a14c | button | Sustained or awkward postures | Yes, No
fb28a310-8cb2-561e-bf72-d57a019c6402 | button | Repetitive or sustained forces | Yes, No
34214a95-3841-51a1-bf4e-63eb1481bc91 | note | 2. Does the task occur over a long time?
6c8da810-d8ee-5e6c-b376-44d52748c8ed | button | More than a total of two hours over a whole shift? | Yes, No
82340f3d-6d46-59a9-861a-14429e99d1e2 | button | Continuously for more than 30 mins? | Yes, No
9c3dad32-e3f8-5cd9-b455-e6d7311e5e10 | button | 3. Does the task occur over a long time? | Yes, No
a7af4a9a-52ff-5f1e-8dfd-0ce660580656 | button | 4. Does the task involve vibration? | Yes, No
125544aa-735e-506b-a178-319eeb48e499 | note | 5. Is there a Risk? The task involves a risk of MSDs (e.g. sprain and strain) if you answered ‘yes’ to either:
b5eda523-6c02-5219-b69a-213dd43893f0 | tickbox | Question 1 and 2 (above)
1b6414b1-311c-5add-b3eb-36ffeffa0a86 | tickbox | Question 3 (above)
56e36077-34d7-5a5e-aed9-15ce5695b159 | tickbox | Question 4 (above)
0cd16434-4ea6-590f-a9d8-22c8120046dc | note | If you ticked anything in question in Question 5, continue to Step 3.
08ad31b6-03ac-561f-942e-c8e3166bd958 | note | Additionally, if you answered ‘Yes’ to Question 4 the task may be a risk and will require further investigation.
43bb97fe-9131-5be9-be82-2660ffb39a19 | checkpoint | STEP 3 - What is the source of the risk?
8d1e9cf7-f475-53a5-90ab-16d167860176 | note | These are the things that are causing the risk and may be changed to eliminate or minimise the risk.
b73be6fb-033a-5d07-b7fe-3c85624d7282 | tickbox | Work area design and layout: workspace available; design of workstation, furniture and equipment.
33e5a4bb-1125-5f9c-9b67-c0ca918b214f | tickbox | The nature, size, weight or number of things handled in performing the manual task.
4b2e8d21-43fb-5539-8e97-b79a576d9999 | tickbox | Systems of work (e.g. pace and flow of work; resources available; maintenance).
68abb300-f394-5a9a-9ce0-557ece1da760 | tickbox | The environment in which the manual task is performed (e.g. flooring; obstructions; lighting; hot/cold/humid environments).
75306ffa-8cad-5fb5-8c60-4770efcfbc4e | checkpoint | STEP 4 - How do I control the risk?
398a9051-c14e-516e-9e62-3cf13abe5e71 | button | Can the task be eliminated? | Yes, No
368f597c-006e-5a4c-9622-48d5c1e579a3 | button | Can you change what is causing the risk (the source)? (e.g. change the work area; alter the size of loads; use mechanical aids; manage environmental conditions; use adjustable equipment; implement preventative maintenance program). | Yes, No
9bffc518-e600-563f-83ee-b46609ceeb6f | textbox | If 'Yes', provide detail:
c4d0d777-07a6-5a79-8614-ff5925bd7cd2 | button | Is training needed to support the control measures? (Training needs to be task specific, noting that training in lifting techniques is not effective as a sole or primary means to control the risk of MSDs.) | Yes, No
6a5b0a4b-fa33-5a1b-a349-4b1922bd8324 | textbox | If 'Yes', provide detail:
249717bf-db57-5fb4-b61b-9f7678983512 | checkpoint | Implementing Controls
2af5e740-8b0e-52a2-a6b3-9e5ba22dcc64 | textbox | Name of Responsible Person:
5fa58af3-1606-5f22-bd13-ee000d4bac34 | button | Responsible for: | Approving, Implementing
e1b9ffd7-6efd-5f3c-9c53-1acc8e453440 | textbox | Name of Responsible Person:
59827434-9895-5505-8e76-8e811858ed18 | button | Responsible for: | Approving, Implementing
9cd466bd-5a1e-5a06-acf9-a0f373c775d6 | textbox | Name of Responsible Person:
c475ab63-1681-519d-b90f-20724591aaa6 | button | Responsible for: | Approving, Implementing
6052a159-cbde-544d-979f-ab6b78557e36 | textbox | Name of Responsible Person:
60efcd64-d526-5420-aed2-141bb0678c2a | button | Responsible for: | Approving, Implementing
89334ebf-57ec-5f05-8b4e-750b91a0dc81 | signoff | BY SIGNING I CONFIRM I AM AWARE OF MY RESPONSIBILITIES AS OUTLINED IN THIS RISK ASSESSMENT
1ac85fbd-c1e0-52f8-a16f-a7d8e29a8854 | checkpoint | STEP 5 - Review the Controls
05cc12f9-13ba-5a46-851b-3ffa3889999b | date | Evaluated on(date):
aa933b5d-a414-56fb-9593-349817c6cb58 | textbox | Name of Assessor(s):
de2d6041-2451-56c8-a1b0-8123bb1f5ec2 | button | Consultation undertaken with relevant workers and others? | Yes, No
09a25e1d-447b-5703-a1a7-cf4cb0ccdd3f | button | Have any other risks been created by the controls? | Yes, No
62630e4b-1b37-507c-a268-7018937bb888 | button | Have the controls implemented reduced the risks? | Yes, No
8363f20e-bbe2-58a1-bdf2-6d6ec2000b64 | button | Can further controls be implemented to minimise the risk? | Yes, No
a80bd9a1-e2eb-5c96-ab03-28f50004f41c | checklist | ASSESS-003 Hazardous Chemical/ Dangerous Goods Risk Assessment |  | ASSESS-003 Hazardous Chemical/ Dangerous Goods Risk Assessment
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
8111ace1-1386-5c1f-8290-3df28e3c8d3f | checkpoint | Details
d64f9e12-a8d1-572d-b52d-a264f7fe2c21 | textbox | Hazardous Chemical (product name):
61131b33-b900-5454-a839-bacf04fddc09 | textbox | Hazardous Chemical Reg Item No:
fa30c358-8185-53ab-a3e5-7a89d93b620c | textbox | Use:
eec44df0-883b-5db0-a668-e111f5465eb4 | checkpoint | Nature of Hazard:
c3865074-534e-5e92-8183-abb02d5e0f45 | tickbox | Toxic (Poisonous)
73380fb3-2daa-58dd-a27c-fd92c28cc19e | button | Route of Exposure: | Eyes, Skin, Inhalation, Ingestion
1a4cca2b-c7c6-582e-8872-a69b23f4f996 | tickbox | Carcinogenic (Cancerous)
8448ff25-8567-56c9-bc8d-c65b7be067c3 | button | Route of Exposure: | Eyes, Skin, Inhalation, Ingestion
fbc7d650-c863-5438-88c0-b6801548cf7f | tickbox | Teratogen (Harmful substance that could affect abnormal prenatal development)
0a973027-0604-5fd1-8e33-1f6843068a0d | button | Route of Exposure: | Eyes, Skin, Inhalation, Ingestion
0c23b16f-1a98-579a-a5cd-b10341a3c93e | tickbox | Sensitiser (Reaction to an antigen, such as pollen)
26e95726-3d59-5326-a5cf-7952dba23427 | button | Route of Exposure: | Eyes, Skin, Inhalation, Ingestion
42fedfa0-4abe-5559-9a9d-3293d48b513b | tickbox | Mutagenic (Capable of mutating DNA, such as radiation)
6b6b9d2f-ae5d-51b8-a33a-bc4e0582efd9 | button | Route of Exposure: | Eyes, Skin, Inhalation, Ingestion
72b4fd57-ee4c-528b-9346-3cc09a71a26c | tickbox | Irritant (Inflammation of the skin, eye or respiratory system)
65ff1186-86dc-5bc0-9441-f7cda9142a6b | button | Route of Exposure: | Eyes, Skin, Inhalation, Ingestion
1488ffce-4246-526d-8862-2701ca976c59 | tickbox | Flammability (The ease of which a substance will ignite, causing fire or combustion)
fb8d25c9-0361-5fc2-992a-c8ac54018ced | button | Route of Exposure: | Eyes, Skin, Inhalation, Ingestion
c5299fc2-0138-5c3e-9df0-fdb6f6a23c55 | checkpoint | Risk of Injury
d5a297e5-61f4-58ff-b1b1-c8ca2eadf8ba | button | Risk of Acute (Short term) Injury: | High, Medium, Low
39a06ae2-da96-5801-a080-9de8bb9bd02a | button | Risk of Chronic (long term) Injury: | High, Medium, Low
6adca422-e108-5631-9168-8f36735799d3 | checkpoint | Controls and Requirements
dff33aea-d864-5296-85a7-3c3d89a4dbd8 | textbox | Control Measures to reduce exposure i.e. change to a safer product, ventilate area, (P.P.E.):
89612ad9-31eb-5b1b-b34f-25be2eacadf9 | textbox | First Aid Requirements and Storage Requirements:
42c21dbd-9bff-5051-bd1f-f936237b2320 | checkpoint | Signoff
f6e6ad58-755a-5ec6-ac1a-b3db6c24bfc3 | signoff | The persons listed below have been consulted in this risk assessment, understand the hazards associated and agree to use the control measures identified above to carry out the works safely and in a manner which protects themselves, others and the environment.
7a2e19d4-a232-5ccb-9e9b-f9c2132fc0a5 | checkpoint | Assessor Signoff
d0aabc79-7a66-528f-976e-31f5a7db0456 | signoff | BY SINGING I CONFIRM I WAS RESPONSIBLE FOR CONDUCTING THIS ASSESSMENT
2ea687ee-acea-5b17-843b-86fee551733b | checklist | ASSESS-004 Plant Risk |  | ASSESS-004 Plant Risk
8111ace1-1386-5c1f-8290-3df28e3c8d3f | section | Details
5011c755-395d-598c-bc65-ea69efabb143 | checkpoint | 1. Competent Peron(s)
9a9b3958-e0c2-5268-aaf5-3e077666511d | note | This familiarisation checklist should be completed by a Site Supervisor or Site Foreman to verify that the workers involved in the operation of Plant Equipment/ Mobile Elevated Work Platforms (MEWP) can demonstrate their ability to understand and operate the MEWP functions in accordance with the manufacturers operating manual. This familiarisation checklist must be verified by a competent person who holds the equivalent licence/ ticket required for the type of Plant Equipment/ MEWP to be operated (e.g. Boom lift/ Scissor lift)
421913a6-005a-5bfe-b708-440417ab5d27 | textbox | Your Name:
3d439d05-c639-5ad1-ab00-1ba3920a9817 | note | Your Licences / Tickets:
11d866e9-f084-5b26-843b-254282a6c100 | tickbox | WP High Risk
5e54de38-508f-50a3-ab0e-e0c8679f8a1a | tickbox | Boom Lift
ea68eb1f-321e-5e02-a622-a3508facf2c4 | tickbox | Scissor Lift
f33fdee4-d517-591b-8e36-9e836bd3d6e1 | tickbox | Vertical Lift
81a98fa0-20d0-5274-9330-e937fa7e313e | tickbox | Other
c7f781a4-a73b-5d49-9565-093b617aba7c | textbox | If 'Other" please specify:
c06fe721-a6e8-585c-ad93-6752e11d8265 | checkpoint | 2. Plant/ MEWP Details
90819d9c-8041-58fa-925f-ff4173355404 | textbox | Make and Model:
72d506d5-4e56-5ec5-8c93-b3f7d99536ce | textbox | Type (e.g. BL>11m, BL<11m, SL, VL):
6b0e5610-cf37-5886-aa78-b8bc2aea3ba0 | checkpoint | 3. Employee Competency
283fe821-9465-5997-884a-e53b824195ee | textbox | Name:
fe2792fe-88fa-5cc7-822e-859e2506a067 | note | Role:
0cae945b-d039-5202-9dc1-c1f31d837e92 | tickbox | Operator
6e501ba1-23dc-5885-a740-dcb403ba9400 | tickbox | Spotter
ab7d246c-0564-52d1-8da5-f8432c1bffa9 | note | Licences/Tickets Held:
51471574-24e5-57a8-9d87-1ad1fd20269c | tickbox | WP High Risk
c8680c7b-abeb-52c1-b43d-450b4de8fcf8 | tickbox | Boom Lift
fe824038-2fe3-59bc-8a08-d3570fef7ac3 | tickbox | Scissor Lift
52a4e5af-5299-5c5e-a60e-0e296500ce88 | tickbox | Vertical Lift
06ebc66d-119e-58a4-8c6d-3668b83861ad | checkpoint | 4. Employee Competency
73351cee-c380-5c96-b1c7-82c4bdc7793a | textbox | Name:
47b977ce-db23-5091-9181-d12522014aeb | note | Role:
4115b285-0dab-509b-b78c-6b3fe3068366 | tickbox | Operator
af2cc185-f772-5a03-969d-bf46bb86577a | tickbox | Spotter
ffc930ab-59a8-5e18-afb0-da251ac3661c | note | Licences/Tickets Held:
eee9b880-b7b4-5f05-9f45-44bc188ceb0a | tickbox | WP High Risk
32033229-269f-5e26-9a26-6024c4bced51 | tickbox | Boom Lift
8f37f26d-6637-5101-b032-1e34a248d86d | tickbox | Scissor Lift
47dfed81-5cfe-5cd8-84b7-d113b35adc16 | tickbox | Vertical Lift
3ef8e758-7384-5d13-8fa3-292a5f04a9d8 | checkpoint | 5. Employee Competency
70f78733-b0b1-5c22-a6ee-c84eb8cd5382 | textbox | Name:
e47caed1-7c4a-5091-84e9-87591d2a2fb9 | note | Role:
c84eba4f-6301-5058-96b5-2fdca6bc206c | tickbox | Operator
7f109594-56af-5ef1-b67b-b1e88673aa41 | tickbox | Spotter
5f1cc387-8b6d-5d5f-a08a-fb01a2b0d557 | note | Licences/Tickets Held:
b4dc56cf-627f-5e84-92e2-81be2c729e0f | tickbox | WP High Risk
ad5efe5c-cc66-52e7-9f33-9be813518ded | tickbox | Boom Lift
f3db69b0-11a3-5ff7-ae41-5bea8ceb8ed8 | tickbox | Scissor Lift
22049df2-afa1-534d-82b8-767d6e6e2636 | tickbox | Vertical Lift
0db35e59-5266-54bd-bc6b-7ababdb43cef | checkpoint | 6. Declaration (to be completed by competent peron(s) noted in Section 1.
f2766483-04cb-5da7-890e-dcc4e17777bd | button | All 'Operators' hold the appropriate licence/ ticket for Plant/ MEWP | Yes, No
5031b2eb-1c9c-55f6-a5cc-e63e9cfc76b5 | button | All 'Operators' understand the operational controls and emergency functions | Yes, No
12f920b1-81aa-59e1-a68c-e7269492885e | button | All 'Operators' are aware of the logbook and pre-start requirements | Yes, No
e2c18959-6e5b-562c-b9a5-4dac9408d32a | button | All Ground Support understand the emergency functions | Yes, No
925a0673-c38f-5fb4-b952-0246d6d57ff0 | button | All GM Fire employees on site have participated in an emergency drill | Yes, No
58559eb2-25f7-513c-9294-7fac027dbbb9 | button | All GM Fire employees have signed onto applicable SWMS | Yes, No
9899d9ec-b306-5aed-bbc5-b1347ea6537c | signoff | BY SIGNING I CONFIRM I HAVE ALL PERSON(S) LISTED ARE COMPETENT TO OPERATE THE LISTED PLANT/ MEWP ON THIS SITE.
298a1679-3b4d-50ad-97f7-8d79b298e664 | checklist | ASSESS-005 Confined Spaces Risk |  | ASSESS-005 Confined Spaces Risk
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
8111ace1-1386-5c1f-8290-3df28e3c8d3f | checkpoint | Details
130a7940-3935-5253-8ae5-82b1055dfd14 | note | Use this form to document the risk management process for a Confined Space.
5ca532df-2d29-581b-82a2-afa02f372b39 | date | Date of Assessment:
efa51e91-77f1-5628-a232-99f3c48b4020 | textbox | Name of Assessor(s):
faca6a3e-c6b2-569d-a658-055a4b1164db | textbox | Position(s):
270f8fc3-f5f3-5606-80eb-fc2c80ae4f95 | checkpoint | Hazard Identification
fad4c4f5-7e3d-5c24-add3-b36005494c89 | textbox | What Hazard/ Risk is associated with the task?
3caf8aa5-c5e5-5180-abaa-0a9a28dd8bda | textbox | Planned control measure to remove/ minimize hazards/ risks
80dd6f73-8abb-5f6e-b96d-a003c0862604 | textbox | What Hazard/ Risk is associated with the task?
d9d61964-0aa1-59dd-b417-a00130fda9f1 | textbox | Planned control measure to remove/ minimize hazards/ risks
2d8973bd-68de-5078-a649-d84eb5324735 | textbox | What Hazard/ Risk is associated with the task?
ad6a71eb-3672-50d8-bb44-58040405bb6f | textbox | Planned control measure to remove/ minimize hazards/ risks
beed0557-db27-53c9-b4fc-4106fb1a89e1 | textbox | What Hazard/ Risk is associated with the task?
e51d3210-35ea-5cdb-87eb-76a364960c2e | textbox | Planned control measure to remove/ minimize hazards/ risks
d291aadf-b45c-58c8-9abb-102b9ccd401c | textbox | What Hazard/ Risk is associated with the task?
9dcad28e-a5ed-5bcf-8b09-877284ed48f2 | textbox | Planned control measure to remove/ minimize hazards/ risks
520f3973-2a3e-554c-9da3-fcd0d6905a7f | checkpoint | Review
a5bad4ff-4c84-55b4-979f-864d1d649e12 | button | Does the Risk Assessment Identify that confined space work is involved? | Yes, No
ba7cd854-f374-50a0-bfdb-ccbcc4196d6d | note | If YES the Confined Space Work Permit MUST be completed
6cec88c8-2282-5790-9d56-16331bfb102c | note | NOTE: EMERGENCY & RESCUE PROCEDURE: Where an accident occurs which requires that an emergency rescue be attempted, the standby/ rescue person is to immediately contact EMERGENCY SERVICES on 000 for assistance.
7a2e19d4-a232-5ccb-9e9b-f9c2132fc0a5 | checkpoint | Assessor Signoff
a9d78622-1c5c-5ef7-96e7-636ddd7d9229 | date | Scheduled review date:
946f9c2d-1950-57b6-981a-43e43c738227 | signoff | BY SINGING I CONFIRM I WAS RESPONSIBLE FOR CONDUCTING THIS ASSESSMENT.
2e9f4f5f-73ce-5181-a4d3-ab809667db17 | checklist | ASSESS-006 Job Safety |  | ASSESS-006 Job Safety
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
5e25be48-4354-51fa-a917-1881487cb8a0 | checkpoint | Client Details
bf83fa46-22f9-52ba-80ce-a37529230034 | textbox | Client: i.e. Principal Contractor
589f8e09-feec-5403-88ff-194eb59adbe6 | textbox | Client Contact Name: Responsible Person(s)
eaeb3e60-e653-5a94-92f4-d3b629923fc7 | textbox | Client Contact Phone:
a7aa3b37-be9e-5945-8920-278208dee51a | textbox | Client Contact Email:
bad8a559-d874-55eb-a218-4243f23c1f05 | checkpoint | Job Safety Analysis Details
e0472b52-555b-578f-9b0d-10ca185460a1 | textbox | Work Activity:
7755fbc5-1db4-5c6a-9eb9-1a50b1b4f39b | textbox | Location:
9c4ccf3a-dc0f-5789-a749-3b3c139a461c | textbox | Who is involved in the activity?
3ff18e9a-8a0b-505d-a5ad-334bf588fe4f | textbox | Plant and Equipment used:
8fc90058-6ecc-5824-be76-439a2920b450 | textbox | Maintenance checks required:
503c2e9e-0cf2-5780-83bb-17e8b8e8cd20 | textbox | Tools used:
b474c44b-9350-5cb0-88c6-309a83224ea6 | textbox | Materials used:
3a661dd6-8651-5a9a-abd9-54ae562e3b84 | textbox | PPE used:
62d2facf-fd51-5926-9608-32ef95c4748f | textbox | Certificates, permits and/approvals required:
538da0a8-b2aa-517d-b88c-85e029139a90 | textbox | Relevant legislation, codes, standard MSDs etc. applicable to this activity
f948400d-3b6d-5037-a27e-a1da8d06232a | signoff | This JSA has been authorized by:
df68f526-1e94-59d2-832e-1b4bc4eb113c | checkpoint | Job Safety Assessment
ab741e71-0e49-5969-b5c0-f1c3f4db8a43 | note | Refer to the attached Risk Ratings table to complete the following..
3e4c920e-6e44-5089-aebe-027b3d41e2f5 | textbox | Job Step Details:
76039bd0-3c61-57c9-8744-263d7e249743 | textbox | Potential Hazards:
ff90c12e-9264-5ec9-bcfb-3809ecc00f80 | textbox | Name of Person(s) Responsible for work:
079e5ac5-4175-5234-8d36-7fe10d966313 | button | Risk Rating: | Low, Moderate, High, Critical, Catastrophic
f64d3e6b-5e0f-5c3b-a0b3-1c3a80d8b0fe | button | How to Control Risks: | Eliminate, Substitute, Engineering, Administrative, PPE
c8538ff2-0ff0-578b-aeef-883e852d2656 | textbox | Job Step Details:
6fa25bbc-560c-5b99-a629-cdc256177219 | textbox | Potential Hazards:
305af7ce-90b2-53c3-ac23-31c07c5e76a9 | textbox | Name of Person(s) Responsible for work:
f921fa6f-7fcd-5f5e-97a3-4c987bd12dff | button | Risk Rating: | Low, Moderate, High, Critical, Catastrophic
278e01f2-0559-54a4-8c20-ae06c6fb8a94 | button | How to Control Risks: | Eliminate, Substitute, Engineering, Administrative, PPE
8c34d454-01a5-5eca-9ee8-bfbf2fc6de79 | textbox | Job Step Details:
7bf50a7e-e54a-51b1-a340-1e56e1576981 | textbox | Potential Hazards:
e422d336-150e-51a7-94cd-4ab59a8286a4 | textbox | Name of Person(s) Responsible for work:
e2e1fd0c-62ed-50c9-b80d-fd9141eae82f | button | Risk Rating: | Low, Moderate, High, Critical, Catastrophic
bfcca39f-b561-5f72-9ea8-3ee3779e362a | button | How to Control Risks: | Eliminate, Substitute, Engineering, Administrative, PPE
42c21dbd-9bff-5051-bd1f-f936237b2320 | checkpoint | Signoff
9c249912-b3c0-5116-b8ec-aba0ea058e1e | signoff | This job safety analysis has been developed through consultation with our employees and has been read, understood and signed by all employees undertaking the works:
930a3e43-5647-50d1-87f2-966cce2343da | checklist | CHECK-002 Site Inspection |  | CHECK-002 Site Inspection
7604d349-3c9d-59ec-8769-a0cfe4110d87 | section | 1. Administrative, training and risk management requirements
b646b6a2-68d2-5b04-925e-0e13a9bb914a | checkpoint | 1.1 - So far as reasonably practicable, all workers carrying out construction work on the project have been made aware of the content of the WHS management plan, including any updates, and their right to inspect the plan.
6ba63d7d-3b3f-5c31-9434-f4939b574a87 | checkpoint | 1.2 - All workers carrying out construction work have received the general construction induction training.
b9691151-2ecd-5ee2-8ec8-b533204f2fd9 | checkpoint | 1.3 - Workers have been informed of the site-specific health and safety rules.
60ac4aca-7460-564d-ba14-2d3d98bfd234 | checkpoint | 1.4 - Suitable and adequate information, training, and instruction has been provided to workers in relation to work they are carrying out.
66bab419-a393-57f6-9c97-758d79271510 | checkpoint | 1.5 - Personal protective equipment (PPE) is being worn in accordance with the projects requirements.
2ab82d7a-cc3c-56a0-a89c-ba9e4252acc3 | section | 2. Safe work method statements
c145e282-9bf0-58ac-8a85-4500302a4c6e | checkpoint | 2.1 - A safe work method statement (SWMS) has been prepared for each high risk construction work activity that is underway or about to commence.
fe929405-eae8-5ca8-8783-fd58e2de54ac | checkpoint | 2.2 - Workers have reviewed and signed off on the relevant SWMS
7934e80d-dec5-5f41-be0b-42bbfcdd01e2 | checkpoint | 2.3 - High risk construction work activities are being carried out in accordance with the relevant SWMS.
8f0ef03e-318f-5cf3-b827-93b54c1df497 | section | 3. The work environment
e6018bbf-c8f1-5f07-b149-1bf83ae3ef97 | checkpoint | 3.1 - The work environment has been maintained such that it is clean and in a safe condition.
79bdc24c-1c00-5acf-983d-ebaa5ce5fad4 | checkpoint | 3.2 - Work areas are clearly identified and separated as necessary so that work can be undertaken safely.
1825c9fa-24bb-50ad-8b3b-a1e424e13ba5 | checkpoint | 3.3 - Lighting at the workplace is sufficient to allow:
f8272eb3-01c5-5337-a307-f72286a48c32 | note | ○ Each worker to carry out work without risk to health and safety.
1be19c4f-a82e-522b-98e5-e5aa656efb60 | note | ○ People to move within the workplace without risk to health and safety.
aef67d61-2c29-5ed8-9db6-bcf3ceacb0db | note | ○ Safe evacuation in an emergency.
e6860137-88a0-51f5-bab0-d6de14d63cb6 | checkpoint | 3.4 - The workplace has sufficient ventilation to enable workers to carry out work without risk to health and safety.
4ff74d5f-cec6-5c19-bd25-e6838e8f1c56 | checkpoint | 3.5 - The entries, exits, and access ways in the workplace are kept clean and clear of materials and waste.
48066b16-7c21-5768-945d-e4a5cf766b0b | checkpoint | 3.6 - A safe system has been implemented for the collection, storage, and disposal of excess or waste materials.
0b615730-4ffb-51cd-bfb3-02fcfc4435d7 | checkpoint | 3.7 - Sufficient area has been allocated to safely store materials or plant for the construction work.
8dca0770-d2f9-575c-9e8a-bc6b57a4f871 | checkpoint | 3.8 - Protruding objects that are a hazard have been made safe (e.g. exposed nails, vertical reinforcing steel).
b201c421-5b2c-5c48-9704-05cf6113c44a | checkpoint | 3.9 - Adequate facilities have been provided for workers, including toilets, drinking water, washing facilities, and eating facilities.
c51929b0-8776-5f5d-9a2c-3ebcffee0dad | checkpoint | 3.10 - First aid equipment has been provided for the workplace and is accessible to each worker.
18a4e767-8b1d-5672-a5a5-274690a036b4 | section | 4. Confined spaces
2825d9b2-da10-596a-9ce0-b40fcc56a1cc | checkpoint | 4.1 - For each hazard associated with a confined space, a competent person completed ASSES-05 Confined Spaces Risk.
0a584ab9-a5b3-52a1-b882-f4b9709cc8db | checkpoint | 4.2 - Prior to commencing the works, FORM-003 Entry Permit Confined Spaces has been completed and approved.
89309c03-7f35-5362-a583-36791c1dba8a | checkpoint | 4.3 - Appropriate signage has been erected for all confined spaces.
d0a6d31c-65a4-5bf4-bc31-672ba9175665 | checkpoint | 4.4 - First aid procedures and rescue procedures to be followed in accordance with POLICY-006 Confined Spaces Rescue in the event of an emergency in a confined space have been developed and practiced to ensure they are efficient and effective.
ded5ed0a-e444-5b8a-bb7f-fdbe7f8fb660 | checkpoint | 4.5 - Workers required to work in or around a confined space have been provided with information, instruction, and training in relation to the:
bed85791-cdf2-5734-99e5-42eabe40f212 | note | ○ Nature of all hazards relating to a confined space
be7ccc94-3134-5b95-8b20-72fefb415b43 | note | ○ Need for, and the appropriate use of, control measures associated with those hazards
b110c5ef-6275-5bf5-a856-5a63e44d03ea | note | ○ Selection, fit, use, wearing, testing, storage, and maintenance of any personal protective equipment
1a99ce71-7f11-5eeb-a21b-b350ded8d8c3 | note | ○ Contents of any confined space entry permits that may be issued
b0c02c77-ff62-5a00-8a01-e40663b3102c | note | ○ Emergency procedures.
e81da6f2-b7fb-5d0c-920d-ac0985916342 | section | 5. Working at heights
e2a6047c-3469-57d7-a1ee-63a6d2ce1e6a | checkpoint | 5.1 - A SWMS is available for all high risk construction work that involves a risk of a person falling more than 2m that has commenced or is about to commence.
c2fb3d08-8253-53dc-a912-7762ad36b3c3 | checkpoint | 5.2 - Where a risk of fall of less than 2m exists:
15a0bb70-25a2-55ce-8391-f9705261ae79 | note | ○ Each hazard that may result in a fall or cause death or injury if a person were to fall has been identified
098e60b1-4049-5b81-9802-dc44b50477cb | note | ○ The risk of death or injury that may result because of the hazard has been assessed
d8e17ce6-5b0d-5d71-adcb-c9012baa2fa9 | note | ○ Any control measures necessary to prevent, or minimise the level of, exposure to the risk is used.
98b57a94-c6a8-50d7-bb1c-2783d46d3990 | checkpoint | 5.3 - Where a risk of fall of at least 2m exists, control measures have been used which:
df712649-e072-54fe-b908-fe63884b915b | note | ○ Prevent a person falling any distance
28993959-da47-509e-a241-bb45845a83ee | note | ○ If prevention is not practicable:
55b684af-87ab-5194-82b6-3e644dbb1a7b | note | – arrest a person’s fall
7575aa24-7d52-5200-8719-e639552c447b | note | – prevent or minimise the risk of death or injury to a person when the fall is arrested.
6a7044d6-a81e-5157-bf4a-f5cbc210f31d | checkpoint | 5.4 - Ladders are not used to support a weight greater than that for which they have been designed.
d81daed7-0057-50a6-9fe9-8aece2cab495 | checkpoint | 5.5 - Ladders are used where the:
d8458251-f7d1-554a-bcc3-372ab76e7d8a | note | ○ Bottom of the ladder is on a stable surface
c8fdd838-d4e2-5652-83e9-9bc5b3b6145b | note | ○ Rungs of the ladder are approximately level.
3f3316e4-f01d-5a03-a2af-4637d940f52b | checkpoint | 5.6 - Scaffolding has been erected by appropriately licensed workers.
e8760cac-e387-5620-9ab6-470830ad9fb6 | checkpoint | 5.7 - Scaffolding is or has been erected and/or dismantled so as to eliminate or minimise the risk of falling at least 2m to people carrying out the work, in accordance with the regulations
faed25a7-0d74-5c49-bf12-7d35d9c1c221 | checkpoint | 5.8 - Safe access to and egress from scaffold has been provided during erection, use, and dismantling.
06596e0e-a7d6-5ec1-ae87-b458bc352bec | checkpoint | 5.9 - Written confirmation from a competent person stating that the construction of a particular scaffold has been completed, has been obtained prior to the use of that particular scaffold.
a1cf7634-7b7a-503b-98b6-a44b1401c2de | checkpoint | 5.10 - REGISTER-007 Plant and Equipment is up to date and includes all mobile plant in use.
92665bac-aa8b-572e-82c0-08a5392f0bfe | checkpoint | 5.11 - CHECK-004 Pre-Start Plant and Equipment has been completed for all mobile plant in use on delivery to site.
3dd77402-8a87-529b-8183-9c072abbce8a | checkpoint | 5.12 - CHECK-005 Regular Plant and Equipment has been completed for all mobile plant prior to commencing operation of the plant that day.
26a08f78-359d-5909-8059-66675eee2c23 | checkpoint | 5.13 - Mobile plant operators hold the appropriate high risk work licence.
23b709bb-1735-5ef2-90a2-edf28c5eaf62 | checkpoint | 5.14 - Where there is a possibility of powered mobile plant colliding with pedestrians or other powered mobile plant, a warning device has been fitted.
a556791d-1316-51ef-8b5c-74f5158d5808 | section | 6. Electrical
b2dcd8ef-695d-5a07-a1c9-d7a4c42cb637 | checkpoint | 6.1 - Electrical leads are arranged to avoid damage.
d2a5d551-016e-5c24-aaed-9a6546efb65d | checkpoint | 6.2 - Electrical equipment has been inspected, testing, and tagged in accordance with AS/NZS 3012 Electrical installations – Construction and demolition sites.
a3dea501-b49e-52a0-b686-be4f3b199e32 | section | 7. Hazardous substances and dangerous goods
28f006f5-6133-536c-83c5-e5fd046e9474 | checkpoint | 7.1 - All hazardous chemicals that are used, handled, or stored at the workplace are correctly labelled.
d9654d68-e223-5e2a-a924-23ef86d304da | checkpoint | 7.2 - A safety data sheet (SDS) exists and is available for inspection for each hazardous chemical used, handled, or stored at the workplace.
569fad8c-3f02-54bb-9e8d-8a513e63a228 | checkpoint | 7.3 - A register of hazardous chemicals used, handled, or stored at the workplace has been prepared in accordance with the regulations and is kept at the workplace.
73d14d34-271c-5e50-a0cd-036c9275e063 | checkpoint | 7.4 - A spill containment system has been implemented in each part of the workplace where there is a risk from a spill or leak of a hazardous chemical.
a5f93861-409f-57a4-9892-aad365d82b0e | section | 8. Corrective actions
a3895f4e-c7f0-509b-ac43-872a6873bc7e | checkpoint | Corrective actions
fefdfa68-8ae7-5784-8f52-ff31386b2624 | section | 9. Inspection sign off
19075f73-f3d6-5581-b9a9-39135e1c7056 | checkpoint | This workplace inspection checklist has been completed by;
4b32712d-5eb5-5f21-8318-9f10d9fee1e3 | textbox | Name:
8f6f1e26-c9d1-5d5c-beb5-fb775c1e28a2 | date | Date:
75e3ab6c-26b3-5c04-9c56-ec536230e4ac | signoff | Signature
690502ea-7da5-5119-ba91-b2aa394089de | checkpoint | I hereby certify that all corrective actions as identified in the above checklist have been completed;
be7ee8f6-2fdf-5e61-aee6-adf9bbb71704 | textbox | Name:
f58dc23b-c6d5-59c2-9d2a-57694b8eff87 | date | Date:
3e494399-cc9e-5e9f-964d-deff12bc6678 | signoff | Signature
7bd28543-904f-5683-acd7-cdd9184635f4 | checklist | CHECK-003 Site Establishment |  | CHECK-003 Site Establishment
8111ace1-1386-5c1f-8290-3df28e3c8d3f | section | Details
0b4ad232-5674-51d3-9408-aef0b58a609d | checkpoint-no-value | Details:
a9f0eb07-3912-523a-be5f-a802d6ff641b | textbox | Project Number:
be704f51-8345-5d07-82ad-4691b8d46bd7 | textbox | Project Name:
55438198-cfca-5417-84b8-414b08417475 | textbox | Project Manager (PM):
cecfc96f-5250-5907-bbf1-e0562cea155d | textbox | Project Address:
71a86034-b956-5203-b873-8d6f798b33ad | textbox | QA Platforms used:
d76c3f2b-8320-5708-a9da-38fbd066c69d | checkpoint | In house, FER & Specification Numbers
62d9c92d-c1ab-5446-89b1-bf80cbc0d1a4 | date | DATE:
087bf1f2-2a91-5ac0-811b-92888709522d | checkpoint | Site visit & survey
9d598589-23f2-5739-abd1-38084d2be5a8 | date | DATE:
f40bf70e-7c03-562e-9e73-8fbcd929c861 | checkpoint | Review Drawings & print for site
767f52ec-aec3-5775-a064-7229f459323b | date | DATE:
86a71627-b83a-5fe5-827a-1173c7cec5b0 | checkpoint | Review Fire Engineering Report
0d7909f1-54e9-5c90-92e6-074eee42c7aa | date | DATE:
eb035cf3-e47b-505b-b522-f71e191c12e9 | checkpoint | Allocate labour
0a895642-a262-5e46-a17d-2bd265707331 | date | DATE:
dae330e6-ef9c-57c6-9197-103abfd54f8e | checkpoint | Review Principle Contractors (PC) proposed baseline program
1692f978-f249-5f30-958a-396ff70c258b | date | DATE:
a55f05f2-ebad-534b-8cbf-1758e22f0184 | checkpoint | Create Fire Services Proposed Programme
07f60850-c8ec-5c07-8cb3-4760f7a199c5 | date | DATE:
7a356f7b-71e1-5c53-87a9-49ac25d117b8 | checkpoint | Upload to ALL necessary QA platforms
b5b18c80-8662-5430-9ca2-81c6feb62800 | date | DATE:
e81b739e-4825-5367-841f-3db753c333bf | checkpoint | Save softcopy in GM Dropbox
c65d94ba-f3ef-5124-bde6-1efbcc2ca74a | date | DATE:
c2e6bd69-c405-5afe-b004-c8b107fec18d | checkpoint | All employees have attended Induction
f2578d06-522d-52c8-91f5-609e406fe43b | date | DATE:
2630ff26-4768-5012-85c8-d89b8e40b4dc | checkpoint | All SWMS soft copies signed & hard copy printed & filed in the ‘on site’ paper folder
ccf4434e-fcc7-5408-8a54-c9b9b3f5816e | date | DATE:
5674c7a7-848b-557d-a867-52fce0b2bfd9 | checkpoint | PM Signature:
1ec883e5-6967-525b-ae22-80125604b1fd | date | DATE:
c87607a0-8578-5433-aab2-734b6f931e89 | signoff | PM Signature
a9f3dae5-2089-56f0-a2a7-1e8117f00339 | checklist | CHECK-004 Prestart Plant and Equipment |  | CHECK-004 Prestart Plant and Equipment
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
8111ace1-1386-5c1f-8290-3df28e3c8d3f | checkpoint | Details
0e841671-e894-5ff8-8c03-82b5d38ebca8 | date | Date:
c1d0f4b3-7c9a-5132-9202-97a201ea48ef | textbox | Time:
bb60eefc-fad6-507f-945f-d1ad16fbf517 | textbox | Location:
24067169-41ae-5b98-ad46-2642b05d62e7 | textbox | Supervisor Name:
0b454d7c-2ee3-5e46-a2c9-e543b923b322 | checkpoint | Plant or Equipment
f5a882c2-e981-51c1-b81b-ea1e16eb70bc | textbox | What Plant/ Equipment is being used?
f2431a16-e799-5a6c-80c2-763dddad7637 | textbox | Person operating today:
dd154f8d-3d7b-5f2c-88c3-251fe510498d | button | Is this person competent and licenced (if required)? | Yes, No
70fb33c4-1f70-5ac0-942b-6a10ea85acdb | button | Is the operator under the influence of alcohol or drugs? (If 'Yes' please explain in comments and find an alternative operator) | Yes, No
cc81ce2f-8bc8-5749-80fd-06fb563d3672 | button | Is the operator tired? (If 'Yes' please explain in comments and find an alternative operator) | Yes, No
63617e94-873e-5e03-9f60-862196254f6a | button | Have you added this to REGISTER-007 Plant and Equipment (located in Dropbox) for this project? | Yes, No
a7d9973d-01b6-5c61-bcc7-8234615b507b | button | Have all relevant SWMS been completed? | Yes, No
f9910de1-77f1-541c-876c-35b08d530ef7 | checkpoint | Plant and Equipment Checks
e3c467e9-a510-5e56-beed-49a3f8877e1a | note | As per WHS Regulations 2011, s206 the person with management or control of plant must ensure the plant is used only for the purpose it was designed and ensure that all safety features and warning devices are used in accordance with instruction. Please check the following:
546a8afd-7693-55a2-914a-54e7c90d72ae | tickbox | Electrical switches, traffic indicators, front and rear lights are working
e5b78bd6-d41e-528e-9746-0c62c2c527e7 | tickbox | Guarding is of solid construction, unable to be bypassed or disabled, is appropriately fixed and operates correctly (check latches/ locks and interlocks if fitted)
8b9ff6ad-23d7-57de-9e48-14a9253d2139 | tickbox | Engine, fuel and lubricating systems are as per manufacturers specifications
5806d6c3-2813-50a0-a427-7fa9935957a4 | tickbox | Tyre pressure is as per manufacturers recommendations
d39fe1f4-ba21-5239-8ecc-7f4573210e83 | tickbox | There is no risk to the plant colliding with any person or thing (i.e. workers, other vehicles or plant, energised powerlines)
54704e4f-9089-5ee6-ae7f-46a0727eac60 | tickbox | There are no mechanical or other failures (e.g. hydraulic failures, release of hazardous substances)
f6e7258f-adb6-541d-b22a-ed50132853e8 | tickbox | Seatbelts are available
5d47353b-22df-563b-a9ca-2faccbdb89e6 | tickbox | There is no damage to switch gear and controls and that controls can be locked off
58c4f0bd-8df6-524c-a238-af2983501734 | tickbox | Emergency stop controls are marked, accessible and coloured red
3ad0b909-d61c-507a-a372-2aec69aa39af | tickbox | Warning devices are positioned to work effectively
4ccae013-80b5-5161-9761-e7028e449e0c | tickbox | There are no hazards to the operator (e.g. things that could fall on the operator)
f7a4206a-0f8f-5a90-863e-6dc75e30731c | tickbox | There is no hazard or risk that could caused the plant to overturn
cf1206a0-2d7e-5f3f-be6c-0f9e888638ec | tickbox | Maintenance and inspections have been carried out
2bcc0a89-8c1f-5fe5-958d-a1f1ba7233a4 | checkpoint | General Notes
d7295a42-11dc-51c1-80d1-cf9ed24c9857 | checkpoint | Operator Signoff
c685b88b-9455-5eaa-8271-b512fa65c130 | signoff | By signing I confirm I have participated in this prestart and understand my duties. I know what PPE I am required to wear whilst operating, the load limits and I am aware that it is my responsibility to leave plant not in use in a state that does not pose risk to others.
cc546369-bca4-51b6-ab24-8e4406ba760e | checkpoint | Supervisor Signoff
411f2708-55c2-5469-af77-82675a4393a8 | signoff | By signing I confirm I have conducted this prestart with the operator (above).
9532b837-f860-5b1d-ab12-067a44cade17 | checklist | CHECK-005 Site EOD |  | CHECK-005 Site EOD
8111ace1-1386-5c1f-8290-3df28e3c8d3f | section | Details
e7f3c29e-5e50-58c0-b5bc-209b95434737 | checkpoint | KPIs
ef28294d-80e7-5a97-9797-47eab0412edd | textbox | What area did you work on today? Specify level(s)
8bac133b-8e7b-54d3-bd45-213c754c0666 | tickbox | Detection - In Slab Conduits
df315065-d10d-5309-a137-f96b6957f3ca | tickbox | Detection - Rough In
79d811d4-f9b3-5356-8c5c-282608faae28 | tickbox | Detection - Fit Off
bd243762-5500-5cc3-863e-a5089b537b11 | tickbox | Sprinkler - Rough In
b32b2f5d-1593-5094-8ac0-574540448662 | tickbox | Sprinkler - Fit Off
b6b03401-f74a-555d-a276-7baec04d7748 | tickbox | Wet Weather Stand down (List names and duration of stand down per person in comments below)
702632f3-f07d-55dd-b02a-798d0cd2c2bb | tickbox | Safety Stand Down (List names and duration of stand down per person in comments below)
ad3f731b-7995-5c43-9ca1-66fcc39f907a | tickbox | Industrial Action/ Techs chose to leave site (List names and what time they left in comments below)
d6aa768d-18cb-5397-9287-98d25f058d4d | checkpoint | Productivity
935439a4-16d9-54f5-94c7-76368fef5f00 | textbox | In terms of production, did the team meet the site goals today? | Yes, No, Partially
5eb767e9-2d9b-5650-9148-f8d6eacb88e9 | button | If 'No', what hindered the progress? | Time management, Lack of training, Fatigue, Equipment issues, Other
e94f5534-5646-540d-aa79-e9ebca99d6ea | textbox | If 'Other' provide detail:
0da64418-8a08-5008-a58c-e5368b811be6 | checkpoint | Clean Up
ff4b227b-9ed7-503b-a008-a24d64c82a30 | button | Is your work area tidy? | Yes, No
2685c8cb-e50d-53b0-81fc-2140a66dc922 | button | Have Chemicals used today been returned to secure storage? | Yes, No
63aa0fac-8064-5883-8936-a62b7a9bec47 | button | Have all tools been returned to toolbox? | Yes, No
ec167b87-5679-50a0-88b1-36f8dbca244d | button | Are all tools (including site iPads) charged and ready for tomorrow? | Yes, No
95ffe66b-b5ad-53bb-9648-f5d931f2f4c0 | button | Have you completed all necessary QA paperwork for today? | Yes, No
bb4bba5b-d0e8-5fdb-a13b-dbc423aaee5a | button | Are all employees aware of where they are working tomorrow? | Yes, No
db72225a-9b45-5d2c-9afa-e9dfb88f7dd0 | note | If 'No' contact management now
a11f6f9a-2853-505a-b6fc-46a0fac484e1 | button | Were there any incidents, injuries or near misses on site today? | Yes, No
2b76a127-74df-54eb-92bd-c06e1d1e92d7 | note | If 'Yes' complete the necessary reports
42c21dbd-9bff-5051-bd1f-f936237b2320 | checkpoint | Signoff and CLOCK OUT
5d29489d-1335-55db-945d-fe7621bce49f | signoff | This EOD has been completed in consultation with our employees and has been read, understood and signed by all employees on site at the EOD today.
1acfb286-05d9-4f83-acb9-7eaea7c711d0 | checklist | CHECK-007 QH Capital Infrastructure Requirements V.4 |  | CHECK-007 QH Capital Infrastructure Requirements V.4
ffed8b4c-bb6d-4c8f-8d14-4d19ff6afdbd | section | 3.4.1 Schematic design
e448faaf-2509-4fcc-a6ed-48fed381b7f2 | checkpoint-no-value | General
fac8b618-b577-5e85-ae3b-ef0bfda77818 | textbox | Project Name and Number:
20fdfc94-cacf-54fa-b1a0-5dc42e56b8df | tickbox | Carry out on-going checks for compliance with regulations.
514a1733-1d05-58e3-9afc-3f8b318ee2c5 | tickbox | Monitor compliance of the developing design with the project brief.
040e8d2a-7b0a-52d9-acb2-4709fa7334a7 | tickbox | Draw up a strategy for fire safety and define the parameters for fire detection and suppression systems, and review with other design consultants, particularly the architects.
6ffd0aa0-05b1-5c2e-a869-94b581d34101 | tickbox | Confirm design criteria, scope and extent of fire services.
4800540b-c979-54cb-b043-b9af5ebf3fe2 | tickbox | Update recommendations to Queensland Health for their development of an operating and maintenance strategy.
08a00a4d-689b-5d76-8d12-313be0073a59 | tickbox | Carry out initial overall spatial co-ordination.
1fb95687-9761-56c9-9cb0-ca23c47a91f6 | tickbox | Provide information for RDS, where these are used
65bd12fb-d7b8-53fc-b371-d43711561132 | tickbox | Identify client requirements which will necessitate design input from a specialist designer, sub-contractor or supplier, and the timing of their appointment.
b1ecf564-d8bf-5933-b3c3-0d2117169bd1 | tickbox | Define the essential performance requirements of systems. This may involve establishing numerical criteria for the nominal capacities of plant, the range of operating duties anticipated and consideration of the requirements for submitting samples and prototypes.
4e2ab3ae-5375-5214-983e-45ef062bf444 | button | Have you advised significant allowances or constraints incorporated in the main design that may affect the specialist design? | Yes, No
7af071b8-358a-5ea2-9c69-e7950949947d | note | If yes, detail in comments
9d85eb40-a496-5b24-9b2e-1e459dae3259 | button | Have you consulted with Queensland Health stakeholders concerning any risk management/WH&S issues? | Yes, No
e400b66a-4f45-51f2-a7af-a05c523aa546 | note | If yes, detail in comments
5a179803-9cd1-4113-bffb-70fb7a5afc0f | checkpoint-no-value | Fire Services Design
208c3a85-1a9e-5c17-b303-c1118e4113f2 | tickbox | Determine main pipe routes around floors to and from risers.
8eebc3dc-d07d-5cb5-98fc-ae0a17d746a5 | tickbox | Determine approximate pipe sizes, head types and locations, valve sizes and locations, and sizes of ancillary equipment (such as pump sets).
db2737a4-b874-5c64-a2f6-a0df5c21755e | tickbox | Determine FIP locations, SIP and pump room sizes and locations.
089b99cf-a310-51fc-a8d5-2501dfaf1061 | tickbox | Design automatic controls systems as required to meet with the operational, functional and spatial requirements of the specification.
8d735676-788a-4a4f-ad66-a3a2f2d2eee3 | section | 3.4.2 Design development
69e84cbb-e8a9-467b-b723-87ece7ec5ced | checkpoint-no-value | General
bf22951c-96d0-5fb8-9691-3b878e0f5a5b | tickbox | Carry out on-going checks for compliance with regulations.
81635b94-bc17-51c0-ab32-a90ff7195215 | tickbox | Negotiate with public and other utility authorities for the provision of incoming services and agree spatial requirements.
b4fb0e1a-ae71-5bd7-a9d2-650d761f4c04 | tickbox | Monitor compliance of the developing design with the design philosophies.
51e9cd6c-1a1b-5b4c-b35c-5b7afb575b95 | tickbox | Review design against NCC
8864f38a-8f18-57bf-aa81-473a177760c8 | button | Has a team-wide design review been conducted to signal the end of the design development stage? | Yes, No
a739b71c-cfd8-4b3b-8cf5-8768c5abf0e8 | checkpoint-no-value | Fire services design
72f03e50-2502-58b7-a231-cb2db9755699 | tickbox | Confirm design criteria for fire systems.
8d97ca4a-2b9d-53ba-8713-4012986bcbc5 | tickbox | Establish indicative plant and riser sizes for fire systems and plant room locations/sizes.
b0fe843d-4b56-4b6d-983d-ca97a824a40a | section | Contract documentation
32e2a27b-3e43-41aa-84a2-26fb34428f39 | checkpoint-no-value | Team liaison
0e734163-96df-5009-a19d-ede4a29481f8 | tickbox | Check the provision for and adequacy of the preliminary builder’s work information previously issued by others.
81230ce7-9ff3-58be-9041-3dd59fa8d22f | tickbox | Confirm builder’s work information for specified equipment or materials, or where alternatives to those provisionally or pre-selected are agreed.
416378fd-2355-50de-8504-33faeb7051fb | tickbox | Co-ordinate the design so that the requirements for all access platforms, stairs, rails and protection elements required for future maintenance and operation of plant/equipment.
a2bd132a-091d-5ac0-a149-7c4febd269fe | tickbox | Carry out spatial co-ordination associated with major spaces: plantrooms, risers, depths of ceiling and floor voids.
0bbdc70e-2395-56bd-9fb4-57af52fc2541 | tickbox | Consider requirements for installation.
5ee25179-35f9-542d-a2e7-331dd4270a88 | tickbox | Carry out final detailed spatial co-ordination between the building services and the structure/architecture.
73dd93e1-7667-5fc6-9fdb-ee5887984d03 | tickbox | Modify the final detailed spatial co-ordination for approved alternative equipment or materials.
e0e0a486-0a27-4ee9-b327-3f36f242400b | checkpoint-no-value | Fire services design
b024f7a6-0f1a-558e-aec2-8966e59d7111 | tickbox | Carry out final detailed design calculations for all remaining services in accordance with relevant standards.
fbc331d6-bd35-5227-934a-c791fa9c2986 | tickbox | Carry out detailed design of pipework systems.
d51ec383-682d-598d-bfa0-e9c4df0e3493 | tickbox | Carry out detailed design of anchors, guides and other provision for movement of services and systems due to building movement.
d7bee0a3-68ef-5e24-be9e-412f7ede7474 | tickbox | Modify distribution systems and equipment capacities as may be required as a result of final detailed spatial co-ordination.
eccaeabf-4d6b-56c9-80e3-d3c92b32c6a0 | tickbox | Check pump system duties based on the final equipment selection and co-ordinated installation drawings.
24facc38-9bf1-5a8b-8520-04f7ff4fbb87 | tickbox | Specify final location of access panels, and other equipment required to facilitate maintenance.
9b5c836e-c711-57a6-9f47-1dde61bfdf03 | tickbox | Carry out final coordination with hydraulic engineer for all drain points
868c9fca-643f-567f-ac99-c7fa9f8fcea3 | tickbox | Carry out final selection of all terminal devices – sprinklers, detectors
370aee46-d823-55ab-9007-22fb11ae72ea | tickbox | Confirm designs for pump rooms, booster systems, brigade connections
98d18702-383f-4ef4-861f-be504208022b | checkpoint-no-value | Commissioning
8de7e87a-6557-5cb7-9a30-25b60264a02c | tickbox | Identify and incorporate into system designs the essential components and features necessary to enable the proper preparation and commissioning of building services.
f4116fc0-1d2e-531a-a40e-f48a6c51d789 | button | Have you reviewed all designs to ensure that systems are commissionable? | Yes, No
de20c3dc-fff8-54c3-996d-635c913c884e | button | Have you reviewed commissioning requirements? | Yes, No
697a3a8c-3066-5410-9068-03903bb01c6c | tickbox | Coordinate fire services statutory and authority testing requirements for the project
40a3cf88-b281-529e-86bb-6e2ccb7606e0 | tickbox | Integrate commissioning activities with other services, particularly mechanical and electrical services for shutdown and interface testing.
a748c738-43f5-42ec-8dae-4438617be031 | checkpoint-no-value | GM Fire Sign Off
07ea1cc8-7a9d-4bc3-b476-152d70e6396f | signoff | GM Fire Sign Off
dfc56307-e0a2-478f-8e36-b6848522c6af | checkpoint-no-value | Consultant Sign Off
ad7b775c-aa93-42dd-a03b-0abbc65549c9 | signoff | Consultant Sign Off
ccd72527-2a8b-4791-a928-104af46570ce | checklist | Communication (empty) |  | Communication (empty)
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
186a21d9-360a-470f-a923-ca138b2cd9aa | checkpoint | Communication
fe2e582c-3091-5fda-ac1d-3836e5acc9bb | note
5450b772-d997-57fe-895d-71ad5cc37336 | checklist | FORM-001 Tool Box Talks |  | FORM-001 Tool Box Talks
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
0e50f726-5e25-5b32-be5e-0af50c2a4fbb | checkpoint | Tool Box Talk
e3272aff-5ad7-5584-9f05-601db13efeff | note | Project: Minor Works
c4982672-0b0f-5087-ad36-2079a30053d4 | textbox | Tool Box conducted by:
b862c72d-bb88-5890-9585-9eb1d66d73f3 | date | Date:
201ee0d5-9875-55e5-a6b4-cf9a175f45ee | textbox | Attendees:
272ef767-b0f9-5d40-860f-37667165b540 | checkpoint | Electrical tools Tagged & Tested
de358699-2ee1-5f01-a52d-02e78a8f5dcb | note | ACCEPTANCE CRITERIA: Completed Onsite
9031bd57-1d4e-547c-b0ec-b6fb0b1da5db | date | DATE:
605677f5-661a-5bc3-a836-02384d30df5c | checkpoint | Tools checked for wear & tear
d34b0a75-d62c-564d-93ac-a1912bd32f6b | note | ACCEPTANCE CRITERIA: Completed Onsite
8aa8c1f1-8235-59cf-9f29-b950ab07c005 | date | DATE:
acfc8acb-9e64-5733-af2a-b8ca4ea1ea81 | textbox | Items for Discussion:
eabcda0d-be6f-512a-b32a-8bddf5fcbc83 | textbox | Items for Review and discuss at next meeting:
95cb37b4-7a6f-5ffc-99b0-5d11fbc535e8 | signoff | Signatures
67624c30-0631-53f9-aa45-6f94413e7795 | checklist | FORM-002 Tool Box Talk Platform Ladders |  | FORM-002 Tool Box Talk Platform Ladders
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
106e79f1-1888-598d-99d2-b5a1def7ffd3 | checkpoint | Tool Box Talk - Platform Ladders
887bab57-3216-58e7-9dd5-6974b3a623f9 | note | DO NOT use platform ladder unless you are familiar in its safe use and operation.
ac68153f-7547-5f9f-b14c-f8801309e330 | note | Always complete as much work as possible at ground level before using the ladder.
3271903a-2c15-5d14-ac31-800aa151f93c | note | Make sure the platform ladder is stable before climbing.
5c4a49ee-d931-5509-bdad-bc64c1ca1617 | note | Project: Minor Works
00a320e9-986f-593f-bfe8-d25f2931da45 | textbox | Tool Box conducted by:
d0208122-f03a-5610-bde4-6bcb1a760f97 | textbox | Attendees:
da9865ac-d3b6-579f-bb6b-472d8b97b3d7 | date | Date:
fe834967-5fae-5142-ad41-d9de6147f88c | checkpoint | Potential Hazards
3674f2b7-e39a-58bf-b062-1209a407d5a0 | note | The folllowing potential safety hazards and risks have been explained to attendees:
5ea57c24-c9ef-5ac2-aae7-14b6543b15e5 | tickbox | Falls from height
e35ecb4b-a22f-5bcd-833f-fe852d10554a | tickbox | Falling objects
a3d70cbf-4729-5583-aee4-bcf73f29102e | tickbox | Awkward posture
016ab889-7fd8-5c55-95e3-1cf5f8ca44c5 | tickbox | Duration of task
674a0483-b78e-5388-ad6a-db7ac2554b1c | tickbox | Repetition of movement
3f4946f8-8fdd-526a-bb60-7b0d27db4098 | tickbox | Sprains/strains
a6af3874-9657-5afa-ac7b-5c30211f6885 | tickbox | Over-balancing
75d35ab2-1c77-568c-80f3-d9d45ae93ef3 | tickbox | Slip/trip/fall
4a7ce000-11b4-5942-9d59-57beec09de90 | tickbox | Electrical hazards
70790ef5-6074-57a2-b56e-987747b11967 | tickbox | Climbing with loads
1bd92719-b7cf-583c-a096-9b04e390c7ae | checkpoint | Pre-Operational Safety Checks
6ffbd377-bf17-5fba-98aa-8caef52856d1 | note | 1. Familiarise yourself with the safety instructions on the ladder.
a2ea6641-1eb7-56a0-a6e1-7e49d7e16115 | note | 2. Wear slip-resistant footwear. Never wear sandals, high heels or flip-flops. Wear appropriate clothing (e.g. no loose or flapping clothing, or clothing that restricts movement when climbing
aaf65bc0-57d6-5a03-b04a-8610a6416a50 | note | 3. Do not use if affected by a medical condition or medication.
2ba95fdc-b818-55eb-8e98-76f82b92f60b | note | 4. Keep ladder clear of live wires, electrical hazards and ceiling fans.
2c22d256-80a1-5046-8b5e-69ef43b328e9 | note | 5. When transporting your ladder check for overhead power lines, live wires, service cabling or electrical hazards.
93412ad9-195b-58ad-a5cc-688db75dd770 | note | 6. Carefully inspect your ladder to ensure there are no worn parts or damage before climbing:
ffc562ba-2d4e-5c0c-923b-aee111b51e69 | note | • joints between steps and side rails tight, all fittings secure, moving parts operate freely
639c69e6-a3c5-5051-a7d0-e2ca755bc18b | note | • rungs and platform are free of paint splatter, grit, oil and grease, welds are intact, and
5dc33034-ebb6-5e46-8386-62410b6d7321 | note | • all components of ladder intact including side rails, rungs, platform, feet, hand grip.
c1ec81fc-3779-5bbb-99e7-d74bdce4d420 | note | If any component is found to be worn or damaged, rectify any faults before use.
b6eb527a-c4c7-5a69-bb85-a66da835bc7d | checkpoint | Operational Safety Checks
df307b10-6066-5dfe-b2be-ccdabe4b711c | note | 1. Complete as much of the task at ground level as possible.
50ceb36d-3a89-51e0-a79d-8e7534c96b76 | note | 2. Ensure the ladder is placed on dry, firm, level ground/floor. Uneven footing may cause the ladder to rock. If this occurs re-position the ladder until all feet have firm contact with the floor. Always check there is no rocking movement before climbing the ladder.
2b10f449-9e31-58fa-8e70-0fe01b8c3789 | note | 3. If castors are fitted to the ladder, ensure rubber feet have firm contact with the floor when the springs are depressed.
37b91bc5-cb01-56fc-9108-0102c7c4058a | note | 4. Ensure the ladder is fully opened and the spreader bar is locked into position. Check for overhead obstructions before climbing.
7cac46ae-5fc7-5ee4-994f-75dd2980ea6f | note | 5. Only light work is to be undertaken on the ladder. Always face towards the ladder when climbing, and always maintain three points of contact with the ladder. Use a tool bag or tool belt to help to keep hands free.
64f23374-768a-5597-b8a4-9427fc451328 | note | 6. Only one person is permitted on the ladder at any time. A second person may stand alongside the ladder and help to steady it, or pass materials/tools up if required. Do not lift heavy weights that unbalance the ladder.
cea9f832-60c9-5a6a-8373-7c2c02db8309 | note | 7. Never stand or sit on the top cap or use the rails around the top as a step. It is not designed to be used as a tread/seat or step. Always stand in the centre of the platform.
c5338561-5326-55d2-8865-025c5fc7aa76 | note | 8. Do not over reach whilst using the ladder. Maintain the majority of your body weight inside the perimeter of the platform.
6a5bcd9f-5002-5193-afd2-5687e1f860a2 | note | 9. Do not ‘walk’ the ladder while on it. Always get off to shift position.
19c1d6b4-49ea-5f94-9658-6f1b832f0141 | note | 10. Before moving a ladder, take care to ensure that all tools and other items have been removed.
2d257990-358a-561e-bc89-f01924822341 | note | 11. Be mindful of your concentration and fatigue level. Avoid becoming overconfident when using ladders during repetitive tasks.
9d5b0bf0-53b6-5af8-a766-a7d78d594580 | checkpoint | Housekeeping
b7b52c7c-7b6c-5b22-8666-70b57f43c8ee | textbox | Items for Discussion
5c711e95-86eb-5f70-9f58-45404bea1e34 | textbox | Items for Review and discuss at next meeting:
0d24abf6-09a7-54db-913a-af58fcfdb176 | note | All attendees have been made aware they should:
fdb2ffa5-48c5-5b86-a475-b5e212b244b3 | tickbox | Return ladders to secure storage in a clean and in safe working order
ac8f4780-7d87-5234-98fe-0fee60585788 | tickbox | Regularly check ladder feet for excessive wear.
61838543-8502-5082-8baf-f0fa703ab465 | tickbox | Enter any maintenance in an equipment maintenance record
3015ae9e-0d1b-58a3-bfcd-57a87f411d9a | signoff | By signing I confirm I atteneded this ToolBox Talk.
02d1450d-190d-5aa4-987f-be5245f64771 | checklist | ITPS-020 Comms Rooms Fire Sprinkler Systems | itp | ITPS-020 Comms Rooms Fire Sprinkler Systems
8111ace1-1386-5c1f-8290-3df28e3c8d3f | section | Details
4293bbf2-8bdb-5ceb-ace2-5b9162122951 | checkpoint | For Equipment Rooms (ER) ensure dry pipe system is installed TAKE PHOTOS AND NUMBER IN COMMENT BOX
cb0777cb-1ab7-5846-aa99-0054eda7be0a | date | DATE:
df672989-592a-595f-8a0e-4016c10640d4 | checkpoint | 2 - For Equipment Rooms (ER) and Telecommunication Rooms (TR) - TAKE PHOTOS AND NUMBER IN COMMENT BOX
59f175e4-146f-5160-909a-e20434835f06 | tickbox | a. Check pipework is not routed above equipment cabinets
0b42cf35-8f4c-592d-978c-84ed745fab51 | tickbox | b. Ensure no t-pieces, elbows or bends are above equipment
2983edb9-3576-528e-b675-59b74332ce09 | tickbox | c. Check no pipe is installed within 1200mm of sprinkler pipe
ede5e022-9019-56ff-8060-4f16c82e530f | tickbox | d. Check the sprinklers are high temperature heads
a2ceb093-2ead-5e6a-a16e-033d2ad84b5a | textbox | i. What temperature
0b714a48-1aa2-52cf-a683-4152a36e3aa3 | tickbox | e. Check sprinklers are installed with wire cages
83e6dd5e-de42-53ab-9fc4-b38934a42448 | tickbox | f. Check all sprinklers are upright sprinklers
620009dc-765e-581d-9d00-988d98021219 | tickbox | g. Check a floor drain is installed
b2562e40-4f58-524b-9695-a1a1ff878468 | date | DATE:
00c8164d-471b-5e4e-8249-1b4ddd19d617 | textbox | GM Sign Off - Name:
2123c370-a2a5-58b5-b49f-e31fc4555fe5 | textbox | PC Sign Off - Name:
50c3dfbf-555c-58cc-9c02-e88c74aef70f | textbox | CS Sign Off - Name:
3f9531ce-bbcd-5a01-aaf1-8875887bafb0 | signoff | Signatures
b9f48705-e269-47b8-8158-66a6fb614cc0 | checklist | ITPS-100 Cast In and Penetration Installations |  | ITPS-100 Cast In and Penetration Installations
8ace42ca-ee47-48db-9cc2-7f294ffc414b | section | Details
e45a7966-ddba-48eb-870c-decdaea9617f | checkpoint | 1. LOCATION - ENSURE
d87964b2-b92c-5c8c-82c3-341885954850 | note | CIBSE C5.2.2 Set Points
f25c1f8e-a85f-5b0c-af98-333ac662568a | button | Is the device setout correct and accurate as per RCP and installation plans? | Yes, No
2aacbd82-b671-5521-8188-a3e93adeb684 | note | Add Photo
43c83b6a-4451-4076-861c-f30232613bbb | checkpoint | 2. CONDUIT INSTALLATION - CHECK
0f124d02-23b7-5cb1-a28a-334d7b2d5495 | note | AS1670.1, AS1668.1, AS1670.4 and AS3000
f823f07a-5b39-554a-8c00-6546d03cc39f | textbox | Drawing Reference and Revision Number:
3b8dcc66-d955-57a2-a159-a7ac1f1c6918 | note | CIBSE C5.2.2 Set Points
1aa44bab-6633-5cba-8799-907bb851b04c | note | Are Conduits routes are correct as per IFC Drawings?
485210bb-7591-5689-96d7-fae2ec6ae369 | note | Are Conduits are joined correctly and glued using approved PVC piping and glue?
180d38c7-6717-5f42-8ef2-395c0b4a1b8f | button | Are Conduits are tied in properly to prevent movement and damage? | Yes, No
45746f7a-e64a-54bf-8738-8bd559d45c31 | note | Add Photo
68c2470f-6bf1-4ca6-80a4-baf7be73df35 | checkpoint | 3. SLEEVES AND PENETRATIONS - CHECK
38fcf89d-be7f-53bf-b881-768bcb50686c | textbox | Drawing Reference and Revision Number:
71b2e299-9723-5f24-8d4a-b8d0812dec2c | note | CIBSE C5.2.2 Set Points
c0021e20-6c22-54bf-a588-8a64a32cc97d | note | Are sleeves the correct type, size and quantity as per penetration drawing?
155802ab-8eac-5242-b621-f910600fdab4 | note | Are sleeves routes correct as per IFC Drawings?
1f6085db-8dd0-5607-8c0a-23b3fbba047b | note | Are conduits joined correctly and glued using approved PVC piping and glue?
342a71e4-3a7c-553d-b0fa-0ef7932925d8 | button | Have sleeves been tied in properly to prevent movement and damage? | Yes, No
6416a66f-80d8-50d1-b302-fbb4042faeee | note | Add Photo
5a85f6ed-6bab-419a-a751-4aad020ebacf | checkpoint | 4. PRINCIPLE CONTRACTOR - CONFIRM
0ece26c0-e88a-58a7-9ecf-80bf2b832c11 | note | CIBSE C5.2.2 Set Points
e0757678-b44e-5a19-b19e-33fe263e3f4e | button | Is the Principle contractor's sign off required prior to pour? | Yes, No
0d662198-3cd1-5fa6-bac6-41e501753123 | note | Add Photo
63e20817-3062-4892-8eb7-9668a763ce36 | checkpoint-no-value | GM Fire Sign Off
32e94e60-c44e-4fe3-8d56-f1d9288dcf35 | signoff | GM Fire Sign Off
eb106abb-eaca-4e89-b3bb-a1f6ef36c7d5 | checkpoint-no-value | Principal Contractor Sign Off
5522b0c2-af41-4a7f-8540-dab77f7bc013 | signoff | Principal Contractor Sign Off
ea88d174-132e-4dd2-ad3a-91be7b4f6624 | checkpoint-no-value | Consultant Sign Off
5e8075a5-fb25-4c89-a6bb-f9707b1e65bb | signoff | Consultant Sign Off
a3bec588-e799-4248-95d3-901ca5f03b92 | checklist | ITPS-101 Fire Alarm and EWIS Rough In |  | ITPS-101 Fire Alarm and EWIS Rough In
93736310-8acb-4813-bfb8-301ce7c33ed6 | section | Details
1a87047c-3812-4635-9d66-e9bf1362b61c | checkpoint | 1. CABLE - CHECK
b4d36882-e71a-5ede-be1a-3fb1f60f82c9 | note | CIBSE C5.4.0 Wiring
f28ec21b-9e82-5f72-9dc7-3b719eca8086 | note | AS1670.1, AS3000
b18d894f-5e22-50be-b035-a80b2c44c824 | note | Is cable installed the correct size and type?
96ebd97f-a270-5575-a548-400a3af4c395 | button | Is cable secured at regular intervals? | Yes, No
6cf299d7-fd90-5566-85ff-ae16cb159597 | note | Add Photo
c432d4ea-d840-5168-9ba1-fdabfcd83ef0 | button | Have you attached a photo of cable markings for Green Star Compliance? | Yes, No
6410f97d-1b72-5f46-8e85-85d207614947 | note | If no, stop and attach now
faad3e19-fff9-467d-87be-3fd143e79a0d | checkpoint | 2. FIRE RATED CABLE - CHECK
ef182fa0-051b-5b94-8044-6a7d67020ef3 | note | CIBSE C5.4.0 Wiring
314c785c-d6de-5081-a992-b6a01029af73 | note | AS3000, AS1760.1, AS3013, AS/CA S009
4eacb167-d12c-5a7c-a6b2-99d266909125 | note | Have fire rated cables been secured with fire rated fixings at a minimum of every 1200mm?
56e22c60-46e0-5041-b19b-43bba8550adb | note | Have compliant fire rated cable and fixings have been used for required circuits?
c9b5c6eb-d311-5b34-b647-a57bd7d07f4d | button | Are fire rated cables installed as the highest circuit? | Yes, No
cafe07ad-1e99-5821-a8de-edd4ac4a8bdb | note | Add Photo
ca6ae18e-0b4d-4808-a7da-ed9e395f5689 | checkpoint | 3. CONCEALED SPACE DEVICES - CHECK
78d9a5b5-0d73-5eca-85db-cd7b5b308c81 | note | CIBSE C5.6.0 Sensors/Detectors
61c9ef64-78a9-5710-9b69-68e0cc4a9722 | textbox | Drawing Reference and Revision Number:
ee7a4000-a3aa-5697-b3e8-3630d0ab2e60 | note | Have all concealed space devices been fit off?
8e6cf140-0c4d-53a0-9bbb-b50d38294b1f | button | Has remote indicator cable been left with adequate length? | Yes, No
1b50aa9a-d1a7-5635-9507-89647f442479 | note | Add Photo
defb6fbc-eb75-44c5-bf90-0d49ea2eeead | checkpoint | 4. ROUGH IN - CHECK
a7509678-d802-53bf-a316-d2115e72bf91 | note | CIBSE C5.2.5 Control Loops
38dfb075-ecc9-5e74-8f09-e9a6afe65f0b | textbox | Drawing Reference and Revision Number:
ec633833-e182-5d70-9b6d-1a9a503c344e | note | Have all devices been roughed in?
cbcfc098-1d1c-529a-98d7-a0010005417a | note | Is there adequate length left for fit off?
e0042054-3ba4-5a61-8abf-6bf37f97387e | note | Are device locations accurate as per the latest RCP?
a46ea558-141f-5334-8cc7-4b8940259822 | button | Have circuits been metered for continuity? | Yes, No
4c32b5d5-98b0-555d-a40c-cd4931ffa447 | note | Add Photo
00c1aaae-a7de-46d7-86cc-854b2d6c67c2 | checkpoint | 5. MAG DOOR HOLDERS - CHECK
4167640c-54d7-5da5-9579-d0974b2e8991 | note | C5.2.2 Set Points
77b784b5-42f8-57ec-be2e-c03ba431ce46 | note | Have wall noggins have been installed?
2e96aa6a-2836-5574-b92a-2517fcec77bb | button | Are cables roughed in to the correct location in wall? | Yes, No
d361e6a2-6ebc-4d8f-b07d-33536c062d13 | checkpoint | 6. SEGREGATION - CHECK
2be3a32c-db95-5fb5-940c-7f070ae5272a | note | C5.2.2 Set Points
90225f6b-1d89-5d8c-84ba-12943f6fbb67 | note | AS3000
eaf763ad-9133-594e-bcf7-9c2acd5c3e78 | note | Is there a Minimum of 25mm from water & gas pipes?
84c8152a-df51-59b8-977d-564e593ffcbb | button | Is there a Minimum 50mm between ELV & LV installation or a physical barrier? | Yes, No
c8b1ab41-d509-4d72-bde3-635630169d78 | checkpoint | 7. AS WIRED DRAWINGS - ENSURE
fb021e28-3170-5c5d-bff3-8e5f3996ffcb | note | C5.4.0 Wiring
d76cd2eb-50a8-588f-a8a3-1ab7ca2bc9d0 | textbox | Drawing Reference and Revision Number:
bb5710b7-8b9d-58e6-a2ae-28c5ef10a266 | note | Are As-wired drawings complete and accurate?
3de4696b-8228-5985-87be-534e301d0ba0 | button | Have photos been uploaded to Dropbox? (as well as below) | Yes, No
147b737d-511b-5014-b027-38f1e368dfed | note | Add Photo
1d800ed8-f2cf-4854-9df5-f91581baf248 | checkpoint-no-value | GM Fire Sign Off
bd955051-4bcc-4826-adaa-2bbf40963f19 | signoff | GM Fire Sign Off
cc392965-719b-46a0-82df-107b4008a19d | checkpoint-no-value | Principal Contractor Sign Off
94343552-2238-483c-ad32-a3855e9f8087 | signoff | Principal Contractor Sign Off
79765fee-7ebd-49a9-b76d-bebc04daabbf | checkpoint-no-value | Consultant Sign Off
3c96f1fe-35ce-4ea4-a718-82dd9fff9a31 | signoff | Consultant Sign Off
eebbcd58-ff2f-43bb-939f-092ad9aceba9 | checklist | ITPS-102 Fire Alarm Fit Off AS1670.1 |  | ITPS-102 Fire Alarm Fit Off AS1670.1
c5ae2ba3-89f3-4a58-a374-fbde7d802dbc | section | Details
c0d3dcd6-42b1-45f9-9e1c-03fc0e52443f | checkpoint | 1. DETECTOR TYPE AND LOCATIONS ARE AS PER THE LATEST RCP
78581d5c-7517-5f44-8d0f-780af83b90d1 | note | CIBSE C5.6.0 Sensors/Detectors
04ef6d66-48da-510a-822c-5e3df5c02bd0 | textbox | Drawing Reference and Revision Number:
3c205706-fb8b-5996-967e-6483f9b41b40 | note | Add Photo
61a3c1a6-37f3-4b7f-bfeb-9e1a80239ee3 | checkpoint | 2. DETECTOR ADDRESSES ARE MARKED ON AS BUILT DRAWINGS
089a6fb1-261c-5f82-bc75-7246d1f68756 | note | CIBSE C5.2.2 Set Points
7679128e-f06f-5b27-af1f-d257afd4ca80 | textbox | Drawing Reference and Revision Number:
45e28bd1-8982-50e0-8ab6-58f4085a0744 | note | Add Photo
f20264c1-e5b7-4d2e-832a-f0989557456b | checkpoint | 3. DETECTORS MAINTAIN MINIMUM CLEARANCES FROM WALLS, PARTITIONS & AIR SUPPLY OPENINGS
922f179c-ee27-5eb7-9bd7-8deb4deda895 | note | CIBSE C5.6.0 Sensors/Detectors
8609c567-67ed-516c-ab84-3b3c9e0efef6 | note | As per AS 1670.1 - 2018 - 5.1.4 & 4.1.4;
a3fe9ec0-923f-545c-96a8-46d17d490484 | note | Is there a minimum of 300mm from walls & partitions?
9a4cbd5a-f98e-58f0-950f-d251f0e2fc1f | button | Is there a minimum of 900mm from air supply openings for smoke detectors & 450mm for heat detectors? | Yes, No
8a379adf-8529-559c-85b2-fdf2fadfc3e9 | note | Add Photo
4081de39-2e55-4268-aed7-0df453f89d1d | checkpoint | 4. DETECTORS MAINTAIN CLEAR SPACE AROUND SAMPLING POINT
8098e963-fcbb-5e17-9658-d9bf18c7f7da | note | CIBSE C5.6.0 Sensors/Detectors
212e46b7-8694-50bf-9f2f-01ee96a83d4f | note | As per AS1670.1 - 2018 - 3.27.1;
e75374ec-885e-5eb5-a07f-e9566a0587f0 | button | Has a clear space of at least a 300mm radius and 600mm depth been maintained from the sampling point? | Yes, No
63ad80f9-2702-5047-96c2-28d63afe953a | note | Add Photo
853e90b4-5cb8-40b5-b759-a87f926c68c9 | checkpoint | 5. PROTECTIVE CAPS ARE INSTALLED ON ALL DETECTORS
65cde617-2dc9-56ba-b7f6-57326e509556 | note | CIBSE C5.6.0 Sensors/Detectors
312881c3-9a9d-5073-a61f-d6fb0d08bac7 | button | Have dust caps have been installed on detectors to prevent contamination from construction work? | Yes, No
0f2ef4c1-2309-5d1f-a41e-b4f011031e18 | note | To be removed once dusty works are complete, or at commissioning.
b6fc3a6c-4077-5ba2-8b3f-0549de6bfb6f | note | Add Photo
1150f14a-f5b8-4cca-ada7-9a6ef51574f7 | checkpoint | 6. MANUAL CALL POINTS INSTALLED AS PER LATEST IFC DRAWING.
225b6aee-e14d-535d-aa2a-ff910f0148d2 | note | CIBSE C5.10.0 Manual Call Points
d7b45826-bc1b-5893-ba96-6861f8bb5fb0 | note | Have MCPs been mounted between 750mm & 1200mm above floor level?
74f27ae9-775b-5cb1-a270-5acc050732ba | note | Is there a clear space of 300mmm on both sides?
11e65864-fe14-57b6-bab8-ddc731b1846e | button | Is there a 600mm arc directly in front of the MCP? | Yes, No
f837895e-5784-587d-b693-023662e281fe | note | Add Photo
6130447d-db18-4b96-9855-7296283c42a0 | checkpoint | 7. MANUAL CALL POINTS SPECIFIC LOCATIONS
989e7443-1270-5a58-93b8-45cb448ea75a | note | CIBSE C5.10.0 Manual Call Points
5579d230-77f6-5997-8bdb-673b279e3006 | note | As per AS 1670.1 - 2018 - 3.14.2;
e582f1ca-8db0-5fb7-961d-a60dda709771 | button | Is at least one MCP installed in a clear and readily accessible location in the circulation space of the main entrance of the building? | Yes, No
7735e26e-3bb2-52b6-89e6-a4d38d071b0a | note | As per the NCC2022 - S20C4;
1121c232-e6c6-5736-8bf0-62e0b9a53d2d | button | If in a Class 9a building, have you ensure MCPs are located in evacuation routes so that no point on the floor is more than 30m from an MCP? | Yes, No, N/A
0e3880bf-a011-54d7-88af-fc17ab7bafbc | note | Add Photo
193ce79b-3ad1-4b11-b6a7-6a67526e444d | checkpoint | 8. FTRS
92917a11-5bf7-5a82-9bf0-da7136715fdf | note | CIBSE C5.8.0 Modules Input/Output
5d989700-55c0-52d3-b8e8-2b157c27b57b | note | Have all FTRs been installed in correct locations as per latest drawing?
be3e7332-ca20-5922-8448-d22a66cbeca0 | button | Have the right quantities been installed to ensure correct operation as per the fire & mechanical matrix? | Yes, No
e954df62-b5d1-5cbd-b3b3-3b2c1538455e | note | Add Photo
548abeaf-fab2-4573-8da4-329405de07e6 | checkpoint | 9. MAGS
82c691c0-45c7-59f2-b65a-edbc69f3200d | note | CIBSE C5.8.0 Modules Input/Output
354a7bca-75b6-5a7c-beb5-a4a3ab7c68a9 | note | Have the mag door holders been secured properly to withstand the weight of the door?
07a94291-756c-51f1-813f-f3e5e01eaac9 | note | Have they been installed at a uniform height on each door leaf?
be6c8195-1a52-568d-8c9a-c1488bc41588 | button | Has a release switch been installed? | Yes, No
f9d4bab8-3b1a-5700-a8b2-7d88d2cc71c0 | note | Add Photo
eae04e16-58d2-41ee-a58c-095df38e7e79 | checkpoint | 10. MASDS
a9e05bc3-771c-58a1-8583-6405f37d1f73 | note | CIBSE C5.6.0 Sensors/Detectors
ccd86567-3c1a-5bcf-9e56-a1e58401749f | note | Has all pipework been installed in line with the Aspire calculation & design?
e476dea3-3159-5b98-98a9-335077aea33d | note | Has all pipework been glued?
5a321e84-5bf9-52e0-b772-2cb4a67a0de9 | button | Is the head end unit installed in an appropriate location? | Yes, No
1ab39c5f-2358-5c2a-9301-21726e74cdd2 | note | Add Photo
8f257b9f-f671-45a3-9f51-79df3e8f2de1 | checkpoint-no-value | GM Fire Sign Off
671d6674-d246-4fba-9636-3297e006e765 | signoff | GM Fire Sign Off
c1446dc7-5efa-40f1-8e62-4fdbdd930b1d | checkpoint-no-value | Principal Contractor Sign Off
8ba87d03-03ce-4c5e-b777-b4b0b76609a5 | signoff | Principal Contractor Sign Off
ae9e8356-0a50-4d78-9e5c-f4cc76bd12b1 | checkpoint-no-value | Consultant Sign Off
0ce98da0-5d55-4210-9b6a-34df8135d63a | signoff | Consultant Sign Off
1d6f6072-afec-4b03-bc52-8da652a5fc4a | checklist | ITPS-103 Ewis Fit Off AS 1670.4 |  | ITPS-103 Ewis Fit Off AS 1670.4
140036d2-53fb-4435-bbd7-fcad09d2d73e | section | Details
9e0a1b5a-7435-4d10-b032-7e279a2e55b5 | checkpoint | 1. WIP
7fe2c610-a451-5580-8de3-b13aea5ef4ff | note | CIBSE C6.2.8 Warden Intercom Phones
6834d497-1a20-5c18-944e-bd73ea7cf70f | note | Are the Warden Intercom Phones mounted at a height of not less than 1200mm & not more than 1800mm?
0abb9d7c-9bb8-5bec-920e-9704279b0c5b | button | Is there one WIP per EWIS zone installed within 4m of the exit? | Yes, No
6fa9e734-eb9d-5c33-a822-caee93ff57be | note | Add Photo
9672facc-5cd2-4f3b-8a8f-01d8c86774ef | checkpoint | 2. SPEAKERS
61179fcb-e2fb-593c-82ba-657831f45406 | note | CIBSE C5.2.2 Set Points
1a57dea7-73c6-57d0-89ff-121bdf859c64 | textbox | Drawing Reference and Revision Number:
afd05a0e-34e5-5d54-8cf2-28c296e2499e | button | Have all speakers been installed to the latest RCP? | Yes, No
3c4ce441-cdbf-50ce-968b-407ec63580f6 | note | Add Photo
a329dab7-8af2-4c8f-b50b-71e3e49af080 | checkpoint | 3. STROBES
78a0ba92-1b03-5a48-96e9-8f5532bc0933 | note | CIBSE C5.2.2 Set Points
2d40f4a0-8f48-562d-a0fe-ee7a58b389e7 | note | Have all strobes been installed to the latest RCP?
3f66bbac-2fca-5385-80ea-03921b072c4e | button | Have all strobes been labelled "EVACUATE" with 25mm lettering? | Yes, No
e121ccd6-fbbd-5932-9a2d-8fe69525acc2 | note | Add Photo
8bae3ffb-b3fa-47f8-a09e-7901208c1457 | checkpoint-no-value | GM Fire Sign Off
37baedba-14bb-4230-b4b5-644319293065 | signoff | GM Fire Sign Off
5a1a0866-d118-4a35-9d6f-25c9e9ad4365 | checkpoint-no-value | Principal Contractor Sign Off
16cc024b-c787-46d9-8ca7-d3ceeb4a9af2 | signoff | Principal Contractor Sign Off
44199d1d-6f91-4ae8-9270-4c723cb5b24a | checkpoint-no-value | Consultant Sign Off
17ff32ac-31e4-427e-bb49-43df6b901b02 | signoff | Consultant Sign Off
1ac64b4a-5d45-4b8d-8d99-1a5a9775934d | checklist | ITPS-104 Fire Alarm Cable Tray |  | ITPS-104 Fire Alarm Cable Tray
215f9ced-014e-49f2-8052-9a6bb35c25d1 | section | Details
4034f164-bd6c-4b63-bcc0-cf99f0012843 | checkpoint | 1. LOCATION & INSTALLATION
4d8587f5-000d-566e-a7c5-75ab0f20db74 | note | CIBSE C5.2.2 Set Points
c738f113-ec4f-597e-9ff8-5ed03642646c | note | Is the tray as per drawings and model?
cc00a91d-8156-55a3-9182-764d904da500 | note | Have all sharp edges have been removed to prevent injury or damage to cables?
8b0dde1b-6a96-50f2-81c1-50be26cb2001 | button | Is the tray supported at intervals of no more than 1m? | Yes, No
f9692ba4-b559-5333-be63-63f037483586 | note | Add Photo
cff85472-38ff-4d11-b6a8-75e6041ace1c | checkpoint | 2. FIXINGS AND FITTINGS
1cd88b77-bcb0-587d-b615-2e808142ad7e | note | CIBSE C5.2.2 Set Points
4e52e64e-975d-5073-a6a6-9689bcbfd727 | note | Have the appropriate fixings and fittings been used (for indoor/outdoor use as applicable)?
c3afc487-7734-561d-91fd-39b50ffc09ad | button | Are Seismic fixings as per the design documentation? | Yes, No
692bd3f1-57db-53a6-8c91-c2f653a0429f | note | Add Photo
74153ffe-6e27-4437-b2f2-8f8ba3873c7c | checkpoint | 3. CABLE SPACING
690542d2-0923-551c-9be2-08ffa536a1e4 | note | CIBSE C5.2.2 Set Points
957cc120-f30d-5015-8c98-56a0c8d6a35b | note | Generally, where possible install in the following groupings:
4689d412-e490-5c27-b4fa-688cd5e8f286 | note | Detection Cabling & 24v Cabling
7796a93e-81c9-5def-9d0c-7a25b61dbd52 | note | EWIS/OWS Cabling
fdab8f8b-8c64-51d2-b7d0-a1f57631965e | note | WIP Cabling
c3bbaf98-bf6d-552f-9fb6-34e5a619f380 | button | As per AS3000, 3008, and S009, is the segregation of ELV and LV cabling at least 50mm? | Yes, No
638ee7a5-af8f-5c4f-a9dd-edafb32f0e93 | note | Add Photo
ec40fb0f-9bdd-4a1e-8926-1cf58cf370c5 | checkpoint | 4. SEISMIC
90820550-7033-5e65-91d2-fad82c428aa3 | note | CIBSE C5.2.2 Set Points
a88f9c0c-80f5-59c8-9bff-e4f7a2f2928a | button | Has the cable tray been installed as per the seismic drawings provided? (Use of stablity strut or catenary wire may be required) | Yes, No
aabacb58-ba84-5c7d-837a-d345a9aa0dec | note | Add Photo
a4facfd9-ef5f-49bf-a736-4f3b2ed51b69 | checkpoint-no-value | GM Fire Sign Off
cf636fec-9834-4347-ad86-c3b144d7802e | signoff | GM Fire Sign Off
cf1d2121-aa80-4a1f-9f64-379de8bfb4ea | checkpoint-no-value | Principal Contractor Sign Off
53de435e-d56a-44a5-aa7d-d80840bdbe82 | signoff | Principal Contractor Sign Off
8bb38fd0-630a-4c20-8d2f-809b7a666598 | checkpoint-no-value | Consultant Sign Off
20306f7b-bee3-4d59-a582-fb4bf6f23ad7 | signoff | Consultant Sign Off
b07419f6-1bf2-4f7f-810c-621a8b166bcf | checklist | ITPS-105 Fire Indicator and EWIS Panel Installation |  | ITPS-105 Fire Indicator and EWIS Panel Installation
26c55128-58cf-4bc1-9411-dd2f141d5980 | section | Details
c6962101-f454-4104-93aa-d76586b500a3 | checkpoint | 1. LOCATION
7d852d66-8c05-5922-a20a-bb2abecd1db6 | note | CIBSE C5.2.2 Set Points
fa47743d-527c-5238-9538-392ed6cb8905 | note | AS1670 (Section 3.9)
f2464098-6683-58c1-b9bf-8c02a367a039 | note | Do you confirm the CIE is:
4bcc4fb3-f7f1-5383-a041-e8dea5462845 | note | Not in an area used for storage of combustable material; and
6310b0e9-23b7-5826-8dc9-d54bd9fef5b2 | note | Not obstructing evacuation of the building; and
6a36379c-d681-55b1-8bef-b34280e30c40 | button | Not in a room containing sprinkler valves, pumps and motors? | Yes, No
93dff588-56c8-5fb1-9a49-48e51db06bb8 | note | Add Photo
8cfcaca1-2d8e-4cef-9cd6-6f1353071110 | checkpoint | 2. LOCATION
8397f44b-ceb3-5928-b04e-d2884303ba3a | note | CIBSE C5.2.2 Set Points
0c58114b-9167-5835-acbd-fbce165540bc | note | AS1670
6ec6f404-0a95-52db-b7da-1bd2a0e02edc | note | Has a minimum clearance of 1m in front and 0.5m to each side been maintained?
0bcc182a-b16c-5c9a-bc4b-72fe1a4a056e | button | Where obstructed by a door, are the words "FIRE PANEL" in contrasting colours? | Yes, No
0a2c58cd-baf5-568e-80bc-cac752eb664a | note | Note - Where the door reduces the sounder, an external sounder may be required.
869499e2-23cc-5f30-adfe-7d4c6b8b7af9 | note | Add Photo
b34b2fe1-f7ba-4578-8982-26b47d1f063c | checkpoint | 3. CONTROLS AND INDICATION
ac36714f-61c2-543f-84a6-fc1a6b379d70 | note | CIBSE C6.6.0 Brigade Interface – FFCP
8ae55f15-5c9d-57ae-9314-36e061e9df2d | note | AS1670 (Section 3.9)
d1323b01-a766-5782-9a3d-e505d66aeef3 | note | Do you confirm CIE has controls that are:
ecf9f5bc-d92d-5234-8f0b-3f187a35043e | note | Not less than 750mm from floor level; and
183f85d0-b8cc-50b3-b67f-67a2b10b8038 | note | Not more than 1850mm from floor level; and
6fefad70-1a33-5efa-ba23-9bfebd1771ef | button | The access to controls is not obstructed? | Yes, No
ca0562e0-8d2e-5a78-aee4-03f4b6b31dec | note | Add Photo
9c385f32-ad2c-4809-b43c-7f44a66a0bbf | checkpoint | 4. CLEARANCE
8ed31402-49fc-5d8c-a587-01a133a4118f | note | CIBSE C5.2.2 Set Point
a89f0e58-564a-51bb-9a49-9db0215e86f8 | note | AS1670
bea86af8-e03c-57d1-a2c4-df0f6fad63ea | button | Is there a minimum clearance of 1m in front and 0.5m to each side? | Yes, No
0e5c63f0-d0cd-561a-8c76-f0db06529002 | note | Add Photo
7ce5396e-4429-41aa-a95d-302a29224d0c | checkpoint | 5. EXTERNAL ALARM
93cc61e8-6178-58cb-ae97-f16eb143ff34 | note | CIBSE C5.2.9 Alarm Functions
4fe8e63b-81c6-5551-b219-67568eaa6000 | note | AS1670
d24ca950-5a27-53d3-82ec-e30d1f72eea5 | note | Is an external wall mounted VAD is located on the front façade no more than 10m from the DBEP?
de5f2d8c-a175-5556-b506-30060a2fa511 | button | Is it visible from at least TWO directions, and mounted with the words "FIRE"? | Yes, No
12fd5968-e98f-547f-996d-e27f042761b6 | note | Add Photo
bdbe42b2-7253-497f-b00e-c2e8166c1d58 | checkpoint-no-value | GM Fire Sign Off
408d2ee2-a94b-4821-8d0c-31d914c42c66 | signoff | GM Fire Sign Off
bc2e2fe4-0d62-4c21-8516-ca0fe761145a | checkpoint-no-value | Principal Contractor Sign Off
2c26d08f-256e-48e0-83f7-3033b7ecd797 | signoff | Principal Contractor Sign Off
91d35db4-11f5-4abc-ba79-b7e5e76a0394 | checkpoint-no-value | Consultant Sign Off
1cdd63ef-1651-4abd-a0bd-357d8b3dd39a | signoff | Consultant Sign Off
a9ed5c7c-923c-4823-b421-ba2d1177d1ca | checklist | ITPS-106 Sprinkler Pipework Rough In | itp | ITPS-106 Sprinkler Pipework Rough In
215924d2-d433-499c-a5cf-c845604f6e84 | section | Details
3c4865aa-302c-4657-8102-4f5beb32f00e | checkpoint | 1. PIPE LOCATION & HEIGHT
11a064ec-df98-5e3d-a151-f6b388b4645f | note | CIBSE W5.2 State of the System
83612e66-6422-5382-b13a-6eb7f3a79fe0 | note | AS2118.1-2017-Section 14.14
5c2c3017-2a55-576d-88b5-2beb79e435cb | textbox | Drawing Reference and Revision Number:
4d8c1b04-6d63-5e1a-aae7-4dfc2e1d99b3 | button | Have you reviewed the Fabrication Cut Sheets? | Yes, No
21048bde-2c9f-5800-b4b1-b1374084fac4 | note | Is Pipework setout as per dimensioned install drawing?
2310b6a8-450b-5ca9-a3aa-6bcaf9ed1090 | note | Are Pipe heights correct?
981a4660-c37e-5da7-b9b1-538fa79d22f4 | button | Have Pipework alterations been approved and recorded for as-installed records? | Yes, No
0aed974d-e544-5fc1-92a5-3c3e51853abb | note | Add Photo
7728f4b9-9d52-4f44-9890-1244ba6aff00 | checkpoint | 2. PIPE SUPPORTS
c2ff86fa-02c4-5340-b2e2-ca2db2f73867 | note | CIBSE W5.2 State of the System
4aa9cbed-c019-56aa-a7a4-3e8848477379 | note | AS2118.1-2017 - Section 7.8
0e4d027a-ea97-56ad-90c0-1aab34b6e9d6 | textbox | Drawing Reference and Revision Number:
f777ce85-c07e-51b5-a4f1-6275108034f8 | note | Is the Pipe hanger type as per the install drawing?
3b931bf8-052e-5e19-adfd-f9e4f25ffa78 | note | Are Hanger fixings as per the install drawing?
7f738ba6-3d1f-5650-bac7-88ace73b308a | button | Are hangers spaced correctly? (not exceeding minimum spacing) | Yes, No
1d22c9b7-18a5-5f52-833f-bd951381a517 | note | Add Photo
06029a72-4d97-43cb-bd26-f973fee1261c | checkpoint | 3. CHECK GROOVES DEPTHS
80003806-4682-5733-81ad-97eb97570db4 | note | CIBSE W5.2 State of the System
e9bb5d1a-83a5-5995-a546-0b49a56525a3 | note | AS2118.1-2017 - Section 7.1
61b6c3fc-0515-5fe4-8251-95d8440ff91f | note | Are groove depths within tolerance?
49f70f53-2735-58f8-8c3d-8bad3dde6652 | note | Are pipe heights are correct?
0cd47000-1a6e-5b8d-8def-bbf586bed019 | button | Have any pipework alterations been approved and recorded for as-instaslled records? | Yes, No
445acbc0-cc0a-5ebb-9e32-a8e697b06c12 | note | Add Photo
d658fd73-9364-478f-b145-f21b5a878e0a | checkpoint | HOLD POINT
54e0dbec-6e7d-5dd0-8c3a-2ff2bc38d8b7 | button | Confirm Safe to Proceed | Yes, No
44b23c15-8b7d-49da-9222-8fc526016e87 | signoff | GM Fire Sign Off
a7764147-dda0-4cdd-84e6-7071507f2ccd | checkpoint | 4. VICTUALIC COUPLINGS INSTALLED
d35756ee-732c-5c26-b467-387f6626f00a | note | AS2118.1-2017 Section 7.10.2.2
8c35a9f2-6eb7-5d1f-b21f-f29f0af5eec4 | note | CIBSE W5.2 State of the System
dea6306a-dc81-5a31-aaf1-7ef383dad541 | button | Have ONLY Victaulic brand couplings been used? | Yes, No
c98c67bb-23eb-5ea4-ae4c-7f0682787001 | note | Add Photo
cf565fd1-965c-498d-b63b-0c98a25bc1e4 | checkpoint | 5. CONCEALED SPACE SPRINKLER HEADS
1b5de2d0-d907-5446-aaa7-769f7951be2e | note | CIBSE W5.2 State of the System
fc405de3-5b63-574a-a2c7-d38dfa872af7 | textbox | Drawing Reference and Revision Number:
94f3a50c-f37d-548b-b230-e2b7de6b48e3 | note | Have ALL concealed space sprinklers been installed as per dimensioned install drawing?
895f587b-fa71-50fd-8e89-cefed81d27eb | button | Have the correct sprinkler types and temperatures been used? | Yes, No
acc13911-279a-5c9d-99ef-ea50625eb708 | note | Add Photo
9cf981e3-c756-4a0a-bd38-bd023e61124a | checkpoint | 6. EXPOSED SPRINKLER HEADS
734b08c9-9cac-50a4-82a0-68467b36b28d | note | CIBSE W5.2 State of the System
e6072c44-ab87-57c0-942d-3311b3a2fd40 | note | AS2118.1-2017 - Section 5
ea613e1b-9326-5154-ae7f-c86d256dcc43 | textbox | Drawing Reference and Revision Number:
9dfe20b3-4e41-5447-a6f8-37d952981db8 | note | Are exposed sprinkler heads installed as per dimensioned install drawing?
7a0d3761-b9f9-5e7e-833d-9796cfb02cb6 | note | Are sprinklers clear of obstructions?
84ca8b34-7ce7-53b8-a25c-d68d312c9ce2 | note | Have the correct sprinkler types and temperatures been used?
9b5de8d2-97ea-5b13-b284-e50f03f8a466 | note | Confirm sprinklers do not exceed the maximum distance from the soffit?
a5ecfa41-99c2-5aaa-851d-0fefe7dae6b1 | button | Have sprinkler guards been fitted where risk of damage exists? | Yes, No
b5dcaebc-5b45-595d-a3e8-294274bc996b | note | Add Photo
09c207a7-00d5-40e3-a743-962f92fb4765 | checkpoint | 7. FLEXIBLE DROPPERS
e4f58a91-8764-5c81-bfeb-93f08cc582ce | note | CIBSE W5.2 State of the System
2e4ef1c9-ad97-509b-a76f-83f1a56d2cfd | note | AS2118.1-2017 – Section 7.6
4aacce0f-a455-51a6-88fb-684bd0462e30 | textbox | Drawing Reference and Revision Number:
49b3a51d-5a48-5d7b-ab83-8c05ed1fc6bd | note | Is flexible dropper installed in correct location?
cdeaabb0-6a35-5a8c-b31b-450785ddd32b | note | Correct sprinkler type and temperature?
9ca6ae41-9245-51e8-84ef-3a0dc7de001b | button | Is there sufficient length to reach on-ceiling location? | Yes, No
7e1a6086-15c9-5a63-a32e-3f8170d7e8d8 | note | Add Photo
52b336e3-5b2a-4b6a-a9dd-6747c103185f | checkpoint | 8. SPRINKLER INTERFACES - VALVES, & MONITOR SWITCHES
2fb97c83-b8de-510d-a188-f7910c4f159d | note | CIBSE W5.2 State of the System
bbfaf1ea-f555-552b-9e49-360bb1e603d9 | note | AS2118.1-2017 – Section 8.13.5
cf90a039-8b29-5b1b-acc9-1442fed0f93d | textbox | Drawing Reference and Revision Number:
1047e031-7748-58a3-b8ab-89fffe328bd9 | note | Have Isolate valves & flow switches been installed?
61f2ba92-7042-5533-a49a-d093e9bce557 | button | Have labels been installed? | Yes, No
22418d75-3f7b-54ac-85a0-6812006603d5 | note | Add Photo
cf5ceb7e-34db-4962-951f-88beaea96de6 | checkpoint | 9. REMOTE TEST DRAIN
9b3229d8-0db7-54b1-bac2-9051d8f3814d | note | CIBSE W5.2 State of the System
51f19889-97db-567d-b7e8-202e60c07f06 | note | AS2118.1-2017-Section 8.14
ab358dfa-e451-57c0-ba1a-2546a8a4b8d3 | textbox | Drawing Reference and Revision Number:
f8f80c6b-12d7-5a39-ab40-c3026bc90dbf | note | Is the Remote test valve installed as per dimensioned install drawing?
cf0d3bc6-1069-5a93-8d19-b4353ff0d311 | button | Restricted orifice installed? | Yes, No
cf3d8173-dc76-529c-86d8-f74799d56aeb | button | Have labels been installed? | Yes, No
51e151ad-d77f-5dd4-a38d-d5f05cea8ce1 | note | Add Photo
d1514b7b-3ff5-44ca-8347-a4f8a7fa439d | checkpoint | 10. SEISMIC
78644ad4-9fbd-5b70-a363-8ba8fc2bfa6f | note | CIBSE W5.2 State of the System
c27f08cb-4d8d-5c9e-b6d5-f76035e4d477 | note | AS1170.4-2007 (R2018), clause 5.4.6 and section 8. AS1170.0-2002, AS5216-2018 & ETAG 001 PART 6, ANNEX 1.
ad89d53b-6795-5028-874c-9405c0c0fc59 | textbox | Drawing Reference and Revision Number:
b27bb89f-b507-5f93-8abf-a550ac801b95 | button | Are Seismic braces installed in accordance with Engineered drawing(s)? | Yes, No
e6751ecf-ee7d-50cc-90e4-14d00a5f027b | note | Add Photo
ef626bcf-4b5e-576c-ae22-5a4bced9cc82 | note | CIBSE W5.2 State of the System
854629fd-5770-58f7-968a-b45ba7b33b31 | note | AS2118.1-2017 Section 7.9.6
ac3731b1-32f5-599e-95f8-505e4a8f1c9c | note | Has painted pipe been inspected for damage?
cb66fcac-199f-548f-87a2-4ef850dfe7ed | button | Have Repairs to paint been completed where required? | Yes, No
2608c536-772b-577e-88af-c063c89abc63 | note | Add Photo
05aafaf4-acff-40e6-a755-a6b6ded666ee | checkpoint-no-value | GM Fire Sign Off
90fa4121-e09d-422d-8d9b-373727327d02 | signoff | GM Fire Sign Off
8c15b572-7ecc-4c32-80d1-d60813bd746c | checkpoint-no-value | Principal Contractor Sign Off
b1688a41-5944-4a4b-a08c-dd049a231b8e | signoff | Principal Contractor Sign Off
6f3e7029-3c80-4624-b16b-dda0a589d4c6 | checkpoint-no-value | Consultant Sign Off
bb15b888-d946-40de-98a9-7eb435498c72 | signoff | Consultant Sign Off
681a054e-760a-4095-b460-76f4e83a3782 | checklist | ITPS-107 Hydrant Pipework Rough In |  | ITPS-107 Hydrant Pipework Rough In
5bd274c4-ba42-4c7c-8742-818404d48848 | section | Details
f1d226c9-0522-46ec-a657-63b81a62ded6 | checkpoint | 1. PIPE LOCATION, HEIGHT & SIZE
f50b133c-bb97-5296-b30d-7c18cf310dd4 | note | CIBSE W5.2 State of the System
51d9cdb4-7563-5a40-b65d-6f5bfe8b6ec1 | note | AS2419-2005 Section 2
52be3d3f-bbc0-5a1e-828f-71c85268135d | textbox | Drawing Reference and Revision Number:
9e8addaf-416b-521f-8a91-db739065ce45 | note | Is pipework setout as per dimensioned install drawing?
1b1993ee-85ca-503a-ad8f-097c45169dda | note | Are pipe heights correct?
8a01ba86-bad8-54e0-a673-cd325c526876 | button | Have pipework alterations been approved and recorded for as-installed records? | Yes, No
bdecb786-842b-5094-b6fe-8bb795621f41 | note | Add Photo
c73db4e5-3e5a-4b62-99ab-d2468591a9c4 | checkpoint | 2. PIPE HANGERS
6516157e-fff7-5247-9ca7-569a76ff1c48 | note | CIBSE W5.2 State of the System
e221231d-374e-5552-be08-4d84275d708f | note | AS2419-2005 Section 8.7
8ba0c18e-331f-5a6c-9f1b-fb5e3885720b | textbox | Drawing Reference and Revision Number:
d7686c9a-03cb-5881-a16f-441a325f9c3b | note | Is the Pipe hanger type as per the install drawing?
84d4248d-4a2f-50f1-aadd-0710821e4499 | note | Are Hanger fixings as per the install drawing?
94201d9c-e56d-5b64-9c0b-30c2b55040f1 | button | Are hangers spaced correctly? (not exceeding minimum spacing) | Yes, No
5af21f99-4e7e-5bae-8e75-fef3f93c18e9 | note | Add Photo
e81a43ed-257b-442e-adcf-6dcc0b6e81de | checkpoint | 3. CHECK GROOVES DEPTHS
c1f384e0-b468-5adf-bc2b-2188e2dcd6dd | note | CIBSE W5.2 State of the System
0de8d8f4-7652-510c-aa99-71da2dbe1b3a | note | AS2419-2005 Section 8
069d81ee-ef42-5736-bb1f-cdba1235e524 | note | Has Victaulic Groove Tape been used?
95bb5f0c-76ca-5995-9163-453b8d9f74cd | note | Are Groove depths are within tolerance?
218e63f1-1079-579c-b07d-2b59d1537a15 | note | Are Pipe heights correct?
3c2c7886-63f4-54e8-9841-942e38a8d9af | button | Have Pipework alterations been approved and recorded for as-installed records? | Yes, No
f50266f9-27f2-57b9-99ea-f2ad1aef1648 | note | Add Photo
62def17f-2cab-46b8-999b-f9a1a83de3a3 | checkpoint | HOLD POINT
22dd7145-ba34-5544-af76-3b957987f234 | button | Confirm Safe to Proceed | Yes, No
fa4ab5f1-db57-4117-bdc8-931602b251a0 | signoff | GM Fire Sign Off
12861439-5090-4ada-a9d3-107d048106ae | checkpoint | 4. VICTUALIC COUPLINGS INSTALLED
a11b01b1-df5d-5abb-b598-96235749103d | note | CIBSE W5.2 State of the System
037fbb1c-b4a7-5b55-ae4c-a5fab375e3ea | note | AS2419-2005 Section 8.3.2
d21edf9f-dc99-5b1f-b581-9e96f8747637 | button | Are Victaulic brand couplings the only couplings that have been used? | Yes, No
890e24ff-7851-5416-b674-e9e84e12fec2 | note | Add Photo
c6311fd9-6e6a-46f6-ad88-76021665a0e3 | checkpoint | 5. ISOLATION VALVES INSTALLED
a4262809-011d-5cf9-96a0-84e24f1b3cb4 | note | CIBSE W5.2 State of the System
36b47c42-429b-559f-a7ba-44c215b0e681 | note | AS2419-2005 Section 8.5.8
582dcffd-6084-5428-9d31-13ebcbcf85a5 | textbox | Drawing Reference and Revision Number:
960fd094-b0d0-5d41-bdae-ff71f4f68404 | button | Are Isolation valves installed as per install drawing? | Yes, No
172610db-bff4-5cc0-8f3c-47bee468b4dd | note | Add Photo
37e74954-4abf-4bee-9326-d220ffc035bd | checkpoint | 6. SEISMIC
31834c19-17e7-548d-af47-810a898a668f | note | CIBSE W5.2 State of the System
05ad9e39-e2d8-51b1-ae9a-246b793267a7 | note | AS1170.4-2007 (R2018), clause 5.4.6 and section 8. AS1170.0-2002, AS5216-2018 & ETAG 001 PART 6, ANNEX 1.
8a127a75-cf55-51c9-b8e7-adedaf4135a8 | textbox | Drawing Reference and Revision Number:
55dfb6ed-8fc3-5f5e-a38f-54fa1e7c216a | button | Are Seismic braces installed in accordance with engineered drawing? | Yes, No
71ce3f4f-bcb9-5597-ab26-f8240b2f8c1c | note | Add Photo
3a1d1411-8fbd-4072-83bf-2cb907bdc934 | checkpoint | 7. CLEARANCES
8477a131-c08d-506e-abcd-a27f7a8ebbf8 | note | CIBSE W5.2 State of the System
0fed9e4e-5962-590f-973d-0f68f5f0d946 | note | AS2419.1-2005 – Section 3.2
0b3edeea-6260-5a28-afed-f4bd003f4bd3 | button | Is the Hydrant positioned so it does not obstruct required clearance for egress path? | Yes, No
97f63bde-8ab3-5211-b521-ce3650711a87 | note | Add Photo
4d2eab08-8f7f-4d53-88d9-f7c19dd393f3 | checkpoint | 8. LANDING VALVE FIT OFF (CLEARANCE HEIGHT/ ANGLE)
8ae71666-bfbc-5182-ac3f-ca0ec994f9f4 | note | CIBSE W5.2 State of the System
ccdb52f0-f5e5-5bc1-a998-4f035eea6fc6 | note | AS2419-2005 Section 3.5
f11be4ff-0620-5f5d-a690-606d7fee3e6e | note | Have you checked:
d515b925-64c8-5011-9485-80eb76a5c8fd | note | Landing valve height; and
61854bb5-5374-5ef3-be0e-771e067936df | note | Landing valve is at the correct angle; and
f512fb90-f2e4-5287-a29b-02d9b5b63a46 | note | Coupling angle and orientation is correct; and
f34a2389-2068-5c5d-b752-071568d3af4e | note | Required clearance for the handwheel has been maintained; and
341d09b6-67ec-548f-9f0a-693f5c33ecfa | button | The required clearance for the nozzle has been maintained? | Yes, No
4aba7d17-32b6-59f5-ac5f-4ab3ac82ad0e | note | Add Photo
07597f8a-6b71-4754-8428-7115eb97442e | checkpoint-no-value | GM Fire Sign Off
1c82a82c-1a31-49c1-bc66-80fcbba1589e | signoff | GM Fire Sign Off
47498a09-7811-46e3-9115-7a2d0830491f | checkpoint-no-value | Principal Contractor Sign Off
d2b7467f-7d5c-4264-9fa6-e01fba76cf6e | signoff | Principal Contractor Sign Off
3fcb109f-b866-48d4-a776-c03f8867a35d | checkpoint-no-value | Consultant Sign Off
dff8e5b0-852e-4eeb-a836-33d080ad3fdb | signoff | Consultant Sign Off
90f292df-395b-4d6c-bfad-23ce92dfe0c6 | checklist | ITPS-108 Sprinkler Fit Off |  | ITPS-108 Sprinkler Fit Off
3b1f3e1d-f0dc-40ae-8409-7761d6211374 | section | Details
44e01334-c498-4edd-b67a-706737ccfd11 | checkpoint | 1. SPRINKLER LOCATION
c20eaf59-5e3a-5188-9f0d-fa5cc54445e8 | note | CIBSE W5.2 State of the System
2f0642e0-d335-5a78-b236-b8e9be0b4037 | note | AS2118.1-2017
0db0e7c9-c13c-59a9-9e7a-c93868d62e8e | textbox | Drawing Reference and Revision Number:
22fec056-e99d-599a-892c-009f3bd0d39c | note | Is the location as per dimensioned reflected on the ceiling plan/ install plan?
3a0d4d03-3f6c-5b33-ad78-9b48f4523b44 | note | Are the Sprinkler temperatures and finishes appropriate for the environment?
d26623cb-cfed-5b99-95e1-382d7cdc71b3 | note | Maximum spacing from walls is not exceeded
cbd567f4-7e3e-5493-ba3a-bff190e5e073 | note | Is the wall spacing within requirements?
57689bff-c0dc-5204-b362-7d85840c2806 | button | Is the spacing between sprinklers within requirements? | Yes, No
d7dbcb4e-c2f5-5142-8a87-9bdfe77a6399 | note | Add Photo
00985fad-dd6b-4be9-9205-162b12ed22fb | checkpoint | 2. SOLID SPRINKLER DROPPERS
431e0088-fec7-5a85-86a7-c0768e93d959 | note | CIBSE W5.2 State of the System
b4c49798-d429-5bc2-a1a9-08713341b8cb | note | Is the arm piece supported by hangers?
77c41b17-5977-5183-b64e-9358c4a151d0 | note | Is Dropper square?
0369bbbb-8fdc-50c5-b2e9-032b643ae798 | button | Is the finished sprinkler height compliant? | Yes, No
2fcf4abb-cac6-5b93-986a-cb13a98759d3 | note | Add Photo
0e723b12-53c6-48a2-ad1f-fa45ec26a166 | checkpoint | 3. FLEXIBLE SPRINKLER DROPPERS
cafd2728-2754-5c66-b672-a14ed72a6860 | note | CIBSE W5.2 State of the System
98696e65-bba8-599a-92f1-df1a61e136b4 | textbox | AS2118.1-2017
7365e66b-5aca-5680-bbcd-1c295d815a8d | note | Has the appropriate lengthed dropper been used?
24b7aca9-cd2b-5d31-95fc-f97861f2bfb0 | note | Are Sweeping bends within tolerances?
739b2265-1974-52bf-8100-35d8bbbd53d5 | note | Was the correct bracket used to secure nozzle?
7ee1b77c-38dc-5672-b816-cf79c21bb186 | button | Is the finished height compliant? | Yes, No
df3c8603-c7bd-59f3-848b-2f96bd2c9ae9 | note | Add Photo
9cf4739d-0007-41c2-ae8e-e4e857f8b3c6 | checkpoint | 4. OBSTRUCTIONS
5d3d7f58-35b2-54f6-b4a3-dec873acfe2b | note | CIBSE W5.2 State of the System
3083daa5-766c-5d1c-8b27-cfd586bc3c34 | note | AS2118.1-2017
a683d51a-d971-5b41-84a6-fd63ab8e5b74 | note | Has minimum clearance been maintained for 'On Ceiling' obstructions?
aa847a8a-88a1-5654-8f10-b320756eb7e7 | button | Has minimum clearance from sprinkler been maintained for 'Below Ceiling' obstructions? | Yes, No
e90e5ea6-a512-5be1-b2cf-c592d2a963bc | note | Add Photo
0e118526-1d2b-4525-92db-78c4ace84b9f | checkpoint | 5. ESCUTCHEON PLATES
433e0293-cdf4-56fd-bc1b-b3b44eb1a4cb | note | CIBSE W5.2 State of the System
1217e941-8e8a-5436-8bfa-b0de12c376b5 | note | AS2118.1-2017
ba2a14d6-30c3-5a58-a233-e5f6b9527103 | note | Have outer escutcheon plates been fitted?
49225782-2853-537c-aa9e-13040730191a | button | Is surrounding ceiling clean? | Yes, No
b049111c-0186-5fe2-97b2-33f14b6a0fb3 | note | Add Photo
1f06f8c9-741b-4d00-881d-0d9e79429b91 | checkpoint-no-value | GM Fire Sign Off
56d52454-17df-429b-9e2e-62bceea89258 | signoff | GM Fire Sign Off
18e7f913-7cd3-4c90-b2c3-9babf5e2af55 | checkpoint-no-value | Principal Contractor Sign Off
02046678-6ce5-4d43-9e43-2583ad693097 | signoff | Principal Contractor Sign Off
2fcb4df0-a428-4acb-b311-b230a84eacbd | checkpoint-no-value | Consultant Sign Off
08011afc-a403-4957-bede-d8bdd45a95f2 | signoff | Consultant Sign Off
05075f61-1837-4a77-881b-b881baa106d0 | checklist | ITPS-109 Portables Fit off |  | ITPS-109 Portables Fit off
9769c824-261f-4491-8d9c-ad48e20477a0 | section | Details
858a7077-cd54-4604-bfd4-101debf00a0f | checkpoint | 1. FIRE EXTINGUISHERS - GENERAL LOCATION
4f483315-3df8-5ecb-9daa-a971703b9ec5 | note | CIBSE C5.2.2 Set Points
45bae984-ba5d-5384-8942-c969ded9b5ff | note | AS2444-2001 - Section 3.2 states extinguishers shall not be located in positions where access could present a hazard to the potential user.
c10f3f59-9531-50d3-9034-df909ca6ba72 | note | Is each extinguisher located in a conspicuous and readily accessible position?
40fee86c-272a-511f-8f96-dc3ee56f7991 | button | Where practicable, are extinguishers located along normal paths of travel and near exits? | Yes, No
edab6f76-d64a-58d5-8335-4fcc53836434 | note | Add Photo
05011592-3878-4e63-b037-267ac4f78b73 | checkpoint | 2. FIRE EXTINGUISHERS - MOUNTING DETAILS
30b85968-3c44-59c5-8e9e-6901c2e1f81e | note | CIBSE C5.2.2 Set Points
8e0d760e-e041-5c5f-aa54-9f4af5370cdc | note | AS2444-2001 - Figure 3.2
5a06482e-e457-5bf9-9aac-8541f8f84d9b | note | Have Location Signs been installed at a Minimum of 2000mm off the FFL?
a05e0690-5713-565a-85df-4364b092829d | note | Are extinguishers installed at a maximum of 1200mm to the top most part of the extinguisher?
72082168-fe5a-5c4a-8878-54469f15592e | button | Are extinguishers installed at a minimum of 100mm from the FFL to the bottom most part of the extinguisher? | Yes, No
528632ea-41d5-5a53-b780-ce9f85f3b371 | note | Add Photo
de84c917-4007-49a1-8653-db75b8f8bcec | checkpoint | 3. FIRE EXTINGUISHERS - VISABILITY & SIGNAGE
65a9ed5a-ff27-54e5-ab28-488cefe51c4f | note | CIBSE C5.2.2 Set Points
11e62430-d8c6-53e0-8f81-64aab1735f91 | note | AS2444-2001 -Section 3.4
ce1f58de-8d96-55e6-8195-ce44b6b6dc68 | note | Are extinguishers, or extinguisher location signs, visible from a distance up to 20m in all directions?
2e5ac9b9-34f6-564a-ba4a-f57fd5db0f37 | button | Are the location and type of extinguisher signs installed as required? | Yes, No
31a34468-f4b4-5459-8f47-01a4d17dd9c1 | note | Add Photo
8a0cf29c-c749-4208-a3c2-cf1d73667b98 | checkpoint | 4. FIRE BLANKETS - GENERAL LOCATION
5ab40522-da82-5c9b-8c31-30a3004db4ac | note | CIBSE C5.2.2 Set Points
68da5168-b475-5ee2-b09e-a5d37bf4ea42 | note | AS2444-2001 - Section 6
d4f4d782-8abf-569c-94f1-ff4aab932989 | button | Are Fire Blankets installed in a readily accessible position, and not in a location where access could present a hazard to the potential user? | Yes, No
b02e808a-88b0-5b0e-b63a-be95dc9f33e6 | note | Add Photo
03b5cfe7-4268-474d-8832-af4a51bbd74b | checkpoint | 5. FIRE BLANKETS - MOUNTING DETAILS
632bcf7a-8721-5816-b57f-c864da517b3d | note | CIBSE C5.2.2 Set Points
e2eb2020-cf0a-5254-a43a-99009d0bcd7a | note | AS2444-2001 - Section 6
95ac4d47-443e-57ae-a54a-3bd69d2202b0 | note | Have Fire Blankets been mounted to withstand the loads imposed when removing the fire blanket from its container?
159d4b15-0ec7-5442-98c3-9381defe5580 | button | Is there sufficient room so that fire blankets can be quickly removed without impedance from nearby obstructions? | Yes, No
2d98cfa2-3b9f-54c8-a1f5-70a1630124bf | note | Add Photo
f4edebcb-7ae6-414b-9ad2-afadcf88800f | checkpoint | 6. FIRE BLANKETS - SIGNAGE
b8df1ae2-c6c3-5227-b866-c7071a647cfb | note | CIBSE C5.2.2 Set Points
f56edc60-bcd5-5393-a898-a7083c8ce754 | note | AS2444-2001 - Section 6
590a908e-4a8f-5e27-803a-f6a23f36f3a4 | note | Are signs located above or adjacent to fire blankets?
8250349a-e0ba-58f1-a4de-f131d244d34e | button | Are signs 2.0m above floor, or at a height that makes them most apparent to the average person? | Yes, No
788b079f-33cb-5467-be6b-3da7b25213d7 | note | Add Photo
c27f5bfc-6082-4f2e-af5d-0272fd9c4dbc | checkpoint-no-value | GM Fire Sign Off
0960981a-979f-49e4-a43a-5e5759f2839a | signoff | GM Fire Sign Off
5fc42704-f545-4c0e-8c0c-73f017582ac8 | checkpoint-no-value | Principal Contractor Sign Off
f51ff344-f270-4ee4-9dc5-f4b4fe43b123 | signoff | Principal Contractor Sign Off
671fed2d-00ab-4e21-824e-2df5fdb1cb42 | checkpoint-no-value | Consultant Sign Off
60a5c935-990d-4a0c-98f0-c5d8f4ef51fe | signoff | Consultant Sign Off
567cfb81-0b4d-48bf-84cf-0df949521439 | checklist | ITPS-110 Valve Set Installation & Fit Off |  | ITPS-110 Valve Set Installation & Fit Off
79628cdc-7edf-4653-9173-051543470351 | section | Details
a82035e1-3009-408e-b4ec-9713bdb1c685 | checkpoint | 1. UNDERGROUND SUPPLY
e83f0559-2ba2-5a5c-8db9-6f2caf0ba124 | note | CIBSE W5.5.2 Flushing Procedure
43334a69-f631-55c4-bb7b-857cfe9f6ccf | note | AS2118.1-2017 - Section 7.9.7
021c2415-42c5-56d1-a730-60417224b60a | button | Has all supply pipework has been flushed by a hydraulic contractor? | Yes, No
becf7188-8cac-5a33-bf10-393a8e5f533c | note | Add Photos
9877f61b-bc70-4f7b-bb78-3c2b9f4ddadd | checkpoint | 2. CHECK GROOVES DEPTHS
aa981ff2-ee91-525d-94f6-76bc956dca61 | note | CIBSE W5.2 State of the System
9ca6cac0-c7ea-59ac-b572-3dd32b22f2ca | note | AS2118.1-2017 - SPRINKLERS: Section 7.1 | Yes, No
2b662d6f-cd27-5cc6-8fc5-80ebe2b5fd07 | note | Has Victaulic Groove Tape been used?
36e6ec18-bd4d-58c5-b3d6-e8d7cc1effe2 | note | Are Groove depths are within tolerance?
698a491e-6c2d-5b86-bcb1-71a1f5c7ec06 | note | Are Pipe heights correct?
04ee1988-58e0-56da-b2f0-714f1ea8d9e4 | button | Have Pipework alterations been approved and recorded for as-installed records? | Yes, No
0b861cae-38c4-5b21-bea5-b397fb549fee | note | Add Photo
c7690f52-d02f-4aca-98bd-1fe680dfc5c2 | checkpoint | HOLD POINT
8d40aa40-4037-5709-949b-ba16dfc3fefe | button | Confirm Safe to Proceed | Yes, No
5ec69a30-2ac0-4650-bb4d-173c1cebe0e1 | signoff | GM Fire Sign Off
a6ecaf08-8a87-4f30-a0f9-4f6e1402668b | checkpoint | 3. VICTUALIC COUPLINGS INSTALLED
10a86a19-de5b-54ad-8705-3c4818f028aa | note | CIBSE W5.2 State of the System
4bdb78cf-346f-5ddf-b58c-a1e4c60b2969 | note | AS2419-2005 Section 8.3.2
79d39ee5-10c7-55ea-a3d0-9d338b7abbea | button | Are Victaulic brand couplings the only couplings that have been used? | Yes, No
87836f86-b9c2-5799-99e2-65d9e11d2711 | note | Add Photo
46539fa7-86ab-4279-ab14-767bfd0b8c94 | checkpoint | 4. CONTROL VALVE ASSEMBLY
869aa5c4-f845-5c6b-9a7d-f7c095276367 | note | CIBSE W5.2 State of the System
db969982-4a9a-521e-9795-624eaf28b66e | note | AS2118.1-2017 - Section 8.1
5100c726-de2a-53d3-9df0-bac87cd616c5 | textbox | Drawing Reference and Revision Number:
8f88728b-f2f7-5e52-a04b-5d739015f880 | button | Is the assembly is installed as per drawing? | Yes, No
c4c9b4f9-81d3-5ada-af89-5bdbe3c03726 | note | Add Photo
4131d8bf-1604-4f55-9881-26ad792d92d0 | checkpoint | 5. PIPE SUPPORT
5464344e-c336-5f57-a14a-97eaf1ca39da | note | CIBSE W5.2 State of the System
f7c1e3c8-13a4-59b5-aa12-d7e90987748e | note | AS2118.1-2017 - Section 7.8
35531109-65b5-55b3-8d12-293fa46b976c | note | Are pipework supports as per drawing?
3556fbf8-4dff-5d7c-a570-308c8d3cce54 | note | Are the supports capable of supporting assembly weight?
f68f84fc-7581-5d23-9b7e-1b637d34c48b | button | Are the supports capable of withstanding forces during operation? | Yes, No
b72c08c0-c0f7-57d1-b820-211702dfb388 | note | Add Photo
efcaaa5c-0db6-4b5c-9cd3-9e2105300837 | checkpoint | 6. VALVES
62cda3c5-83ac-5364-a297-35a74238b505 | note | CIBSE W5.6.2 Mechanical Checks: Automatic Control Valves
fe149b1a-ea2b-5ef3-852a-a05764d69e6e | note | AS2118.1-2017 – Section 8
51606f2b-b72b-5e8e-9269-17e26a4f0edb | note | Are Valves installed as per drawing?
43251d9e-4312-55a7-8472-5afd84a9af61 | note | Are valves are installed in the correct orientation?
414bb49c-b948-5a1d-b070-5916f2e0e8ba | button | Does the clearance allow for manual operation and future maintenance requirements? | Yes, No
043e39ab-83f2-5710-8bb8-4af6549147d0 | note | Add Photo
ae1e6464-362f-4010-92f3-507b69c3d19c | checkpoint | 7. INTERFACES
a1e029a2-23c8-5b18-ba83-abc38e1a7a6f | note | CIBSE W5.6.2 Mechanical Checks: Automatic Control Valves
a953ddeb-3614-529b-bee1-41641e12fe04 | note | AS2118.1-2017 – Appendix H
5b0a0ab3-a966-5630-939d-38f03e87ca99 | note | Are valves/switches installed for connection by other trades?
e97ff9ff-657d-53b2-b576-3e46a5f74777 | button | Have clearances been provided for connection? | Yes, No
9c8e5536-589b-5383-8a80-b5cd9f26d16f | note | Add Photo
81895e48-e535-4ad0-bfa8-7ee538410d52 | checkpoint | 8. PAINT / FINISH
6231f861-db4b-5516-9f41-c575939c6d1f | note | CIBSE W5.2 State of the System
9210b530-5b81-5b01-9a7d-8e33e075ccae | note | AS2118.1-2017 Section 7.9.6
61709f2b-17d1-51e2-81c4-2e0fca2c9958 | note | Are exposed mild steel pipes painted gloss red (unless specified another colour or galvanised pipe)?
cc37c386-1fc7-5b47-92ef-9bfe93d8f340 | button | Have threads been de-hemped and tidied? | Yes, No
0c8b6a4e-5378-5d3c-bb67-83e3d843114a | note | Add Photo
bf10ed1e-979f-52a4-b4d6-381bf5b28e32 | note | Add Photo
e4738428-688f-4ac8-99eb-f0e8ad630371 | checkpoint | 9. SECURING VALVES
d35f4aac-ddaa-5f9c-8ade-ddd6c10e580c | note | CIBSE W5.2 State of the System
c4441a51-1e97-57f3-a0aa-f2c4bda2c08f | note | AS2118.1-2017 – Section 8
01e443e5-a493-5684-aa17-ace3deba9812 | note | Are valves secured by 003 locks?
65c600f6-82d0-5e68-a0ee-877ee57037fa | button | Have straps and chain been installed? | Yes, No
bdbe0589-2ab6-590f-9efe-0c3eb43d45f9 | note | Add Photo
70456378-4f57-4daa-9f47-33ab1232a8a1 | checkpoint | 9. SECURING VALVES
005c4e0e-3ca0-5418-a87b-6dec9c6487f0 | note | CIBSE W5.2 State of the System
97f50b7d-7942-58b6-bf1c-bc0ed5bd8d57 | note | AS2118.1-2017 – Section 8
5caffe89-d958-506a-a6d8-dfcf5f3eaaa5 | note | Are valves secured by 003 locks?
05f05429-a036-5bb1-a62f-b1fb8423c278 | button | Have straps and chain been installed? | Yes, No
b97f6328-d559-5f3d-82b9-d20f63148229 | note | Add Photo
6e7dce68-279c-4c59-832f-6f67bf730ae8 | checkpoint | 10. LABELS & SIGNAGE
3aa32def-afce-5894-af04-5301020c562e | note | CIBSE W5.2 State of the System
8f46e0f8-b900-5976-80bb-09d6ef169396 | note | AS2118.1-2017 - Section 3 (3.3.4)
0ae25068-7076-5c51-8b14-982abe32728e | note | Are Equipment name labels secured?
4b572740-1080-5745-b3dd-6ae967908836 | note | Are Valve position labels secured (normally open / normally closed)?
7e5b022c-9f8a-57ac-a036-4de1e39915e5 | note | Have "Sprinkler Stop Valve Inside" signs been fixed at the valve set enclosure entry?
b6f7fb8a-7df5-564e-a52d-82d9b0bfc09c | button | Has the Sprinkler Block Plan been installed? | Yes, No
31f97fc4-797d-5419-93c3-63cbea519106 | note | Add Photo
e8046de8-59df-4954-a9a7-0d286f59c8ef | checkpoint | 11. SPARES
f0fbf8aa-5544-5abe-9707-4c91d83dcb94 | note | CIBSE W5.2 State of the System
33a6e7db-dcc0-52c2-953e-51e3ae4be7e5 | note | AS2118.1-2017 – Section 6.7
37b80b73-6ba8-5c2f-af8a-04f1df642191 | note | Has the correct size sprinkler spares box been installed?
9ad61261-311a-5c40-9045-486083dc0735 | note | Have the correct number of sprinklers been provided?
78433a2a-31db-5e0e-aed0-873b69fba652 | button | Has a sprinkler spanner been provided? | Yes, No
04f331f0-6c69-5c3c-8dbe-054ac949962d | note | Add Photo
5ed2559d-3fc4-4f19-9699-8a73100d75de | checkpoint-no-value | GM Fire Sign Off
9c2c973a-0e25-4334-8ee8-de9fe32258fc | signoff | GM Fire Sign Off
47c85462-24b0-455a-9b31-180b56c4baa0 | checkpoint-no-value | Principal Contractor Sign Off
2184d34c-fc21-426a-9589-4e107b49bfb7 | signoff | Principal Contractor Sign Off
0622af77-1900-4149-83f6-96dad32f651c | checkpoint-no-value | Consultant Sign Off
a2280107-6084-404f-937c-5de9365923b7 | signoff | Consultant Sign Off
6ddcaf2a-e874-4d12-b75d-333652fc92dc | checklist | ITPS-111 Tank Installation |  | ITPS-111 Tank Installation
533e1274-07f3-4cf2-a5ca-e2ac190f978c | section | Details
0bff288c-a060-4506-932e-cc1596605415 | checkpoint | 1. LOCATION, CLEARANCE, ELEVATIONS
694af5ba-e966-561c-9d0e-f9818474b6f9 | note | CIBSE W5.5 Pre - Commissioning
786445df-ced8-516c-a965-e39e689c3250 | note | AS2304 - Water Storage Tanks
89885499-0155-5d79-a3c8-a585ef4555a6 | textbox | Drawing Reference and Revision Number:
ec5f0150-89f8-501b-9fb8-8493e522ea10 | note | Are Structural Elements as per AS2304 – Section 3?
a1679bf0-26ec-521e-a149-c4fc4f195983 | note | Is the correct Installation drawing onsite?
9d660fa6-7931-5fe4-b026-cabe5e4aae32 | note | Is Ladder selection and orientation as per the submitted design drawings?
b06abb03-eaf9-5ff0-95af-3778aa8eb8da | note | Is Nozzle selection as per submitted design drawings?
8def7db7-a974-5585-9758-78e3df8b7cd3 | note | Has the poisition of the Tanks been confirmed with the Principal Contractor onsite?
0fa7f7c6-7b1b-5c3f-8149-d2b6873105b0 | button | Have you check the subcontractors Competencies and Authority to work? | Yes, No
f05968d6-2cfa-53e3-851e-df437659f52f | note | Add Photo
58878ff5-d1b1-47fe-a892-b093572a3831 | checkpoint | 2. COMMISSIONING
4d3d3570-0229-51dc-982d-769a344cf56d | note | CIBSE W7.10 Commissioning Certification
370a8514-507f-5bad-9797-c19ffc615c11 | note | AS2304 - Water Storage Tanks
c0f482ec-1909-50f3-9c03-5894e51de0de | note | RECORD, CHECK, INSPECT
82258a60-6544-585e-95f1-839a53f4e9aa | note | Structural inspection was complete prior to filling; and
3c7f1bc4-c2da-5037-a01b-783ed8fc5965 | note | All ladders have been inspected for conformance and clearances and position of tank accessories (AS2304); and
1190d1b7-2d1a-50cc-af6b-7dfecbf8cc0d | note | Hydrostatic inspection was performed after tank is filled to maximum capacity; and
8119e1f1-96f6-5957-8aba-dbb461923a6f | note | Any defects have been recorded; and
df54f24e-79c6-56e1-ad83-7b97909f1184 | button | Have Certificates and warranty periods been submitted? | Yes, No
9e4da74f-7d7c-5ab2-a971-dc73bb4d9390 | note | Add Photo
f5723470-d69c-450e-b53f-c186a504150c | checkpoint-no-value | GM Fire Sign Off
e2c010f7-71a8-4745-ab85-7c54f12e132b | signoff | GM Fire Sign Off
4873f1a6-4a73-41f6-b6a3-530fd796670a | checkpoint-no-value | Principal Contractor Sign Off
33cfe3cd-e365-45d8-af37-6f8780c906ea | signoff | Principal Contractor Sign Off
d9e12cba-91d9-4e52-9e37-0d0aa391fbbf | checkpoint-no-value | Consultant Sign Off
1d3b9ad4-f92d-4c2a-a374-1c74196161d5 | signoff | Consultant Sign Off
bca0a7a7-026e-47e7-968a-afbc86713979 | checklist | ITPS-112 Deluge Rough In and Fit Off |  | ITPS-112 Deluge Rough In and Fit Off
344d1551-1736-4a4f-a0e6-81c9628e5ff1 | section | Details
fb4954aa-f640-4169-ae17-e7d8a8ac721a | checkpoint | 1. LOCATION - VALVESETS
3edb83a2-1b0f-5f96-bfce-e7d58f39bc35 | note | CIBSE W5.2 State of the System
47ddd8d6-cbd7-5d21-a2c1-896812c099c8 | note | AS2118.3
48aefcee-af99-5372-892b-547aaa650216 | textbox | Drawing Reference and Revision Number:
24c77284-4fa8-5ad4-a6dc-ee4659df7b2a | note | CHECK:
b9917a4d-90a7-5260-a726-5c9f14417384 | note | Valves located outside building shall be considered protected if the external wall has a FLR of 60/60/60 or be situated at a minimum distance of 10 m from the wall.
8bb188f6-ac25-548b-b64f-286f53c50d63 | note | Valves located inside the building shall be situated at a minimum distance of 10mfrom the perimeter of the protected area.
16306186-23f1-5637-9e36-3c3dbabe47f3 | note | TRANSIT TIME:
6494af44-ba69-508c-a9f5-35597d504157 | note | Deluge valves shall be located as close as practicable to the system they are controlling. This will help ensure that the transit time to the most remote zone is no more than 30 s.
57dea1fc-676f-5b5e-ba51-62a557b0d6d4 | note | Add Photo
6fc8eb9f-da74-4270-b8eb-767ab8605cb5 | checkpoint | 2. LOCATION- DELUGE HEADS
f0dec8e5-1504-5b0e-b523-632bf07efe4d | note | CIBSE W5.2 State of the System
bcb2d119-3cb0-5cb3-947e-e8e501efa5bc | textbox | Drawing Reference and Revision Number:
6a78ea2e-240a-5adc-8b32-d8ad5a211d02 | note | Are Deluge heads located as per dimensioned reflected ceiling plan / install plan?
00ab9959-b9de-5bda-b128-cbd05e207d6e | note | Confirm sprinkler temperature and finish are appropriate for environment; and
0893d966-e488-5d39-98e8-a8b01a02395e | note | Maximum spacing from walls has not been exceeded; and
670d691b-deab-53f0-bf0b-d635fa22b2ae | note | Maximum spacing between sprinklers has not been exceeded; and
a817b23c-056e-5221-b963-40722f1c4f4d | button | All is as per manufacturers detail and FER? | Yes, No
44ff7830-f4c4-5458-af0b-8b829474a7c9 | note | Add Photo
533e822a-cba6-48a4-9347-c47af429b59e | checkpoint | 3. DELUGE HEADS & PIPEWORK
bd8be3d2-dc05-53c0-aecf-243b1e977314 | note | CIBSE W5.2 State of the System
d11dd337-9fe6-5b14-b1e4-67dcd853b615 | note | AS2118.3
0d9e7b87-0d5e-5ccd-88d2-94cfba71e386 | note | Open sprinklers are be nominally 15 mm or 20 mm diameter, and either upright spray (SSU) or pendent spray (SSP) pattern only.
69439ccc-979d-53fd-8de8-d01f615ecb99 | note | Deluge system pipe and fittings not normally filled with water or foam solution shall be hot-dipped galvanized.
deca8208-8641-5d86-bd3d-6510b04d7feb | textbox | Deluge Sprinkler Head Type:
3f6a392d-0a5a-5283-8a0b-d8564c608454 | note | Add Photo
bcab0821-ecdc-488d-9ea9-b3a4fef32031 | checkpoint | 4. WHERE SPRINKLERS ARE USED AS DETECTORS - SYSTEM PARAMETRES CHECK
b8983b9c-31ee-5ddc-9079-8b54e41698f3 | note | CIBSE W5.2 State of the System
b79e1a80-7dc3-50be-bcfb-9d1cd2889d8a | note | AS2118.3 Section 2.9
ea78e07e-6e69-5639-bbb0-57f180f6cbee | note | Where sprinklers are used as detectors, ensure the piping layout shall be designed to ensure a response time of no more than 20sec after the operation of the most remote sprinkler or manual operation.
08aace81-b5fd-5db0-b168-7488ffeabca8 | note | Manual control shall be located at each deluge valve and at a strategic point/s within each zone.
6924df0e-495c-5d53-b2cd-3bd1615d66b8 | note | Deluge valve trim shall be in accordance with figures 2 &3 in AS2118.3.
d7c8a704-eb9b-558c-a8df-0e1cf0e52407 | button | Ensure a remote test drain line is installed (close piping deluge systems) | Yes, No
593b7b09-c327-5b81-a41f-1339f2233f4d | note | Add Photo
dba86c41-0072-4060-a345-bc1b8f9b3798 | checkpoint | 5. SOLID SPRINKLER DROPPERS
40b50a8c-e69c-5bd9-a91b-6c3f388a6752 | note | CIBSE W5.2 State of the System
79ce4a46-72de-577a-9d49-cb86a2f1fa60 | note | Is arm piece supported by hangers?
8497591b-316f-5541-b241-9cb7c3070b03 | note | Is the dropper square?
a04f9736-c5e7-538c-84ec-f82976a92248 | button | Is the finished sprinkler height compliant? | Yes, No
d75b8a25-64a4-5580-b5bc-a19f2d95ec2f | note | Add Photo
783c6c0d-196c-44cc-acc3-cba4d7b68493 | checkpoint | 6. OBSTRUCTIONS
ee0fdc57-3b8d-5fbb-a357-1f3106959a15 | note | CIBSE W5.2 State of the System
50c2b4c1-eb76-5466-885f-51ea4bfebe80 | note | Has minimum clearance been maintained for "On Ceiling" Obstructions?
c4b8635f-eba2-5d85-a063-7b308bfaac92 | button | Has minimum clearance from the Sprinkler been maintained for "Below Ceiling" Obstructions? | Yes, No
6f8c70d9-e32e-4b72-94fb-4c87e3db459a | checkpoint-no-value | GM Fire Sign Off
4d757a17-5cda-4ac8-9dfa-8d1f4929f4db | signoff | GM Fire Sign Off
d01858c5-2b49-4e3e-8b1d-20390aae7504 | checkpoint-no-value | Principal Contractor Sign Off
07ec8836-69fc-40db-a373-bd260d97c01c | signoff | Principal Contractor Sign Off
2848bb99-a11d-47ed-aab3-8e9e8b984296 | checkpoint-no-value | Consultant Sign Off
8d76322f-a472-46c6-9cd1-d16921210507 | signoff | Consultant Sign Off
85e242de-3b66-47f5-9ea3-1f6d56dca6d5 | checklist | ITPS-113 In Slab Sprinkler Sleeves |  | ITPS-113 In Slab Sprinkler Sleeves
57b5bdcc-ae49-4f65-bed3-ff2d7f4c41ca | section | Details
794e2a5e-7e00-4974-b183-16f8cf5baadd | checkpoint | 1. TYPE, SIZE, QUANTITY - CHECK
821c7649-1724-56c8-a426-7237baf8473e | note | CIBSE W5.2 State of the System
16d8a9c5-f7a3-5775-b9e0-39898a3c8e5e | note | AS2118.1-2017
fde6c663-d2a6-575b-af02-ffac4077df2b | button | Are sleeves the correct size, type and quantity to criteria and specified drawings? | Yes, No
990a8070-ae4c-5786-8cec-ad6aa9eca6d8 | note | Section 9.5.2
4049d779-8f5f-5753-83c5-b6fb1c4905c5 | note | Has pipe with a minumum DN 25 been used;
81f6cca8-397e-580c-a35f-70d6af941831 | button | Or where a pipe supplies a single sprinkler protecting an external balcony, canopy or carport, or supplies a single exposure sprinkler, a minimum of DN 20? | Yes, No
5a9740eb-4069-5378-a0fd-927d440b0702 | note | Add Photo
0c0a0ff0-fa80-4f5f-8e07-51155bd3cc31 | checkpoint | 2. LOCATION - CHECK
90898548-b100-5486-9913-9b0ab8e9de35 | note | CIBSE W5.2 State of the System
715f85a6-1b48-5348-834c-66177fa13375 | button | Have sleeves been installed as per specified layout and design criteria? | Yes, No
1fef486f-f605-5b83-b237-96d01bf6f99c | note | Add Photo
b1a52fe6-b48a-47ba-a907-09c3515b4106 | checkpoint | 3. INSTALLATION - CHECK
64c59348-fd42-5edb-8cb6-ea02a51cf739 | note | CIBSE W5.2 State of the System
b3a63f59-1d34-5ec3-ba83-411139bea95a | note | Are sleeves joined correctly and tied in?
c08f7a96-84a8-5bcf-8a36-ea3ead96135a | note | Have sleeves been checked for damaged?
9bf92d2f-9f86-5aaf-969e-72363cae0810 | button | Have you ensured sleeves are not resting on form work? | Yes, No
b9425232-0d21-5f12-9a0a-447f7b22de67 | note | Add Photo
bcb28bb0-f791-45e6-b5f1-72ede1c8cbab | checkpoint-no-value | GM Fire Sign Off
cb403c98-44b1-4b22-8fe1-84bb4b0387b2 | signoff | GM Fire Sign Off
8ab27011-193e-4204-9708-03077b074c60 | checkpoint-no-value | Principal Contractor Sign Off
0c891e29-00b2-48bd-8671-dc1bae79e9d6 | signoff | Principal Contractor Sign Off
ed7e4030-7b35-4b7b-96d0-ff76f924ae2f | checkpoint-no-value | Consultant Sign Off
3744b141-5ee6-4d1c-845b-5a6d54bb07bb | signoff | Consultant Sign Off
39fdedc4-4d42-43d0-b53d-967bc3e3b4b3 | checklist | ITPS-114 ASD Rough In |  | ITPS-114 ASD Rough In
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
951f2448-f255-435d-9ccc-afe917ef8210 | checkpoint | 1. LOCATION
7df20633-1d08-5170-b3ac-e1b42d8b7f0e | note | C5.2.2 Set Points
2fd9f97d-915a-5d49-909a-8b8eb27da926 | note | AS1670.1
66af5395-088d-5587-af6b-20373b40d453 | note | Have you check that the ASD device does not cover an area great than 2000m2?
60c0ece8-a444-5f27-b37e-a35b35c6bf1d | note | Is the ASD unit in an accessible location with no obstructions?
fd28fa82-966d-5587-bd6f-fdaf4e598723 | button | Is the ASD unit free from damage? | Yes, No
70f06354-f236-53a6-8f58-a1020f050c69 | note | Add Photo
e3b9bbaa-547d-4021-a635-16b46f338eb0 | checkpoint | 2. SAMPLING POINTS
d65a152a-fba4-5fbd-bb75-8a05d5c8cd1b | note | C5.6.0 Sensors/Detectors
dad14f5f-862b-5404-8fce-9a679cd010ac | note | AS1670.1
df1edab6-f389-5ca7-843a-4adbef4c0d86 | note | Are ASD points unobstructed, unpainted and free of burrs?
cc5a2a5e-7832-592d-9ad5-663d4c0a2be7 | note | Have ASD points been labelled and identified as required?
0e9f0440-a004-529f-99e4-c8deace68eca | note | Are ASD points installed in accordance with spacings of point type detectors?
18c83e51-74f0-52a0-8acd-a8d519c1a376 | button | Have you confirmed ASD points are no more than 600mm below ceiling? | Yes, No
8354d343-c9ac-5571-9e24-0acc5acbe9d4 | note | Add Photo
028dade2-994f-454b-8096-de12c9899e7d | checkpoint | 3. EXHAUST
755872e4-9aaa-5219-862f-3df3c0cf4a25 | note | C5.6.0 Sensors/Detectors
0fd19434-8c23-5410-8123-82d32ddd4cd7 | note | AS1670.1
0e7b8cad-13c5-5913-9064-3c532cf4ee58 | note | If the ASD is mounted outside the protected area and the potential for pressure differentials can occur between the sampled and exhausted air:
d1161729-da4d-51f8-b0ee-85b36c9b3459 | button | Are the exhaust outlets returning back to the protected area, or as per system design? | Yes, No, N/A
b083fb4c-b31f-597f-bbf8-4b2891c8d78c | note | Add Photo
8cb47156-2394-47bd-bce0-69bf30f624ba | checkpoint | 4. OTHER INSTALLATION REQUIREMENTS
059f2a05-2d46-51b3-ba58-ef82a3ff67a1 | note | C5.2.2 Set Points
7215bbb2-84ff-5073-9944-2da56de6f1b6 | note | AS3000, AS1670.1, AS3013, AS/CA S009
dffbcbba-632c-5b49-9176-805e02aa7fab | note | Are all sampling points AND capillaries red in colour OR have visible red stripes at least 2mm wide at intervals no more than 2m?
af59efa7-0f09-576c-afca-fb82081da28c | button | Is the pipe orientated to ensure identification of markings is visible? | Yes, No
7dd422cb-7c83-5457-acac-f7dc3bfd4fcc | note | Add Photo
9b1f9e83-363d-43b9-9245-f7ddfde494bb | checkpoint | 5. CABLING
8b74338a-7397-528b-a575-da4d20d00a67 | note | C5.4.0 Wiring
b5abcd27-a18b-58ff-98be-4e674a02ea3a | note | AS1670.1, AS3000
ea760c7c-3a9b-5087-9030-8fa1a09adff6 | note | Is the cable installed the correct size & type?
888e395a-0988-5b54-8440-29a21980e024 | note | Has cable been secured at regular intervals?
844fc97a-d347-5a61-81e2-d2b594c747ab | note | Has 24v cabling been installed where required?
a80e8d75-96b6-5d8b-91db-9303d7f1c437 | button | Is the power supply in accordance with AS1670.1 Cl 3.15? | Yes, No
77b55e93-0d36-5a3b-b64e-60d04d67a66b | note | Add Photo
0fe0eaf6-b6c0-46a1-8cd4-25a49c93a6e6 | checkpoint | 6. PIPE LAYOUT
e85d5241-f5ec-5565-b893-ffc4c870788c | note | C5.2.2 Set Points
ac559116-f53f-5c07-bd9f-e5da7e6223dc | note | AS1670.1
94bef180-27c4-599b-9ac5-88ff9db1c887 | textbox | Drawing Reference and Revision Number:
7199167d-7d24-54aa-a9ae-77bd3f476864 | note | Is the ASD pipework as per Aspires or Calculations?
28641ec4-1f75-5964-8fc4-b5477b04625f | button | Have you confirmed the pipework layout with measurements? | Yes, No
f02d14ea-34ce-58de-8f56-eefcb983642f | textbox | PROVIDE measurements:
07ffeb21-fb1a-55f3-896b-a525bf9d64d5 | note | Add Photo
8b364e82-d4fc-41c5-995d-eefa8016d8a3 | checkpoint-no-value | GM Fire Sign Off
9450cd5e-71d2-48fd-9720-c4208b572b55 | signoff | GM Fire Sign Off
c5e501c1-b83b-49d6-b4bb-321505e56dbe | checkpoint-no-value | Principal Contractor Sign Off
3f5541e6-26d3-4c95-9e02-2864c84c1c26 | signoff | Principal Contractor Sign Off
72b688f7-74da-4a6d-b500-28d6f358cbf1 | checkpoint-no-value | Consultant Sign Off
b28f9ab4-cf2b-47ad-ae02-e99434498a43 | signoff | Consultant Sign Off
e61dd2c5-ffde-442e-a9ff-57162eed07fc | checklist | ITPS-200 Fire Detection and Alarm Commissioning |  | ITPS-200 Fire Detection and Alarm Commissioning
c239f723-a7fe-4c04-9b53-54cfd1de8a29 | section | Details
024ccffc-99c6-4cbe-a3a6-6d432e79dfe3 | checkpoint | 1. CONDUCT 100% TESTING OF ZONING
ee4315a0-a0f2-56c8-a313-de8efcae8fe8 | note | CIBSE C5.2 Dry Fire Commissioning – Automatic Controls
6a3f5b07-0919-5ccd-ada7-4935f6ee6384 | note | CIBSE C5.2.9 Alarm Functions
7050b410-6dbb-52fa-964f-a63e1bc7a73d | note | CIBSE C5.6.0 Sensors/Detectors
9d031fe8-8f9e-5706-98ef-86b6265d39e7 | note | AS1670.1-2018
bb5aaffc-ad57-526a-a1b3-1135fd8a6f25 | note | Are Detectors activated when tested?
ed50b36c-5020-55f1-98b3-469d0230f9f3 | note | Do indicators function correctly on Detectors and FDCI?
97682f82-5c6f-50f1-b895-87ed83f73730 | button | Has "GMF-COMRPT-001 Fire Detection Zone Commissioning" been completed? | Yes, No
eae6f826-794b-54c6-9612-5a1db8fef866 | note | Attach relevant photos and a copy of GMF-COMRPT-001 below:
bbb41a36-34c2-49b3-a0db-23f134735b94 | checkpoint | 2. CONDUCT 100% TESTING OF SMOKE AND THERMALS
13c49489-a7d3-5b57-80f9-09c7b1f2fc7d | note | CIBSE C5.2 Dry Fire Commissioning – Automatic Controls
c1b45a94-88b5-5aa9-89d9-1fab528c097e | note | CIBSE C5.2.9 Alarm Functions
b59bcacd-e82e-5872-b516-0e18b3352ac0 | note | CIBSE C5.6.0 Sensors/Detectors
ab5c3cbb-5ac1-5b9f-8721-fc0cb38c0ec5 | note | AS1670.1-2018: Ensure Detectors are activated when tested and correctly indicates on the detectors and at the FDCI
284a3830-3347-5eb5-9651-f6474b05019b | note | Are Detectors activated when tested?
0db8c70e-5bbb-556e-bb20-b702bbd2e315 | note | Have all dust covers have been removed from detectors?
08255c05-1a3b-58fe-9b29-4d0f0e95f723 | note | Do indicators function correctly on Detectors and FDCI?
0eeba058-f5d1-59d5-9691-2015438b2bca | button | Has "GMF-COMRPT-002 Fire Detection and Alarms (Smokes, Thermals, Duct Probes)" been completed? | Yes, No
5cc2903d-b82a-55da-be4f-398671212ee2 | note | Attach relevant photos and a copy of GMF-COMRPT-002 below:
532698bc-d7bd-45c5-829c-790edf4b6a81 | checkpoint | 3. CONDUCT 100% TESTING OF MCPS
e6b24fb9-420e-52ca-990a-620a085b23d4 | note | C5.2 Dry Fire Commissioning – Automatic Controls
f0d20b2f-ec83-522c-836a-a0861bc9b5ac | note | C5.2.9 Alarm Functions
6cdc37fc-76b3-59de-b538-3877d5e40cfe | note | C5.10.0 Manual Call Points
81dae59f-72af-549f-b6d8-e3b83182d227 | note | AS1670.1-2018
c947558a-88b2-594c-b24b-3d449f2ae676 | note | Have you checked:
e15340e2-a999-5f3d-9d91-77ae9283fe61 | note | The correct operation of each manual call point; and
4519505c-74d7-57de-a0bd-4e640e103cfa | note | That the activation of manual call points on the same circuit as other actuating devices does not cause existing detector alarm indications to be extinguished; and
e00bedf5-51fb-5d3a-8afd-676d1a96b5b6 | note | That manual call points are not subjected to alarm dependency; and
c589eeaa-8cb7-5e0c-a1c0-a7df200069b0 | button | Has "GMF-COMRPT-003 Manual Call Points" been completed? | Yes, No
e5677c8c-e001-5980-a2f6-28173c4cdc55 | note | Attach relevant photos and a copy of GMF-COMRPT-003 below:
f6109c1c-b92c-42ba-9a4e-1226cff0b024 | checkpoint | 4. CONDUCT 100% TESTING OF DOOR DEVICES
c628d8f7-5ee5-5d02-bfea-2ce0120e3a53 | note | C5.2 Dry Fire Commissioning – Automatic Controls
595f6322-f423-52d0-9a58-b494283e83fa | note | C5.2.9 Alarm Functions
906f19b0-de04-5305-92b8-727ae6b77442 | note | C5.8.0 Modules Input/Output
b22c70b0-e68c-5bb1-93c2-1774c1a3dce0 | note | AS1670.1-2018
c134d9f0-2f1b-5ef6-8d91-7575606d26b7 | note | Has the operation of each device/door release been checked after install?
ab8b3d12-5204-546b-9377-699d2e5488b2 | button | Has "GMF-COMRPT-004 M.D.H / Auto Door Commissioning" been completed? | Yes, No
ad7c6af8-7e9d-5597-a366-25795a4b9534 | note | Attach relevant photos and a copy of GMF-COMRPT-004 below:
547b2d13-a9e0-4b9d-8932-49e3ec04ad24 | checkpoint | 5. CONDUCT 100% TESTING SPEAKERS AND ZONES
ea379239-a723-58ba-82d4-47fbed2e928a | note | C5.2 Dry Fire Commissioning – Automatic Controls
e05ef984-25c2-551d-87c3-f1ca5c4458bf | note | C5.2.9 Alarm Functions
c2967f53-1b24-541e-8a82-9c2a1d712c55 | note | AS1670.4-2018
1fe1e43e-3764-5e92-845c-c19354b94026 | note | Have the audible signals, visual and tactile signals been checked? (automatic operation)
93d3ffdf-c790-5b06-b321-82a05e95053e | button | Has "GMF-COMRPT-006 Emergency Warning Commissioning" been completed? | Yes, No
97032364-8f9e-5a88-a68a-c23b8c465cde | note | Attach relevant photos and a copy of GMF-COMRPT-006 below:
7572b4db-a447-4f4b-b9ea-d6672eedf236 | checkpoint | 6. CONDUCT 100% TESTING WARDEN INTERCOM PHONES
bba5166f-2ad0-5b0e-95be-9d7b4bd883fc | note | C5.2 Dry Fire Commissioning – Automatic Controls
c25f4dee-d3a0-5abb-97af-ea40418ccf75 | note | C6.2.8 Warden Intercom Phones
1eb0fd7d-1508-5dc8-88fe-4804e6e34adc | note | AS1670.4-2018
db839ce9-add9-518a-961d-edf861501d41 | note | The WIP audible call signal shall have a SPL of not less than 80 dB(A) when measured at a distance of 1 m from the WIP.
1cb056ce-54cf-56ce-bf6d-549150a4cdb0 | note | The SPL of the WIP handset audible call signal shall also be met when the WIP handset is mounted within a security enclosure.
97be055d-ee4a-583a-a7c4-8fff7d6612cc | button | Has "GMF-COMRPT-007 Warden Intercom Point" been completed? | Yes, No
458bf145-0d24-5df7-b028-085c8c260202 | note | Attach relevant photos and a copy of GMF-COMRPT-007 below:
a9969a1f-6ffb-4658-9b23-d585f622a90e | checkpoint | 7. CONDUCT 100% TESTING CASCADE AND EWIS ZONING
098cab9d-7da0-5a56-98ce-bca8a211abc6 | note | C5.2 Dry Fire Commissioning – Automatic Controls
54aa94f6-2af7-5bbc-bcbb-bc89830105f9 | note | C6.2.5 Cascade Sequence
23d2cd17-290b-516a-a23c-18532266c0a2 | note | AS1670.4-2018
0cf9e9f8-0e9b-565b-917b-ed636c68768d | note | Have the audible signals, visual and tactile signals been checked? (automatic operation)
9322515e-b61e-524e-a3a7-c00c5440c4a6 | button | Has "GMF-COMRPT-005 Emergency Warning Cascade and Matrix" been completed? | Yes, No
9f346b0b-6b55-584e-af91-a7505aa3ad68 | note | Attach relevant photos and a copy of GMF-COMRPT-005 below:
f08f590c-6bba-4b84-b8e0-448a07fcdd16 | checkpoint | 8. CONDUCT 100% SPEECH INTELLIGABILITY TESTING
764745e8-54d8-5e50-9de8-5df83bc3dff2 | note | C5.2 Dry Fire Commissioning – Automatic Controls
14df95de-ac1f-564c-9492-b6cebcdf2a1d | note | C6.2.5 Cascade Sequence
64787a93-e66e-5f3e-8b18-b2debad2437c | note | AS1670.4-2018
7209b08a-a7cf-5ebf-b98c-18f8c69ffbee | note | Have the audible signals, visual and tactile signals been checked? (automatic operation)
808d621e-2af1-5a85-b397-2261978f044f | button | Has "GMF-COMRPT-008 Speech Intellegability Readings" been completed? | Yes, No
32fe1f6c-989d-56b6-82f5-9da78003563f | note | Attach relevant photos and a copy of GMF-COMRPT-008 below:
de6fc352-a993-45d1-9754-1827f8dd9cfe | checkpoint-no-value | GM Fire Sign Off
26ebffa2-7960-4930-b61c-5ff8aa3295c0 | signoff | GM Fire Sign Off
5fa71dc0-4153-4828-ba65-06a58172b2c4 | checkpoint-no-value | Principal Contractor Sign Off
0f9490fc-f510-4cc3-a826-24c6fef25902 | signoff | Principal Contractor Sign Off
700dd228-dc17-4761-8756-ba3ebd18fd90 | checkpoint-no-value | Consultant Sign Off
282a8e49-d248-4921-b582-aaf3bde5d41f | signoff | Consultant Sign Off
7479bfb1-fc68-4d19-8661-d34f82c5b643 | checklist | ITPS-201 Interface Commissioning | itp | ITPS-201 Interface Commissioning
f0ba96ec-6b7d-494d-833c-b6550ebba335 | section | Details
90727fe0-9cff-4748-a34a-dd27cc8a0276 | checkpoint | 1. CONDUCT FIRE MATRIX TESTING
e73e4734-b3ef-5168-931a-23a145c7b3b5 | note | CIBSE C6.2.4 Fire Matrix
29290f95-a6c7-5e51-bec7-50d214777c49 | note | AS1670.1-2018
6a7e7bce-c753-5c00-973a-21166ae4f13f | note | The ‘end-to-end’ test should include the activation of associated detection devices to confirm that all required functions operate correctly in accordance with the system interface matrix.
8670498c-5599-5f8e-b134-6a60e3a011e4 | button | Has "GMF-COMRPT-009 Systems Interface Matrix" been completed? | Yes, No
3ede0f24-e283-5a07-8a8b-cc8e9f42644c | note | Attach a copy of GMF-COMRPT-009 below:
23fe5f68-8416-4933-b079-3809a094bf22 | checkpoint | 2. CONDUCT FIRE FAN CONTROL PANEL AND BRIGADE INTERFACE TESTING
41a37762-9715-5f7e-94a1-6a38c911da86 | note | CIBSE C6.6.0 Brigade Interface – FFCP
9867413e-06a6-5545-a871-6d97c7fb7afb | note | AS1670.1-2018 Appendix A
e3ec352d-5c5b-5921-a54f-3cd4663de436 | note | Check Fan Control Operation as per Matrix.
22c9f3eb-ec57-5f7a-a719-9bd1e93f6b93 | button | Has "GMF-COMRPT-010 Fan Control Matrix Testing" been completed? | Yes, No
9211b871-c501-5564-bab7-3337597e324a | button | Has "GMF-COMRPT-011 Fan Control Overrride Controls" been completed? | Yes, No
26c0a4da-76d0-5404-9a02-bed9cc74da29 | note | Attach a copy of GMF-COMRPT-010 and GMF-COMRPT-011 below:
2312e616-5dce-4c90-8777-62510f97475b | checkpoint | 3. SPRINKLER INTERFACES FITTED OFF
182cdda9-0040-5d63-a786-ad7fa76d61e0 | note | CIBSE C5.8.0 Modules Input/Output
0f3b372d-e185-5f97-afe5-3d7952894713 | note | CIBSE C5.2.9 Alarm Functions
30e7ce3c-18da-59f9-b4ee-16733dec0b9d | note | AS1670.1-2015
eaa20771-eab6-5e06-874d-550cceaedd86 | note | Prior to any interface testing, have you checked all systems listed in the system interface schedule are complete and operable?
b9f6689d-0339-51fa-9ed2-e2a9e3d410d0 | note | Have you checked all systems interfaces to the FDAS?
3d531b4c-b75d-5474-9ab9-b8788fb9bd0d | note | Has "GMF-COMRPT-020 Sprinkler Zone Commissioning" been completed?
1294c68f-e8dc-5e42-9787-90e45087c0eb | button | Has "GMF-COMRPT-021 Pump and Tank Indication" been completed? | Yes, No
6618248a-4e9a-5b5c-a072-593d6a181bcc | note | Attach a copy of GMF-COMRPT-020 and GMF-COMRPT-021 below:
c2a20429-7f6a-48e4-9874-8b60813ef98c | checkpoint-no-value | GM Fire Sign Off
067f3c2c-e8c6-46c8-bd5a-b72f3dcc1f5a | signoff | GM Fire Sign Off
92592e89-b9a1-428d-8276-a76cc69f182d | checkpoint-no-value | Principal Contractor Sign Off
f13abdbc-2322-4323-ad32-47bc99940335 | signoff | Principal Contractor Sign Off
35c9c86b-5922-49fb-8ee4-a202cd941bb7 | checkpoint-no-value | Consultant Sign Off
753db100-530a-4a2a-90ed-dcefc6d6086b | signoff | Consultant Sign Off
5fde217e-1f7e-4037-a122-8c231f0df5c6 | checklist | ITPS-202 ASDS Commissioning |  | ITPS-202 ASDS Commissioning
dcccfc99-78a3-4ec1-9b6d-308b9b6257e8 | section | Details
08deffb4-b636-4c8c-83ec-213f0d32646f | checkpoint | 1. VISUAL INSPECTION
6af49052-1bf4-50c6-944a-eb00442c318e | note | CIBSE C5.6.0 Sensors/Detectors
78263802-9930-51e3-8bf6-fb8f0ab646fd | note | AS1670.1-2018 Appendix A
071a24a5-6471-5c56-b6ad-b4af95c1371b | button | Have you visually inspected every sampling point to ensure it is not obstructed? | Yes, No
09e3a85c-e519-52e6-84f6-fa63cfd8190e | note | Add Photo
0da9be4c-977e-41b7-9597-2894338a8dff | checkpoint | 2. ALARM TESTING AND TRANSPORT TIMES
73af8985-f5ef-5ce3-8378-e430ba97debf | note | CIBSE C5.6.0 Sensors/Detectors
1b842952-7e18-5523-97d3-e94fb748d017 | note | AS1670.1-2018 Appendix A
343d5f36-a20d-5282-9abb-a954e3ef0a31 | note | CHECK AND RECORD
9e2292b1-aa3a-50d5-b4a5-7d09f0cfafdc | textbox | The response of all capillary sampling points using a test medium placed at each sampling point:
f84afb27-eb4d-5a45-84da-286e29f831c7 | textbox | Measure and record transport time (TT) from the EACH sampling point:
c07ef504-59e4-5a5e-b755-407933aee053 | button | Has "GMF-COMRPT-012-ASD Commissioning" been completed? | Yes, No
74f5ca98-ab01-5530-9d0e-ff806f95e902 | note | Attach a copy of GMF-COMRPT-012 below:
fd1b5055-283e-4bb6-b4cb-64aa822b65fa | checkpoint | 3. OPERATION - ALARM, FAULT AND ISOLATE
8c6a0c7a-856f-51ac-a889-30f6ef107c84 | note | CIBSE C5.2.9 Alarm Functions
12407f69-5d64-5c6f-a614-3345a979c7ee | note | AS1670.1-2018 Appendix A
4b5a11dc-df97-574b-9ba4-a5d280da0529 | note | Have you checked:
ba6872e8-3307-5f64-b022-1f28904ca052 | note | The operation of remote indication of alarm and fault signalst; and
9fac8b82-7701-54dd-abe9-1d140a7fa0be | note | The operation of airflow failure indicators; and
dd6fb008-b735-5354-9b8d-5d140e62ae4f | note | The operation of the system failure indicators; and
8a5c7532-775e-5312-96d2-67c91b988ae4 | note | The isolate and reset functions; and
b1b1cbda-0967-51b8-b42c-312eec69dc35 | button | The fault and alarm test facilities (where provided)? | Yes, No
6c0643c3-27ef-4532-a8db-b37a28189dba | checkpoint | 4. ASD MATRIX (If Applicable) - Including Thershold Testing
5130212b-ed91-51cd-a24b-97b92deb5926 | note | CIBSE C5.2.9 Alarm Functions
2e09d3c7-f4cd-5c71-b9b6-2514ecea1106 | note | AS1670.1-2018 Appendix A
9a374001-d118-5e96-bb5a-71527401f428 | button | Has "GMF-COMRPT-013 Double Knock Testing" been completed? | Yes, No
8df71c7e-cc34-5245-a4ac-6cc2944ecd28 | note | Attach a copy of GMF-COMRPT-013 below:
482ddcb1-f57a-45a3-b2a2-8d954c441a29 | checkpoint-no-value | GM Fire Sign Off
517ce48a-75da-41db-be86-d83ebb3211f1 | signoff | GM Fire Sign Off
36b9b6ae-0930-4639-8201-23a235260c4d | checkpoint-no-value | Principal Contractor Sign Off
b17c3735-a792-4e2e-b65e-2f72fdafb72a | signoff | Principal Contractor Sign Off
c311689c-de38-4bad-9cf9-edb707ebcd4a | checkpoint-no-value | Consultant Sign Off
f7834bb1-0945-4b76-97e3-8570bf7079c1 | signoff | Consultant Sign Off
602c1777-996e-4f4f-8b26-971b669dce5a | checklist | ITPS-203 Pipework Pressure Testing |  | ITPS-203 Pipework Pressure Testing
6f6d8ca9-eedd-4180-b62e-d839dc4ac278 | section | Details
1de96cfd-012a-49cb-963e-eab85ca6bfe6 | checkpoint | 1. SCHEDULED TEST IS APPROVED - CONFIRM
052a5cb1-d896-5a3a-a50b-65ad918ea01d | note | CIBSE W5.5 Pre - Commissioning
c4b511ce-5633-58b6-8310-c3c3534dd73c | note | Have you received Approval for test time and location?
b958a41d-384c-5c15-b268-b46adc162a27 | button | Has the site been notified? | Yes, No
19e52452-0124-5eda-8094-8686ce21efca | note | Add Photo
bb18b0f8-15bb-442f-85ca-445fdb2f7da3 | checkpoint | 2. EXCLUSION ZONE - CHECK
8760b917-a843-51c0-b40b-ededba3cc7cb | note | CIBSE W5.6 System Checks
fa2c3db0-4780-5e66-81fe-78ad95a479ed | note | Has an Exclusion zone been set-up?
e2161e7e-ff5b-5db1-bc9e-692718524059 | note | Have you erected appropriate barriers and signage?
0b41453f-229e-59ac-b7af-cf227c43560f | button | Have all workers/occupants been notified and have they exited the area? | Yes, No
81023e64-4d5b-532e-bd15-5120f44bf669 | note | Add Photo
b7b4d761-6730-4a69-bb92-54efb5dd4320 | checkpoint | 3. VISUAL INSPECTION - CHECK
5ff7f7ec-ce62-57c6-ba40-9ad4dbf6a832 | note | CIBSE W5.3 Check before Filling
1d4b91a9-e6d2-5373-a0f8-0c4ba8e36505 | textbox | Drawing Reference and Revision number:
08034ccd-a51e-5f80-80fb-f7fa9fae1efc | note | Is Installation complete?
73205271-fe7a-5e14-81a3-dca863eb2367 | note | Have End Caps been fitted with lockable ball valves? (BLANK END CAPS MUST NOT BE USED)
b52f1351-635c-569d-ab76-2c51f421696f | button | Are all outlets sealed? | Yes, No
f7a30235-eae9-5e06-8e2d-e4b40dda759b | note | Add Photo
157b65b2-d0f4-4098-85f4-a928b0361a35 | checkpoint | 4. FIT TEST PUMP AND CALIBRATED GAUGE - INSTALL
be2dc54e-48ee-5606-8368-6ab46744bd5b | note | CIBSE W5.3 Check before Filling
27f33472-832b-5ce6-b7e8-06bfb4b26550 | note | AS2118.1-2017
46e265ea-052b-5c4b-8227-3a3c0ee93e19 | note | Is the Pump installed in a safe location?
cf7a847b-ee5e-5b88-98d6-7d507c586930 | note | Is the Callibrated gauge in visible location, and accessible to photograph?
52715ad8-9340-5d79-a95b-784624321a4a | button | Have the Pump and Callibrated gauge been tested? | Yes, No
b1b10b72-7558-5f44-bbca-0bda7b97bc74 | note | Add Photo
d2882727-13ce-4d0f-bb67-5a5139d45ab7 | checkpoint | 5. CONDUCT BREATH / LUNG TEST
22f43c53-fdcd-587e-8507-5de412f712bd | note | CIBSE W5.3 Check before Filling
68f470d9-84f7-5d24-a953-0afabf67df4a | note | AS2118.1-2017
828dd799-ed32-5948-a14e-3df0dc0f058a | note | Perform Lung/Breath test where possible;
7df8782a-24bd-5627-8dfd-0ccf31366248 | button | Is the system sealed? | Yes, No
653c8944-081a-50c7-8701-7019f393f20a | note | Add Photo
6cc85bf3-26a9-412b-90b6-c6a40fd87a5b | checkpoint | 6. FILL SYSTEM - STATIC PRESSURE ONLY (OR AIR PRESSURE)
92b70cc4-6e00-5dd3-a613-358ee91d599a | note | CIBSE W5.4 System Filling and Venting
b46111dd-54a7-592b-8fd5-f768aaf244c7 | note | Prime system to towns main pressure OR 300kPa (depending on test);
d57922ab-ca35-5fb9-82c0-f256c0892985 | button | Are there any leaks in the test area? | Yes, No
912e8b4e-b71b-5548-aaf1-3341bd721923 | note | Add Photo
efe4a48e-c3ca-4514-bd72-f317ee705a51 | checkpoint | 7. START PRESSURE TEST - CHECK
4052cc50-c24c-50e5-9804-a39235454d79 | note | CIBSE W5.4.1 Pressure Testing
5a9c9a6b-7efe-5904-90bc-6501028c7c5a | note | Increased pressure to 600kpa start pressure;
6bd8b6bf-d43c-52c8-b96b-3f83e60f6a4e | button | Are there any leaks in the test area? | Yes, No
be49329f-4e21-5d1a-8153-fabc762b947d | note | Add Photo
dca5c9cb-e6b5-43e1-9aca-ebf529c1f55f | checkpoint | 8. INCREASE PRESSURE
f58ca306-3cb8-5aff-a76c-c81ea633a75b | note | CIBSE W5.4.1 Pressure Testing
2acfbacd-1ba5-5ec6-80b6-657c9412b336 | note | Progressively increase pressure in 100kPa incraments; and
2b7cdb2d-6a8d-5a75-920f-eb24fa14bcf0 | note | Inpect test area for leaks at each increase; and
c466a20f-b410-507f-b605-7da711debcb1 | note | Repeat until pressure reaches 1600kPa;
1285b532-5bf5-5461-9e1d-4c1a15315c74 | button | Were there any leaks in the test area? | Yes, No
b7a1283e-18f6-5de1-a397-1f8191a2133e | note | Add Photo
64771fd3-e101-497d-bdc7-7e64db16a14d | checkpoint | 9. HOLD PRESSURE
7962d713-3f8e-5ff1-9c84-f849907e14e7 | note | CIBSE W5.4.1 Pressure Testing
c6d1eaec-7926-5efb-b470-2278ecce87c8 | textbox | Record Start Time and Photograph Guage:
0ea8273a-9258-5999-831a-c98ce5ab53cb | note | Hold pressure for 120 minutes.
f9743c33-05b7-5e78-be4c-671315900c39 | button | Was there any pressure loss? | Yes, No
58ba340f-7ef0-5498-b746-90bb3a3104eb | textbox | Record Finish Time and Photograph Guage:
51bef9d0-cd47-5204-8362-ce5129f24575 | note | Add Photos
286bc8b0-26da-40ca-b028-e36e77d4846b | checkpoint | 10. DE-PRESSURIZE SYSTEM
75e457c0-0714-5050-8794-2d0ab1252c64 | note | W5.4.1 Pressure Testing
f20f47ce-0db4-5974-ba5a-b9a8f5bd7acd | note | Release test pressure from system.
11be04d9-1a69-5eab-81d5-69beabbc5f4d | note | System remains primed with towns main pressure.
8e39a1d0-fd39-59bc-9b24-bcbb1df35402 | note | Add Photo
034d32b1-fe3f-4bbb-b173-f9e48b808e46 | checkpoint-no-value | GM Fire Sign Off
5d984f29-ce91-4a07-8ce4-6305c703367a | signoff | GM Fire Sign Off
0fe89533-bfee-40be-b1f1-7e7165f2487d | checkpoint-no-value | Principal Contractor Sign Off
3942409f-fd27-45ae-9b15-ad87fc966979 | signoff | Principal Contractor Sign Off
8edf7e6f-9861-46fd-8df2-8dbf95380168 | checkpoint-no-value | Consultant Sign Off
89dde126-263b-4912-8b12-1b159fd5a8e7 | signoff | Consultant Sign Off
c30ccc4d-2a47-4cc1-a2fb-e52f7a92d307 | checklist | ITPS-204 Electric Fire Pumpset Installation and Commissioning |  | ITPS-204 Electric Fire Pumpset Installation and Commissioning
8f0bb661-262d-4106-b91a-a31f74fa71e2 | section | Details
c259aaeb-a7bd-4c4c-98ac-696a103bc51b | checkpoint | 1. CHECK AND CONFIRM - LOCATION
0af457fe-2947-5392-a59a-ba2ba7acd9dd | note | CIBSE W5.2 State of the System
a45b1aa1-3138-5a1d-ad95-661d4c1aea48 | note | AS2941.1-2013 – Section 11
301e09c5-6a75-52a1-a26a-c2ea5e11b502 | button | Has the Installation Pump been installed in a position that is protected from falling debris, and vehicular and mechanical damage? | Yes, No
e75fd553-eccd-5c07-95fa-55c1a7b67cfb | note | Add Photo
e3535982-7abd-437b-8e3a-a19e4d94ddf3 | checkpoint | 2. CHECK AND CONFIRM - CLEARANCE
07f4df96-df68-51ed-ab09-9be5296e1a1c | note | CIBSE W5.2 State of the System
215be300-0075-59b5-80ac-182986d75315 | note | AS2941.1-2013 – Section 11
dae0ea3f-4e9c-5b80-8f95-4a38685227ea | note | Is there at least 1.0m of clearance around the perimeter of the complete pump setup; and/ or
2adc9ca6-5c05-525f-8f89-54901c1a4b9c | button | for multiple pumpset installations, there is a clearance of atleast 600mm between each of the installed pumps? | Yes, No
6c3b71bc-2e77-53a4-a654-1d7a76c30e3b | note | Add Photo
8f6e072f-9a97-40d5-9861-f77b4a01d60a | checkpoint | 3. CHECK AND CONFIRM - ELEVATIONS
238732dc-2570-50ce-80c2-f380caea72b2 | note | CIBSE W5.2 State of the System
6a523a0c-5860-5b1b-8eea-14d4a8c6fc3f | note | AS2941.1-2013 – Section 11
2d9989d5-ec09-5c52-8e24-13605b745b0b | note | Have pumpsets been installed with the centre-line of all suction pipes at the same elevation; and/ or
99d99d60-eb21-5591-9955-19ac7934bb3a | note | if the pumps have been installed at different elevations, the elevated pump is installed on a properly constructed mezzanine floor; and
d4dac703-aea5-5637-943a-2c870d9181bb | button | with head clearance of minimum 2.1 m to the underside on both levels? | Yes, No
e6abb8de-1072-5d79-b226-8347d6924b3b | note | Add Photo
a1321eaa-5bf1-493a-851d-2fb7f22ffe80 | checkpoint | 4. CHECK AND CONFIRM - PLINTH
d99ff559-ede8-5f4d-914a-4bffb6066d58 | note | CIBSE W5.2 State of the System
5b41f821-dbeb-565a-822a-0d244548d30d | note | CIBSE W5.6 System Checks
a47130f9-8e26-5e98-8a02-9ba6025392fc | note | AS2941.1-2013 – Section 11
16e2623c-8acb-57d2-a348-e4510ef27ba5 | note | Have pumpset baseplates been mounted on concrete plinths with a height not less than 150 mm above the floor?
0b5427d6-d42d-5596-a9e3-bbdbf1cdfe69 | button | For fixing purposes, does the concrete plinth extend 150 mm past the edge of the baseplate on all four sides? | Yes, No
765abdbd-c6fa-58df-a48e-0d6e746b933e | note | Add Photo
1f4ad68a-af26-4cc6-bc8f-8c9ab60a75e6 | checkpoint | 5. PRECOMMISSIONING CHECKLIST - CHECK
a60edda0-ba44-577a-9101-53a59ab2feea | note | CIBSE W5.5 Pre - Commissioning
f6bda158-bbbf-5f1a-8269-264336d68e39 | note | CIBSE W5.4 System Filling and Venting
e8d88ffd-4de9-5f53-805c-175c562803a5 | note | AS2941.1-2013 – Section 12
042338c6-7168-5ff6-810d-0e4099b4245b | note | Have you checked the coupling alignment to ensure that the unit is aligned within the manufacturer’s specified tolerance?
ed0979f5-be9f-57ea-8e20-11d907dae1ef | note | Have you confirmed the direction of rotation?
14d0a71c-e0bf-5aab-b2f2-069aa53e1a05 | button | Has the battery electrolyte level, and the battery leads and connections been checked? | Yes, No
22d1b9d8-f616-5903-8500-2c4ad1320e92 | note | Add Photo
eca3b525-37ea-466e-ad2c-c7e9680169b4 | checkpoint | 6. PRECOMMISSIONING CHECKLIST - ENSURE
6b1b7dbf-e13b-50a5-a284-ce6a52ac4db2 | note | CIBSE W5.5 Pre - Commissioning
0b423332-eed2-51e3-a15b-a7acdad2f1db | note | CIBSE W5.4 System Filling and Venting
ea657bf2-6d7b-5494-8a08-bb05a149a3c4 | note | Is the delivery from the pump under test the only supply to the measuring device?
ddaf0713-21ee-5480-b224-9c5b5642f10e | note | Does all flow from the pump passes through the device?
56f61b05-4cfb-5d6d-ac41-b06028e53c93 | note | Is the pump primed and lines are clear; and
78bc28e2-4a69-5902-a750-f9dceec044d4 | note | valves are correctly set (open, closed or adjusted to required pressure); and
40737c90-219e-5d25-b58f-adf441ebd047 | button | is water available? | Yes, No
87563cf6-b1b5-5387-97be-a7a96e263a04 | note | Add Photo
639b3e9b-8b40-4644-aab1-23f50321dfa0 | checkpoint | 7. PRECOMMISSIONING CHECKLIST - ISOLATE
fdce6337-4e87-5eef-aedd-9e6c6a460b8b | note | CIBSE W5.3 Check before Filling
c39fcbd6-d374-5755-9b7f-dd0b2da33b3b | note | CIBSE W5.4 System Filling and Venting
3ad7c5fd-2d65-5a5b-a9e6-e7a1b88e9a8a | note | AS2941.1-2013 – Section 12
7c7942a5-dc81-538f-b192-eb10d003965d | button | Have you isolated all other water supplies to the fire protection systems, such as the automatic pressure maintenance pump and any other compression-ignition engine driven pumps in the system? | Yes, No
81b51f7f-6e1f-5bb6-8626-9ff4e2778581 | note | Add Photo
1a2f05b3-b5ab-45ef-9de2-273fa6081e36 | checkpoint | 8. PRECOMMISSIONING CHECKLIST - REPORT
385b518b-dcb5-5fe4-90d1-5de3eeba4ab1 | note | CIBSE W5.5 Pre - Commissioning
f4dc03bd-de1a-5046-9b3e-4f55982f52e6 | note | AS2941.1-2013 – Section 12
6cfc6611-01c3-57e9-b1ff-5980736a68fe | textbox | Pump plate details:
5af0f04b-08dd-5c71-b987-cf0ea8574714 | note | Add Photo
c6040fab-774e-43ca-be3d-8d872b6075b2 | checkpoint | 9. COMMISSIONING CHECKLIST - RECORD
a6d2aabf-16e6-5705-bc4d-baacba572b35 | note | CIBSE W7.10 Commissioning Certification
266e64ba-bf10-5e92-888a-24e699eab079 | note | CIBSE W7.2 Flow Rate Measurement Tolerances
d1d14d79-0cc0-527f-a3aa-5c6fbc19c8d8 | note | AS2941.1-2013 – Section 12
315a55d8-569b-5013-8b65-2378cb36c9b2 | textbox | What is the pressure in the system at which the pump starts automatically?
ae964b21-3964-5744-bc3e-6b12f3ffc87a | textbox | Pump shutoff pressure:
123f6ef0-acb3-5a6d-8259-432877097a7f | textbox | Motor shut off pressure:
02a0ba99-1ee1-55fa-be03-c138beae3d2a | textbox | Delivery pressure at maximum flow:
18490b5a-d52c-5900-abad-57163a4f7a8b | note | Add Photo
f5482528-2028-4fe0-a9ec-3af817e0372a | checkpoint | 10. COMMISSIONING CHECKLIST - RECORD
36d32659-e8bd-5cdd-8022-e95d92ae2ae1 | note | CIBSE W7.10 Commissioning Certification
f1a4e710-1c47-5f93-bbbd-982b02d4d4de | note | CIBSE W7.5 Preliminary Flow Rate Check
b6a583ea-07f0-5d50-bd8e-f52c78e51a11 | note | AS2941.1-2013 – Section 12
b404777f-bfdf-59c2-a022-61d67aa99dbf | textbox | Record the pressure on discharge gauge and motor current at three other flow rates between shutoff and maximum flow, one of which should be at the duty flow rate:
7b9e014d-2195-5fb3-ac20-50e8dc03200a | note | Add Photo
c94b01f2-a430-45cb-be83-379486992cba | checkpoint | 11. COMMISSIONING CHECKLIST - RUN AND RECORD
be6e4d5e-df14-5dc6-aa23-6cab9dac9952 | note | CIBSE W7.10 Commissioning Certification
fb4385f1-dcbd-54f4-baf0-1f18e302ab81 | note | CIBSE W5.7 Static Completion Records
eb6d176f-3f4c-5083-8648-ef568ec76c5f | note | AS2941.1-2013 – Section 12
791d90b1-031d-551f-bfc8-30c59f75ebb7 | note | DURING OPERATION:
56140022-4a6e-5dc8-b515-a196b87256d8 | note | Have you checked the temperature of the bearings and stuffing box leakage and noted any abnormality?
a569f7fe-e013-5393-a44b-ac5e5483c293 | note | Have you checked that all alarms and indicators, both visual and aural, have been activated; and
38f89ed9-4e19-56d5-8323-acbd5b9e85ee | button | Alarms and indicators, both visual and aural, revert to normal stand-by status when pump is stopped? | Yes, No
775af2db-46d2-552d-8c5a-324e4fa5b924 | note | Add Photo
244e2e34-4528-41e6-9505-967419b8b5b9 | checkpoint | 12. COMMISSIONING CHECKLIST - RUN AND REPORT
a4d4147f-c43f-5e0d-8751-66fba63c17fc | note | CIBSE W7.10 Commissioning Certification
b723c051-e076-5740-a414-21bb8fb7a01f | note | AS2941.1-2013 – Section 12
7c82d50b-c7f2-5cf8-b3f4-d5689c4afede | note | RUN AND REPORT:
fc4b5580-fd5a-5195-bd50-f29342dbe3e7 | note | Is the electric pumpset, together with its associated control gear and ancillary equipment, functioning correctly?
42cd96ab-ee9b-5a4d-8f4b-b9c255a4cca9 | button | Does the pumpset satisfy the intended performance conditions? | Yes, No
afc1df72-295d-5e3e-8677-44472e7163ef | button | Are there any operational abnormalities? If Yes, detail below. | Yes, No
9b898472-d1b3-5985-ad2e-367ea6b3ca6d | note | Add Photo
0a24289a-557b-4df0-bf96-73837693f62a | checkpoint-no-value | GM Fire Sign Off
468e49db-1f2d-4cc6-94f2-e9e93f1370e4 | signoff | GM Fire Sign Off
c065b285-1ff5-4187-852b-f45419d359fd | checkpoint-no-value | Principal Contractor Sign Off
124c8ff1-4856-4f77-b2db-88d791b56131 | signoff | Principal Contractor Sign Off
dee60f6e-94c7-417d-b27d-d7cbf7cf6115 | checkpoint-no-value | Consultant Sign Off
932509db-89d9-488f-bae9-5a5fe01fe25c | signoff | Consultant Sign Off
b225c4ca-4192-44b2-9a7d-ce4b375c0f4e | checklist | ITPS-205 Diesel Fire Pumpset Installation and Commissioning |  | ITPS-205 Diesel Fire Pumpset Installation and Commissioning
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
4ce8a016-716e-4119-a807-6438dd1d0d46 | checkpoint | 1. LOCATION
794d0e1b-427c-577c-872f-8289bab1e680 | note | CIBSE W5.2 State of the System
686ffbcc-ec7d-521c-9d27-25947de4b41d | note | AS2941.1-2013 – Section 11
2adb0d11-9d2a-5bb3-a1b6-58e23cf20fa6 | button | Is the Installation Pump installed in a position that is protected from falling debris, and vehicular and mechanical damage? | Yes, No
4df3f32b-0f87-5657-8c3f-a6e21ef8fd91 | note | Add Photo
54061128-a235-4f60-8a3c-d283d1335169 | checkpoint | 2. CLEARANCE
76d8b8c5-cbc0-5097-9f5f-9d5c3af94244 | note | CIBSE W5.2 State of the System
9aa700d0-ad24-51d3-8b46-183fff9d583a | note | AS2941.1-2013 – Section 11
f749bc67-c5a0-51df-bb01-c98506f32005 | note | Is there at least 1.0m of clearance around the perimeter of the complete pump setup; and/ or
aed13af4-22b7-5d02-b6e3-8233d7317ed2 | button | for multiple pumpset installations, there is a clearance of atleast 600mm between each of the installed pumps? | Yes, No
268f7072-6619-5644-9d73-d9ebb6a98ed8 | note | Add Photo
675e3953-b21a-4ad0-bf09-42567bd9b816 | checkpoint | 3. ELEVATIONS
f46cfa5f-0707-52d4-bfa1-53bfe364c43e | note | CIBSE W5.2 State of the System
9654eadf-0ceb-55c7-9d38-d23a5c197700 | note | AS2941.1-2013 – Section 11
0d73cca0-1903-554c-88b3-7386dc4fbd8a | note | Have pumpsets been installed with the centre-line of all suction pipes at the same elevation; and/ or
5b13ac35-221b-5169-a4a8-256dab2c2c08 | note | if the pumps have been installed at different elevations, the elevated pump is installed on a properly constructed mezzanine floor; and
acc4194b-766c-5831-9450-1adb4d845be1 | button | with head clearance of minimum 2.1 m to the underside on both levels? | Yes, No
14103439-dc2e-599c-87a0-30ce2ea3a6b1 | note | Add Photo
81e0f263-dad4-427a-af7f-d5efe6a0a6e6 | checkpoint | 4. PLINTH
48c97d13-0628-55c4-a52f-d329abe8128d | note | CIBSE W5.2 State of the System
9399cda3-de56-5783-91b3-83f0c37cf42b | note | AS2941.1-2013 – Section 11
cf3bf002-a5d5-5807-adb5-726e71f0a6aa | note | Have pumpset baseplates been mounted on concrete plinths with a height not less than 150 mm above the floor?
bd37f5fe-91c5-56e4-876e-e156a9557a0c | button | For fixing purposes, does the concrete plinth extend 150 mm past the edge of the baseplate on all four sides? | Yes, No
9ef51a25-72d5-5453-bfc3-8cb05384f310 | note | Add Photo
6caf1ba3-e213-4999-b4f8-613bcecfe6da | checkpoint | 5. PRECOMMISSIONING CHECKLIST - CHECK
a6288286-7f1b-5dd3-8394-fed057b7504c | note | CIBSE W5.5 Pre - Commissioning
7c21a387-f111-5938-ab94-1bbc614726e4 | note | CIBSE W5.6 System Checks
aa5e8242-9950-5086-b5c1-f9650df7fbd0 | note | AS2941.1-2013 – Section 12
f32c9d1d-f54b-5369-9845-f3365cfcbb2d | note | Have you checked;
a5704812-7296-5229-884f-d236462b83d8 | note | The cooling supply system; and
dea07c29-762e-5bb0-9847-c59584d87512 | note | Engine fuel supply; and
c0e16c39-1614-5b7b-aa6b-6d57480455a2 | note | The coupling alignment to ensure that the unit is aligned within the manufacturer’s specified tolerance; and
05b5ca73-41d5-56e1-a696-c1411eeb07f2 | note | The direction of rotation; and
886bfe0d-ab0c-5922-9615-190e1457d4ea | note | That the engine lubricating oil is at the correct level; and
8326b3b4-c592-5bc5-a0a3-d415f92a347c | note | The battery electrolyte level and the battery leads and connections; and
a8803385-4669-5ac2-9023-ac0c4c11030f | button | That the exhaust system is intact? | Yes, No
c4bd2397-874c-5123-9a93-cbbb52b84522 | note | Add Photo
c1b3d17c-5960-43ed-8533-9295e58bc863 | checkpoint | 6. PRECOMMISSIONING CHECKLIST - ENSURE
f2ac4c7d-e199-50a4-b4b4-8c4844d7e9b0 | note | CIBSE W5.5 Pre - Commissioning
4a83a057-c48c-5634-98c1-f4c45aa542a6 | note | CIBSE W5.4 System Filling and Venting
f87ba262-d673-5206-b659-06ff26e3fcfd | note | AS2941.1-2013 – Section 12
bce6df7b-8cb6-5f07-9ce2-97a6b9854ecb | note | Is the pump primed and lines are clear; and
487c4f22-37a3-5c82-bd46-14134ef14cf4 | note | valves are correctly set (open, closed or adjusted to required pressure); and
334d11fb-7b43-54d2-a998-55c4e5b7b1dc | button | is water available? | Yes, No
0afe26e6-6897-5565-b2bc-8c8d81e6d139 | note | Add Photo
fd9cf697-3927-4b7f-a1e6-9bb40344f444 | checkpoint | 7. PRECOMMISSIONING CHECKLIST - ISOLATE
b8b6c16d-c996-552d-8183-3f3e6f15a476 | note | CIBSE W5.3 Check before Filling
dde4fdbb-e2a1-5999-b41b-0b340fa4982d | note | CIBSE W5.6.2 Mechanical Checks: Automatic Control Valves
12da7dbe-a45c-5411-8b34-d9a5c1e5d39a | note | AS2941.1-2013 – Section 12
1c5ee796-e8e3-5c56-8941-4cd94160e178 | button | Have you isolated all other water supplies to the fire protection systems, such as the automatic pressure maintenance pump and any other compression-ignition engine driven pumps in the system? | Yes, No
0db53e62-ec9f-5916-85e0-f81f8d1c225c | note | Add Photo
06f8dd1c-e3c8-42f8-9a19-d633128cfd83 | checkpoint | 8. PRECOMMISSIONING CHECKLIST - REPORT
699335ec-c08c-5722-9640-015a90d537f7 | note | CIBSE W5.5 Pre - Commissioning
363c3ca4-2040-56db-a7da-dc6711e7aa84 | note | AS2941.1-2013 – Section 12
e7c265b9-237d-51cb-a3f1-628bdcc784ca | textbox | Pump plate details:
06b2ad24-c743-52d0-b6a7-3bb01b06b318 | note | Add Photo
9de6ad24-9873-4fc2-9d09-f6f8cad53eb6 | checkpoint | 9. COMMISSIONING CHECKLIST - RECORD
9fdc2da0-be2f-5776-80b0-a4ed8ca147f0 | note | CIBSE W7.10 Commissioning Certification
96adc920-fb98-5022-8aa2-935da569ad6a | note | CIBSE W7.2 W5.7 Static Completion Records
aa37baa3-6a77-5355-a2e0-e6febb1296d8 | note | AS2941.1-2013 – Section 12
3f97bb98-632e-54a6-bf5d-18ee0e1fe17c | textbox | What is the pressure in the system at which the pump starts automatically?
b9779469-c274-5f9b-9e38-f392f69f8bc1 | textbox | Engine oil pressure:
300590e9-f721-556a-83c8-0907c6ce3d1f | textbox | Pump shutoff pressure:
a583503a-f9bd-5f82-8c94-41dddfbdd7d4 | note | Is the Coolant flow correct; and
d8e2b1a1-4362-56fd-9da8-5640f14b14fc | button | Are the fan belts rotating and intact? | Yes, No
573cdf2e-49ca-5a1a-bbed-cc13747d61fa | note | Add Photo
b4f51475-6a2d-5885-becb-0aed1a830701 | checkpoint | 10. COMMISSIONING CHECKLIST - ISOLATE
34d928d4-b9bb-52f4-a207-87e55c84b6a8 | note | CIBSE W7.10 Commissioning Certification
05cf3260-4c6f-59f9-925c-051faf6d69b6 | note | AS2941.1-2013 – Section 12
ad2cd759-071a-5a3b-a267-98919468bc20 | note | ISOLATE the flow meter, partially open the test valve, and flush to remove any debris or foreign matter;
c86753cf-9de2-5f3c-976d-f6a4767887fb | textbox | open any meter-isolating valves, open the test valve, and record pump delivery gauge pressure when approximately full load flow is indicated on the flow meter:
2b90ec82-c5d2-5ac4-a1df-5db191cc2f60 | note | Add Photo
b9f052e6-e367-44ac-87dd-5dbb542e2b97 | checkpoint | 11. COMMISSIONING CHECKLIST - RUN AND RECORD
7c198f01-15d0-5179-aacf-7f6cc7dc3882 | note | CIBSE W7.10 Commissioning Certification
4e41ddad-fa1b-5d69-936f-5aa8ef9b07fa | note | CIBSE W5.7 Static Completion Records
216d48d3-f40f-50f2-b065-22746228af05 | note | AS2941.1-2013 – Section 12
3808afd6-096a-56d7-a966-afb08390b4f6 | note | RUN the pump for 30 min at maximum flow and record.
85c324eb-7978-5870-bb73-02dbf6d56af9 | textbox | Suction and delivery pressures:
3bc1a54b-e7fe-5c73-bbd2-6d5717580a12 | textbox | Engine running temperature:
bef05381-4376-5910-b711-7d32fe4b7cf4 | textbox | Engine oil pressure (within the engine manufacturer’s limits):
70583689-1e01-579f-8b2f-02786794a553 | textbox | Air temperature at pumpset:
93b0c498-f14f-5e40-8647-7f2dca4eacb5 | note | Hold the engine shutdown mechanism closed and simulating an automatic start signal until the engine has attempted to start for five automatic starting cycles.
3da5fb4b-c30e-5f25-96af-74186d4dc46e | button | On the sixth starting cycle, return the engine shutdown mechanism to its normal starting position. Does the engine start immediately? (Clause 9.3.6.2) | Yes, No
cf87689c-22b1-5db8-8800-84352c7e5d09 | note | Add Photo
89136ac2-e7da-4e71-a217-c350de26b0a3 | checkpoint | 12. COMMISSIONING CHECKLIST - RUN AND RECORD
ed60559c-6802-576a-9039-af992d446f15 | note | CIBSE W7.5 Preliminary Flow Rate Check
456c383e-a94c-5f72-8e5b-ccd49c1e7dad | note | CIBSE W7.2 Flow Rate Measurement Tolerances
af71fb18-5590-5fa9-980f-2cf72875722a | note | AS2941.1-2013 – Section 12
2e7a63fc-1937-516d-ac01-0fa327f5be11 | note | RUN the pump for 30 min at maximum flow; then
8ef4f6cf-6be2-59cd-8430-6734765f89b1 | textbox | Discharge pressure at three other flow rates between shut-off and maximum flow, one of which shall be at the duty flow rate:
9af852e3-223e-50b1-98ff-26acdc0d8e54 | note | Add Photo
dd3d2e6f-1737-484e-8668-9e581e9320c0 | checkpoint | 13. COMMISSIONING CHECKLIST - RUN AND RECORD
88b0c517-c4e7-5e0a-8f13-5dee0728761a | note | CIBSE W7.10 Commissioning Certification
f2889d4b-c540-5330-942c-8674032f367f | note | CIBSE W5.7 Static Completion Records
fdaf169d-ab25-5a8e-bc1b-e61eb216d6c9 | note | AS2941.1-2013 – Section 12
4b54d5f7-4419-5cca-b9db-53ade154d1d1 | note | DURING OPERATION:
2790d9fc-b6f4-5886-b46c-1378ee69ed15 | note | Have you checked the temperature of the bearings and stuffing box leakage and noted any abnormality?
479f48f8-b4c4-51ae-a5ac-635fbff14a3a | note | Have you checked that all alarms and indicators, both visual and aural, have been activated; and
31ac04f5-e82f-5839-b71d-3fc0bb732e21 | button | Alarms and indicators, both visual and aural, revert to normal stand-by status when pump is stopped? | Yes, No
89c5ba42-39f1-53a3-9f77-0fc68a5c5034 | note | Add Photo
562239d0-93ca-499d-a4dc-43537d65d5ae | checkpoint-no-value | GM Fire Sign Off
b70049f6-f23e-4b93-be4a-a692a143cb15 | signoff | GM Fire Sign Off
6ba80533-95e6-4bf9-b5c0-9c8640af64d0 | checkpoint-no-value | Principal Contractor Sign Off
e06386d2-67db-4b92-ae29-cf4a8bd4833f | signoff | Principal Contractor Sign Off
dbf9dc45-d8a2-44ab-b08d-e4a20e96abd5 | checkpoint-no-value | Consultant Sign Off
cc2d01a5-a24b-403d-91d2-cd072b39b6a1 | signoff | Consultant Sign Off
1cabaeaf-f2bc-4654-8318-aa4b4c5b98cb | checklist | ITPS-206 Sprinkler Commissioning |  | ITPS-206 Sprinkler Commissioning
6bcf63e6-3b56-451f-b5cf-671ae4dbefed | section | Details
7b8be648-0cf2-4c88-ac36-e3124de49196 | checkpoint | 1. CONFIRM WATER SUPPLY & PUMPS PREVIOUSLY COMMISSIONED
4fcbe6eb-5c1c-5e48-9a70-e37bb6113011 | note | CIBSE W5.2 State of the System
5fa17fca-803c-51bc-8c7b-f741bf3425b2 | note | AS2118.1-2017 - Section 14.9
d4269adf-f4c8-5352-b879-702e341bb651 | note | Water Supply & Booster Pumps have been commissioned
74fc67c1-e549-50a5-a96a-964b7e5b2f64 | button | Are all Valves in the correct position? | Yes, No
68a91b46-9055-4af8-bcfa-a17a1ce28941 | checkpoint | HOLD POINT
9c6a5ea7-fbe4-53fe-a4d0-c2dd167604b7 | note | There is a risk of damage to pumps if system is not ready for sprinkler commissioning . Refer ITPS-204 and ITPS-205.
cc4dc793-49fb-47f2-b7d4-156558e20807 | signoff | GM Fire Sign Off
181f0738-c5ef-4d58-94cb-4f0c78b25b5b | checkpoint | 2. CONDUCT FLOW TESTING TO PROVE SYSTEM PERFORMANCE
d0d4faa6-df79-5a22-8b76-82c7de271fe3 | note | CIBSE W7.5 Preliminary Flow Rate Check
17e2309d-0043-546d-90d1-d9284ab001f0 | note | AS2118.1-2017 - section 4.2.2.
619658c0-c0ae-55fc-8e93-9b87bd78664f | note | Test
5dcf893b-74c0-5ab8-a8e9-d75c8e249cf7 | note | 1) Confirm flow & pressure requirement
b28726e8-c320-5447-bedd-1d7c142a8fef | note | 2) Secure flow meter to annubar test line
a913a5d9-6ce0-55ed-af8d-49329d6df259 | note | 3) Manually start booster pump 1
f50d99c0-90d0-5a2d-9ed5-e2f4a7435bcd | note | 4) Incrementally open annubar test valve
8a233bbf-b744-5062-ac0d-fd5551904637 | textbox | 5) Record test flow & pressure at each stage:
c624306e-868c-5945-9d4c-e9e5ff2129bf | textbox | 6) Record pump data at each stage:
21aa8828-2554-5b24-9588-135f6cc81179 | note | 7) Confirm system achieves pass result
bd8f4d3a-6552-587b-9785-68da8ba33e1c | note | 8) Close annubar test valve
c32cdce4-e45a-5b17-979e-94f3d9fabbfa | note | 9) Stop pump
d7e8a62b-0016-5da1-b3c4-99deceab7b5a | note
1eada872-04b9-5045-ab3c-dc416a2f91cb | note | Has the Sprinkler Block Plan been completed?
50184010-8115-5473-90aa-c2e77c1f2343 | button | Have you recorded this on the Pressure Gauge Schedule? | Yes, No
433be3b0-5485-5336-b03d-90885a8d1b1d | note | Add Photos
d131509f-70d3-4ff9-9f9f-ce81c0547de1 | checkpoint | 3. CHECK OPERATION OF DBA PRESSURE SWITCHES
900d448d-02f4-5f03-86fd-f4edc18db458 | note | CIBSE W5.6 System Checks
6c4040ba-b4d3-5d88-b126-f0e00fe0a3fc | note | AS2118.1-2017 - Appendix H4
e3f14c9a-b904-57e7-a0eb-9f9e920ab8a4 | button | Does the pressure switch change state when system is activated (Rise in pressure switch)? | Yes, No
402f2022-c78f-5cf4-8503-6d1e81ff97d4 | note | Add Photo
c3bb5cd4-ede0-4b66-ad97-630ea83147a4 | checkpoint | 4. CHECK OPERATION OF PUMP START PRESSURE SWITCHES
943ce8ae-21b3-5bf2-bf9d-1cd540f42f6c | note | CIBSE W5.6 System Checks
0c10cf0d-7d08-5b04-9ba2-ea4d494b186e | note | AS2118.1-2017 - Appendix H5.4
2464c3cb-8675-5a7b-a1ec-e0be7d0f5820 | note | Are the pump start pressure switch settings in accordance with pressure gauge schedule?
02c5538f-da50-56ea-a49d-72451a2baaa3 | button | Have you checked the operation of All pressure switches individually? | Yes, No
224b56d7-2169-531a-94dd-72486cdf25f1 | note | Add Photo of Pressure Gauge Schedule
b2fa6223-977f-488c-8498-fef490eb0d2f | checkpoint | 5. CHECK OPERATION OF DRY FIRE INTERFACES
9e37f3f6-9c8c-5b41-8c8e-d39619f6998c | note | CIBSE W5.6 System Checks
29f259a4-d5b9-52b6-818e-4b57d0ebd66e | note | AS2118.1-2017 - Appendix H6
e14a28f2-d096-5925-a95d-8616071b3694 | note | Activation of ancillary Pressure Switch (Rise in pressure switch) registers at FIP
c895d274-933d-5dcd-9606-3f3dd7bd5ddd | note | Activation of flow switches register at FIP | Yes, No
cecbcbc2-d4ec-5178-88df-67c7a9eef671 | note | Change in valve state/position register at FIP
fe6d163b-bb69-5336-8859-9b4c98caaa55 | note | Attach the valve list
b5b835ec-1b4f-497c-816f-e8fa259d4ca5 | checkpoint | 6. COMPLETE FORM 71 & ALL TEST RECORDS
63f2b108-145b-5c67-98ff-a507539cd49b | note | W7.10 Commissioning Certification
df81f9d1-1f56-5f16-a39d-fb3c711b34c6 | note | NCC 2019, AS2118
e2e53fe1-bfef-5b9c-8944-24364c1e4356 | note | Flow test pass result on Form 71*
cce41cb0-5896-537a-a625-53760ab4a786 | note | Record the pump start pressure switch set points:
b63e0a49-86d5-5412-bd74-100b13f0b5f4 | button | Record the dry fire interface test results: | Yes, No
3bbe32c4-579c-5350-b5f7-0166f49e03a0 | note | *Form 71 - Fire Hydrant and Sprinkler System Commissioning This form is to be used for the purposes of commissioning water based fire safety installations, as required by the Queensland Development Code – Mandatory Part (MP) 6.1, which is a building assessment provision under the Building Act 1975, section 30.
7943767c-f7f0-5581-a553-f7c08e55dc90 | note | Add Photo
1ab0ba15-74f5-4da9-8736-e7c4219490c8 | checkpoint-no-value | GM Fire Sign Off
8513a17b-2f88-44cb-823c-7eeb291a6116 | signoff | GM Fire Sign Off
0f18376e-fa18-4141-b14f-87870972350c | checkpoint-no-value | Principal Contractor Sign Off
2d97aad7-0470-4ac9-b3ef-230dfc967f9c | signoff | Principal Contractor Sign Off
e95e0250-7d55-45b6-bcea-b755442a8e13 | checkpoint-no-value | Consultant Sign Off
d51fdc72-0377-404c-a732-87c39c4678b0 | signoff | Consultant Sign Off
936569a0-3c1d-4cd1-9330-40f73f9fb97e | checklist | ITPS-207 Hydrant Commissioning |  | ITPS-207 Hydrant Commissioning
5da954b6-8c7e-4c84-b76a-de303451e9b6 | section | Details
306931b9-35cc-4502-b856-7f88e0c9ab49 | checkpoint | 1. CONFIRM WATER SUPPLY AND PUMPS PREVIOUSLY COMMISSIONED
67162e0e-aa2f-52af-8f03-12b909632fcd | note | CIBSE W5.2 State of the System
2aa00cea-589e-50d3-8ec1-8384470fe438 | note | AS2419.1-2005 - Section 4 - To comply with Part 4.2
a038b067-6f92-5cf1-a432-ea63758bb722 | note | Have the Water Supply and Booster Pumps been commissioned?
486647d5-9504-57bf-9593-e0547df91587 | button | Are ALL Valves in the correct position? | Yes, No
7f0bf0f8-15f5-4586-8e1d-b0e681597d89 | checkpoint | HOLD POINT
e0db078b-6abb-545d-bd1b-3e5e1bb3a2a5 | note | There is a risk of damage to pumps if system is not ready for sprinkler commissioning . Refer ITPS-204 and ITPS-205.
452f16e1-586f-4af2-9013-c306a51df91f | signoff | GM Fire Sign Off
fc6f701b-0e92-40a0-93ba-e34613de16d3 | checkpoint | 2. CONDUCT FLOW TESTING TO PROVE SYSTEM PERFORMANCE
bbd67080-9b81-54c9-8d2d-6f57787da293 | note | CIBSE W5.2 W7.5 Preliminary Flow Rate Check
28e0a66d-506a-5966-8eb6-b8b63da71611 | note | AS2419.1-2005 - Section 2
8a08166a-7e72-519f-8e04-fa0e403d0100 | note | 1) Confirm flow and pressure requirement
15f9d7fc-b36e-5e95-b871-860b8928a7d8 | note | 2) Secure micrometre and calibrated gauge to hydrant outlet
015e222d-0f1b-545d-9941-7e67d7dc9f28 | note | 3) Manually start booster pump 1
51d8b087-63e5-5f23-a42f-bddb1d16b3e8 | note | 4) Open hydrant valve to required flow rate
98d3ec1f-8c96-5d77-8d15-73ef807b6c46 | textbox | 5) Record residual pressure at required flow rate:
87f4e39f-30d1-5075-9385-ccc4fc75e85a | textbox | 6) Record pump data:
9bd49c47-ec47-5851-9e35-bd7f583c5ee9 | note | 7) Confirm system achieves pass result
b1588bae-6c0d-5f6a-9b1e-3689eabd6e26 | note | 8) Close hydrant
9bd3ae6a-2d83-59af-b9ba-b3464135e4a8 | note | 9) Stop pump
8605ac18-c248-508d-b311-b43a830c816e | note | Attach Hydrant Block Plan and Pressure Guage Schedule
ada11013-f927-4a0a-a13a-1df4d641c005 | checkpoint | 3. CHECK OPERATION OF PUMP START PRESSURE SWITCHES
ec5ee493-40e7-531b-9420-a11604a12296 | note | CIBSE W5.6 System Checks
9578ca02-714e-59fa-9b2b-9c8f52c35f15 | note | AS2118.1-2017 – Appendix H5.4
6ff4fb58-26c5-5fa1-9482-48288fff250e | note | Is the pump start pressure switch settings in accordance with pressure gauge schedule?
82bd242c-7736-5e31-8666-e83aeaab1b9e | button | Have you checked the operation of all switches individually? | Yes, No
c6b71d69-c2e6-554d-9302-b78cd270c8e3 | note | Attach Pressure Guage Schedule
8e12f8cd-dd87-4997-bd9c-fe519407e38f | checkpoint | 4. CHECK OPERATION OF DRY FIRE INTERFACES
e78564d2-f6d9-571c-b4df-9026fb0fc79b | note | CIBSE W5.6 System Checks
6165621b-fdb4-5d2b-9107-d913f20abb18 | note | AS2118.1-2017 Appendix H6
e0e29483-5ef7-5145-ad15-df1e71609159 | button | Change in valve state/position register at FIP | Yes, No
39e8f28c-cc48-5a3b-852c-5f2111588911 | note | Attach Valve List
8b7babb8-7973-405e-8a11-d8bf40fb5e13 | checkpoint | 5. COMPLETE FORM 71 & ALL TEST RECORDS
8b8085f6-48e9-57fc-af9d-a2cd7f225d51 | note | W7.10 Commissioning Certification
67cba855-a73c-53e6-b113-92a15360be86 | note | NCC 2019, AS2118
b1be5bba-9bfe-5dbc-9e7a-f672736e21f6 | note | Flow test pass result on Form 71*
47d8c24a-6ffa-54f6-8eac-f2e18416b1e4 | note | Record the pump start pressure switch set points:
13a8f1ff-8255-58af-8776-87ef28701b6e | button | Record the dry fire interface test results: | Yes, No
606a63f7-2ac0-5d1b-9ce1-069f57859058 | note | *Form 71 - Fire Hydrant and Sprinkler System Commissioning This form is to be used for the purposes of commissioning water based fire safety installations, as required by the Queensland Development Code – Mandatory Part (MP) 6.1, which is a building assessment provision under the Building Act 1975, section 30.
d767ead4-9b3b-5739-b1e9-fab3fd4e43c1 | note | Add Photo
7020a9a6-cb3e-465f-b5af-e8a699dd3d79 | checkpoint-no-value | GM Fire Sign Off
716fb599-25d1-4b11-81ee-17bdf50d84d1 | signoff | GM Fire Sign Off
8570eb08-6647-4a82-a0fe-ef92f4ac2565 | checkpoint-no-value | Principal Contractor Sign Off
fae64b20-60de-4656-8314-f15232d4f396 | signoff | Principal Contractor Sign Off
4ae3c153-80cf-45d3-a54a-c399ab5822ce | checkpoint-no-value | Consultant Sign Off
c90d1822-2a60-4ccb-a7c6-da2c12c9fb3c | signoff | Consultant Sign Off
4cbbe903-e191-44b5-a24f-6f4030891b9d | checklist | ITPS-302 QH Concept Design | itp | ITPS-302 QH Concept Design
e74e34ba-07b4-4cea-873d-0ff61c49a7b1 | section | Details
8afa0829-f72f-4144-b42f-bbc8d3e5e72a | checkpoint | 1. Compliance
fba5d73c-55f3-503a-8ee5-24bb91cea4e8 | button | Does this design comply with the QH brief and CIR? | Yes, No
30ddf771-f4c0-5a56-b714-3fe7eb88ff43 | note | List all codes and standards that you have complied with.
36b8878a-47ae-5e07-b6c2-20cbaa9b627f | textbox | Australian Standards:
a783a59f-a936-58a6-8833-cc55cb0ffd16 | textbox | National Construction Code (NCC):
d2f53d58-0c8f-55fc-9fcf-710d9ae3d386 | textbox | Site-specific factors and requirements:
3e6b5ec6-6a82-5232-81e4-4829efb5a0e4 | note | Redundancy and reliability:
b8b80f4c-9ac1-53c2-80db-0659831fc397 | button | Is this in accordance with the AS and site requirements? | Yes, No
6ae83e9f-2aed-56a8-9c6b-50da7affb58d | note | Future proofing:
72feb80f-f199-55ff-a445-92f793e05510 | button | Have you allowed for site expansion at major infrastructure (i.e. sprinkler manifolds, water storage tanks)? | Yes, No
7527e294-d1e0-546f-a4aa-c30a3985ff5a | note | Disaster management:
18572a93-d234-5439-8e51-ad863df95551 | button | Is this in accordance with AS, NCC and site-specific disaster management requirements? | Yes, No
524ae679-7cfc-5841-823f-2638037fa907 | note | Performance & Maintainability:
0ef8922d-1848-5be3-9db8-9cfdf756ad3b | note | Is this in accordance with the AS and NCC requirements and;
e534cc9e-dd5a-5cba-9125-13b345ae2497 | button | Have you assessed plant and riser spatial requirements for maintenance? | Yes, No
2960f79e-0735-4c20-9502-6966046f2f2d | checkpoint | 2. Design process
b744930e-3d37-53a0-9b63-8cf5640ca0a3 | button | Have you completed a preliminary assessment and sizing of fire services infrastructure requirements, including tanks, pumps and major valve sets; and | Yes, No
fe220dc5-637f-59e6-90f7-ef0f94086955 | button | the reticulation strategy to determine the quantity and location of risers; and | Yes, No
e360bc68-4823-5be2-b318-b2e632f593e3 | button | identified the required plant and riser areas for integration into the building’s spatial planning? | Yes, No
8b55d44c-14e8-4a71-bcd1-b74662cedafa | checkpoint | 3. Cost estimates (in conjunction with QS for all phases)
252ad874-99d7-5987-9d7a-2d637da6e83a | button | Did you coordinate with Quantity Surveyor (QS) for cost estimates based on preliminary plant requirements and outlet counts? | Yes, No
bcab164b-88ce-4582-86d1-04de70a0a1f6 | checkpoint | 4. General Coordination
27f8917a-38e7-565d-a91a-465ab7a815fc | note | Have you provided spatial requirements for plant rooms, risers, and access points; and
33a550fa-ae04-509d-b94b-15cf0fd3a414 | note | Liaised with key stakeholders; and
539a02f4-d053-5182-b89b-1966db5eea66 | button | Provided input into the concept design report, including engineering baseline assessment for existing buildings? | Yes, No
380bdb8f-aabe-4ad9-8fb7-053bca38fd04 | checkpoint | 5. Documentation and Reporting
5cb141a9-04a7-5073-9435-a77b76363886 | note | Have you prepared design reports and documentation; and
78df995d-7357-5fd1-879a-b36550ef7825 | note | Reported any areas of non-compliance; and
b1cca2d1-fa75-58c3-8a66-63d1e7147951 | button | Provided preliminary schematics to articulate requirements? | Yes, No
6fd0d998-cf4b-5195-ac0f-4d83d3bb2018 | note | Note all deviations must be raised via non-conformance submission.
f79a7f9c-3d81-412e-bc0c-7543be9075a0 | checkpoint-no-value | GM Fire Sign Off
ff1e6ca8-1103-404b-89a1-b57ca92e0e96 | signoff | GM Fire Sign Off
cf55389d-61b1-41ff-ba6c-a319dc84542d | checkpoint-no-value | Principal Contractor Sign Off
2fe88535-6d5b-4181-8b5d-ced0630e8b19 | signoff | Principal Contractor Sign Off
797cdb5e-de05-4c5b-a4c7-991b7d283050 | checkpoint-no-value | Consultant Sign Off
1d9be49d-0c00-4831-aa27-3bec377d5890 | signoff | Consultant Sign Off
ee7cee11-f09d-4f5e-af32-5336c4f323a7 | checklist | ITPS-303 QH Schematic Design | itp | ITPS-303 QH Schematic Design
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
4dfc4e43-35bb-434e-b838-44660d3345fa | checkpoint | 1. Compliance
759acac5-b513-51bd-a251-8d48d99dd42d | button | Does this design comply with the QH brief and CIR? | Yes, No
86a1e7eb-0a37-56fe-a16d-4f471fd9e3cb | note | List all codes and standards that you have complied with.
e8ac6182-af6e-5ec2-9275-b8db7b254e28 | textbox | Australian Standards:
46279c9b-f1bc-5d47-b33d-56ba5caf3e08 | textbox | National Construction Code (NCC):
35085561-cb5c-55f8-9b83-bb6f0201ea16 | textbox | Site-specific factors and requirements:
1444cada-8189-5cad-8305-0446b7120688 | note | Redundancy and reliability:
b9a5133c-27d5-57e7-90cc-13e71231fc8c | note | Confirm strategy for site supply redundancy and reliability.
ff59bc84-8b85-521a-9238-d07b0000a3e0 | button | Have necessary details been included in schematic drawings to confirm reticulation redundancy and reliability strategies? | Yes, No
35372ec5-a200-56cb-93cd-0a42a0cfb651 | note | Future proofing:
cb6831b8-8b4d-59f9-bf4c-81baf5db257a | button | Have you documented and aligned the strategy in the schematics and design reports? | Yes, No
5a2edc6a-0c0d-5e92-b55d-7f280fcd7332 | note | Disaster management:
39fd9a92-64d1-5682-a5ae-64336aca2b28 | button | Has design documentation been aligned with the disaster management strategy? | Yes, No
481359ff-d4d0-55e0-ba81-f784eaf1515e | note | Performance & Maintainability:
8efb34a8-f7f4-579b-a447-f6fb6a189116 | note | Have you confirmed performance is in accordance with the AS and NCC requirements and;
0f424372-2e7d-59e8-94f8-f5ffcfaeadb3 | note | Refined from concept design; and
2de1455d-e5cb-567f-9f1e-21bde67a9234 | note | Confirm servicing access on SD drawings for plant areas; and
51d75d38-faaf-5d91-a2ac-be7a51eda9bb | button | Provided a statement in the SD report that maintainability has been included? | Yes, No
11a12f36-ab8b-4a31-80c5-9fd6e3ec4f7d | checkpoint | 2. Design process
d4603174-71d3-52da-b079-f4ad66ff6c9f | note | Have you refined major infrastructure requirements; and
cb656fbe-04e3-5b63-a079-5ccbdf87e868 | note | Confirmed all points of connection to external infrastructure (e.g., water supplies); and
47a79f43-8727-5b0b-acdf-e467f2c96e9d | button | Prepared fire services schematics and preliminary plant room drawings? | Yes, No
a897f0c8-8ef4-477d-8be1-defd70c8f0aa | checkpoint | 3. Cost estimates (in conjunction with QS for all phases)
bf16b356-c8c4-5345-9474-9531736087d0 | button | Have you confirmed cost estimates with QS based on any revised design parameters? | Yes, No
d29725bf-8798-4f6e-86c5-4384d9b0ca7e | checkpoint | 4. General Coordination
dfedf2a2-e7c5-5af4-a5eb-ba9e3d81358c | note | Have you provided spatial requirements for plant rooms, risers, and access points; and
8fd3dbf7-1ff6-5605-9510-699265708789 | note | Liaised with key stakeholders; and
305ebc2c-a0ba-51b7-ac88-366fcaa7311e | button | Provided input into safety in design? | Yes, No
e607e51d-da6d-46f3-ab5c-6ef9fb09b47e | checkpoint | 5. Documentation, Reporting and Drawings
2c9f2f3f-cd1c-5275-91cc-bba8badea38c | note | Have you provided input to the schematic design report; and
25bae3b4-bd45-5024-b0ff-99146786837f | note | Provide preliminary specifications if necessitated for the delivery model; and
5fc74b15-b180-5792-a271-1f5d84f828ad | button | Prepared schematics and preliminary plant layouts? | Yes, No
bfbfd651-fdcc-496b-9028-c4d39aad1533 | checkpoint-no-value | GM Fire Sign Off
77d09fe7-d292-4f0b-8fe3-219dffda50a5 | signoff | GM Fire Sign Off
89d3b0a6-483b-43c3-b597-7b61c88a77b2 | checkpoint-no-value | Principal Contractor Sign Off
c1a2b043-70e5-4b27-a022-3af13cf09d00 | signoff | Principal Contractor Sign Off
990f5f56-2189-4004-aca8-a85e657d3a62 | checkpoint-no-value | Consultant Sign Off
ac348ec0-ff09-423c-b974-340a18b79ae0 | signoff | Consultant Sign Off
133fb81c-8d45-4c58-84fa-2c7a45c7f48c | checklist | ITPS-304 QH Detailed Design | itp | ITPS-304 QH Detailed Design
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
459f5bc1-8a57-4442-90f3-1b6374dce9d3 | checkpoint | 1. Compliance
8461a29b-0295-50e0-8843-922af30b7d60 | button | Does this design comply with the QH brief and CIR? | Yes, No
44c9fc38-4a1f-51f4-9577-57b9523bcfea | button | Have you provided a summary of applicable codes and standards in the design report, and detailed within draft specifications? | Yes, No
4befde92-24dc-587e-ad00-33f403fa77ca | note | Redundancy and reliability:
94e7affc-0e5f-5f7c-99c8-4eb7e1b94bc3 | note | Reconfirm strategy and no material changes to site requirements.
fc70f06d-5514-5a74-9e2c-30452c6c578a | note | Future proofing:
76879034-887c-556f-acce-055c527f3fff | button | Has the strategy been documented in schematics, plans, design reports, and draft specifications? | Yes, No
bb83ce9a-63d8-5760-a9c8-79f5261f6ba7 | note | Disaster management:
11fe8a85-ca48-55c1-a9a3-6a44884b097f | button | Has design documentation been aligned with the disaster management strategy? | Yes, No
adaaf844-5045-5640-81cd-470c0ff4aa08 | note | Performance & Maintainability:
e8876fdb-f8ca-5dea-af70-3517b391e70f | note | Have you confirmed performance is in accordance with the AS and NCC requirements and;
391aa1a0-45c4-5291-a380-9457bfeea39c | note | Detailed design drawings to show maintenance provisions for plant areas; and
75ceb6f9-158b-5eff-9da4-824c9b7e8190 | note | Ensured all valves will be accessible and not concealed in ceilings or enclosed; and
3c3b3f38-90e5-5758-b96a-2883dfc543df | button | Safety in design review? | Yes, No
70353f7c-dcec-5127-b5f4-5b324f3167a8 | note | Commissioning testing and post-occupancy:
80d69ab4-e3bc-5424-96d4-15150665e6c1 | button | Have Preliminary requirements been included in draft specifications? | Yes, No
af40787b-4dd2-4e54-8b7a-93bdc981f884 | checkpoint | 2. Design process
da19dc1d-521a-54c7-a5bc-ac3894c16eb7 | note | Have you verified any department-specific fire services design requirements during the user group process; and
9cd04cbf-a16c-555d-8884-076744bd5ca9 | note | Ensured RDS capture final requirements for outlets and any other special provisions; and
f6500d85-11f0-50d4-95bf-4c4b0de2c6fa | note | Updated documentation and progress fire services plan drawings; and
8e9d3c2b-dca7-5f87-ba62-8b50116a6f6f | button | Provided confirmed plant room drawings? | Yes, No
fd5b6e4b-be22-45ef-bdfc-438315ef2864 | checkpoint | 3. Cost estimates (in conjunction with QS for all phases)
f6d012d5-72bc-5432-b88a-901b5fd1e088 | button | Have you confirmed cost estimates with QS based on device counts and/or SQM basis per department? | Yes, No
6dc79496-5598-4aae-ae6a-69dd0f514ee5 | checkpoint | 4. General Coordination
d5987aa6-ef4d-53d1-97e5-26f34cc5c44b | note | Have you refined requirements via user group consultation; and
e23ec75a-a9ec-51a6-bc2e-5ee641a723e9 | note | Coordinated with architect for access and maintenance review; and
42ebb623-496d-5149-8324-dcf4f28f4251 | button | Coordinated with other engineering services, particularly for points of interface (associated works)? | Yes, No
0fb3622a-59de-48dc-ac36-508aed7d7cee | checkpoint | 5. Documentation, Reporting and Drawings
751e07bb-2d74-5df2-a957-150a797219f2 | note | Have you provided input to the detailed design report; and
45e31579-4630-52db-8d59-0ad066da13a7 | note | Provide preliminary specifications; and
da5b79d5-a7cb-5f1a-a41d-d45dfaaa8fe2 | button | Prepared technical schedules for major plant and equipment? | Yes, No
ed12fa4f-168d-5197-b254-7f4807f4e469 | note | Drawings:
ffa28819-5024-5158-a9f0-49139a3c0948 | note | Has the Schematics been revised; and
8fe30eca-9c18-598e-8d35-6cfd76a36d84 | note | Have plan drawings been provided (plant areas, floor plans, reflected ceiling plans for typical rooms); and
b8b0688e-f27a-5c60-8ae0-d107fb66a5b1 | button | Do they include maintenance requirements? | Yes, No
b81db297-851b-499e-befb-e1ddcbe56dd3 | checkpoint-no-value | GM Fire Sign Off
66c9b0fb-1161-4f24-8f36-a6a97d377b7f | signoff | GM Fire Sign Off
b2a86ba8-ad5f-49e1-b10f-27b66cf11ac8 | checkpoint-no-value | Principal Contractor Sign Off
5a1c0d5c-5b01-447e-8032-cc49f6fc34f0 | signoff | Principal Contractor Sign Off
d46cd526-4c4b-41e1-b53a-50121b7f7f9c | checkpoint-no-value | Consultant Sign Off
aa343bd2-d20f-45bf-b16c-9c1b8662358d | signoff | Consultant Sign Off
73005baf-803a-4729-9c5b-7a228e894099 | checklist | ITPS-305 QH Construction Documentation | itp | ITPS-305 QH Construction Documentation
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
7faeb37b-2f1a-463c-bde9-d414a6b6e821 | checkpoint | 1. Compliance
d6540663-31ba-5eda-88c0-4dbf36c07442 | note | Only deviations that have already been approved up to this point are assumed.
c650ad2c-51e0-5ebf-b07a-59b97cf30e1d | note | New design deviations should not occur in the CD phase since all scope has been approved during the Design Development (DD) phase.
7b2ec361-1967-57f9-9d00-f69b3ed168b1 | note | Only deviations with detailed Construction Issue Resolution (CIR) specifications will be considered.
aaccb674-9b33-5b8b-9a19-75c150dad535 | note | All deviations must be raised through a non-conformance submission process.
b698764c-5aaf-53d8-9fd0-e03cdee67398 | button | Has a listing of codes and standards been provided? | Yes, No
ddff9408-eb73-5be4-97e8-43ad4af35c96 | note | Redundancy and reliability:
2756ebad-bc9a-5f30-85d2-52c156a989c3 | button | Do specifications and drawings incorporate redundancy and reliability requirements in accordance with the site strategy? | Yes, No
514e7219-f87d-5f13-a089-cabcfae63583 | note | Future proofing:
9cbc904f-88fa-5531-96e1-9cb04651fa4f | button | Do Specification and drawings include future proofing per approved strategy? | Yes, No
41cc3aea-9c2f-5f5a-86b3-070aa7385b25 | note | Disaster management:
654635c4-75b2-5eb4-acf8-281981b0281f | button | Have you ensured design documentation captures extent of the required strategy? | Yes, No
e5374fa5-1844-5314-b476-bff669e75832 | note | Performance & Maintainability:
0c64b131-0ba9-57d8-bc93-3e90febe0034 | note | Performance meets the requirements of Australian Standards and NCC; and
43b5a2b9-d979-5fc7-83f3-091de1c5d3bd | note | Maintainability for all plant areas, risers, serviceable equipment and valves is detailed in the documentation; and
4cfeb15c-44ea-5eaa-af14-17e31613c8f6 | button | Have you completed the safety in design review? | Yes, No
0147b965-e3c8-5bf1-815a-92ce96353c27 | note | Commissioning testing and post-occupancy:
1b786ec9-ecaf-5512-b844-4cfca81f666b | note | Have you ensured testing and handover requirements have been specified; and
ade22b5f-480b-5d41-869d-d456f58a2bfe | button | O&M requirements are included within specification? | Yes, No
eeb523a7-9bc4-46da-93c0-021d4e6b6aac | checkpoint | 2. Design process
ea10ed99-a39b-514e-948a-e5bd940cc698 | note | Are specification and schedules ready; and
f2234a3e-819e-5825-b7b2-a9d01b03865b | button | Have final drawings (plans, schematics and all necessary details) been prepared? | Yes, No
f52f679d-81e2-4204-a79a-12098ef5fe2d | checkpoint | 3. Cost estimates (in conjunction with QS for all phases)
771b311a-bb20-5fa6-b44a-c5f4091cbb0d | button | Have QS confirmed cost estimates based on final design requirements that have been confirmed by the engineer? | Yes, No
f5389d5c-619e-44e6-8a6e-2da9f08ef1a6 | checkpoint | 4. General Coordination
49c0390d-2fa0-50b8-9c56-d9e3df5e61c3 | note | Have you coordinated maintenance requirements for inclusion in specifications; and
8edd7fe8-6f18-5d5a-a622-55b3b973a1a0 | button | ‘work by others’ within specification documentation? | Yes, No
ab7f85ef-8e78-4b7d-96c4-e6974601da77 | checkpoint | 5. Documentation, Reporting and Drawings
18adf019-bdaf-5ebe-b245-5c133f36c9b8 | note | Have all detailed specifications, technical schedules and associated documentation for fire safety services been provided; and
f404c4ee-c5e0-5d3b-b906-b68b0bddabbe | button | Are all schematics plans and details finalised? | Yes, No
a4f0a16a-ea35-4e07-b7d9-b849c4ffb03e | checkpoint-no-value | GM Fire Sign Off
c4b8ff3d-1706-481b-94ca-43f8b0ab210d | signoff | GM Fire Sign Off
d9e0a1b2-6ac9-4b64-95e8-21124980cd71 | checkpoint-no-value | Principal Contractor Sign Off
de2caeeb-0e43-4af8-8711-7dfdd7fdf9b2 | signoff | Principal Contractor Sign Off
16a2051a-3956-4318-bb58-bf9875c349c7 | checkpoint-no-value | Consultant Sign Off
ad3bd892-cb6c-41d8-a82d-c45e46e4e132 | signoff | Consultant Sign Off
f707b54b-c4ca-4978-9137-e1317ec8651d | checklist | ITPS-400 Temporary Fire Strategy |  | ITPS-400 Temporary Fire Strategy
ebae269f-8367-4e83-a6b6-e0eb70a9d934 | section | Details
511b03de-fd22-4286-aeae-9f91e479a00c | checkpoint | 1. INSTALL AND CHECK PORTABLE FIRE EXITINGUISHERS INSTALLED AT FIRE EXITS
faf4bb99-4b1e-4d33-8ab4-860aca06cb36 | checkpoint | 2. INSTALL AND CHECK HYDRANT BOOSTER INSTALLED, BLOCK PLANS, LABELS
c9e3e0e3-5ce6-4e1c-9b6e-e22e98c2f7d2 | checkpoint | 3. CHECK EXTERNAL ATTACK HYDRANT IS WITHIN 20M OF BOOSTER
8647a4d0-9cda-4baa-830c-bcea5ee08362 | checkpoint | 4. INSTALL AND CHECK SYSTEM IS PRIMED WITH WATER (TOWNS MAINS)
9bf43ca2-d47d-41be-9c4e-46e7eeaa6f85 | checkpoint | 5. INSTALL AND CHECK HYDRANTS INSTALLED PRIOR TO JUMP
72b05451-f74d-4883-aacb-90322f163ac6 | checkpoint | 6. CONDUCT WATER PRESSURE TEST OF HYDRANTS
bde6be51-9ca0-46fb-a727-d2914ff774f0 | checkpoint | 7. HOLD POINT DETAILS
43a5f0aa-6f75-5a87-abb6-6677f259d248 | button | Hold Point Required: | Yes, No
1a3dafea-3716-4eb7-8c44-4d603a802204 | checkpoint-no-value | GM Fire Sign Off
aeaf81f4-af0e-4a03-962d-4616683668a8 | signoff | GM Fire Sign Off
70354177-f4c6-43fc-9504-d371c59dd988 | checkpoint-no-value | Principal Contractor Sign Off
b52879d0-5189-4172-abf7-2afbc86d3c3f | signoff | Principal Contractor Sign Off
6b1ff98c-ffbe-4551-b827-8b2a9f12b156 | checkpoint-no-value | Consultant Sign Off
d407d0cf-d050-4e9b-b308-2d0a532972e4 | signoff | Consultant Sign Off
3a058ec3-6a06-4d0d-8a56-6e30921a529a | checklist | ITPS-401 Site Temp Asset Lists Extinguishers |  | ITPS-401 Site Temp Asset Lists Extinguishers
8ca88900-3ee1-41d8-bef3-ea715c8f9a54 | section | Details
bd6eb1a3-8da1-422e-ae47-03770d186536 | checkpoint | 1. ASSETS 1 TO 10
1f4db744-6979-572e-926f-0d31244c78c2 | note | Add Photos and Numbers Below:
61a6f193-4da8-4335-8a3d-b4d1102412f0 | checkpoint | 2. ASSETS 11 TO 20
1a65182e-7d3a-58e4-918e-9c1aa044d9f1 | note | Add Photos and Numbers Below:
e52ada7f-bbbf-444a-b1e5-b5067999bae1 | checkpoint | 3. ASSETS 21 TO 30
10bbe412-34a6-54e8-bab0-44ea5023b09f | note | Add Photos and Numbers Below:
1eedb57e-ba37-4558-900c-4202873188e0 | checkpoint | 4. ASSETS 31 TO 40
f66cbd3c-d86f-5916-87be-8822edf10157 | note | Add Photos and Numbers Below:
9f788a1e-c34b-4ced-a8b4-938387b2a142 | checkpoint | 5. ASSETS 41 TO 50
0df95690-b919-5fa2-acc1-8d125eeed0eb | note | Add Photos and Numbers Below:
c8b547ec-2dac-462e-b07e-34c61bc1b0ab | checkpoint | 6. ASSETS 51 TO 60
2d6609af-e091-57f7-9b1b-2a9dac3d1417 | note | Add Photos and Numbers Below:
a22a3824-505b-40cd-abaa-fb9b90339e8e | checkpoint-no-value | GM Fire Sign Off
545b4098-da67-40e9-a1a3-3372ea8bf573 | signoff | GM Fire Sign Off
15f8eb8e-9112-4524-9a05-c30d4ca65811 | checkpoint-no-value | Principal Contractor Sign Off
b66564f9-2f84-4112-b087-e4f31f7b7e82 | signoff | Principal Contractor Sign Off
ca5a9b16-7e30-4af6-9152-11d124cc9fb5 | checkpoint-no-value | Consultant Sign Off
75f9446c-68f0-4b79-8211-b81372a4f65c | signoff | Consultant Sign Off
1e70382a-cd84-5ae1-8862-c1c058edde43 | checklist | Lendlease Contractor Schedule H Checklist |  | Lendlease Contractor Schedule H Checklist
7a748d55-533f-527b-b0f9-60e8fa293f5f | section | Incident Reporting
38cbcaa2-534b-452f-a320-76d33f74f460 | checkpoint | Incident Reporting
b5b35a37-7382-54ba-8bfb-811dbf4572bf | button | Any incidents were immediately verbally communicated to Lendlease | Yes,No
6801e20c-e2f1-5a7f-a0d5-fe47c4fd717b | button | A copy of Incident Notification Form was submitted within 4 hours | Yes,No
66e9a4c6-0421-5ef0-8732-cd78bca8e3a8 | note | Detail any incidents from the past month below and attach relevant forms below.
826609b4-fc54-5a39-ad75-e1293f234680 | section | Workers compensation first, progress and final medical certificates and Return to Work Plans
0c9492a0-811a-544b-b5bc-2fc846063034 | checkpoint | Injuries and Illnesses
e20f96b2-5ee3-56b2-b5c5-912388171f1b | note | The following have been provided;
5492c177-794d-5136-81c9-8f8430e1d1c8 | button | First Medical | Yes,No
823e0dc6-15b2-594f-962a-261c0a26bf92 | button | Progress Medical | Yes,No
09fd6dbb-22b0-55d9-bec1-c657d23b526c | button | Final Medical Certificate | Yes,No
d36edd68-abcb-576d-b8fc-6978886ed6b8 | button | Return to Work Plans | Yes,No
a20041b8-0ee5-5f04-a4e5-2f9b0b26598b | button | I have submitted any necessary Injuries and Illness forms within 2 hours. | Yes,No
b9e71c13-fb0c-5796-9a4d-1f3ce13a3ae0 | section | Reporting
e2cefbe1-7b4c-58cb-9296-52013acd2aff | checkpoint | A copy of any regulatory notices has been submitted to Lendlease via email immediately following receipt from regulator.
4094ba7a-5738-5658-93bd-78c5dff3acda | checkpoint | Daily Pre-Starts have been delivered to the office by 9am each morning.
4fb06383-4684-5418-9d3a-cc9f4daa39dd | checkpoint | I have submitted a copy of Toolbox Talks to Lendlease weekly, including records of attendance.
67b6449c-0fcb-586a-8ebf-2addf988ee69 | checkpoint | I have conducted a miniumum of 1 EHS inspection per day and a copy of EHS inspections for the month have been submitted.
2c6854ff-7dce-52fd-90e9-e611023a913b | checkpoint | Labour Statistics and Man Hours
c45fef96-b2bf-597b-b3ce-585cf62a4bdb | note | Contractor Labour Statistics:
3961a981-e885-5a9c-877f-050b8d38419c | button | Has been completed weekly? | Yes,No
2fcfc2ff-fc1b-5978-9631-1633f919466f | button | Has been submitted before the 26th day of each month? | Yes,No
506b1288-bedf-5659-a27b-52efdb96cd11 | button | Is attached below? | Yes,No
c5929b96-f03b-5652-94b3-156328f9754d | checkpoint | SWMS
1bfaab1b-8e49-53ee-9e9e-873030346dbc | button | Copies of updated SWMS have been submitted to Lendlease | Yes,No
e4104c40-5765-5a71-b723-f81d0bcfb590 | button | Contractor SWMS review register has been submitted to Lendlease | Yes,No
1adcbe56-3cdc-5f92-af30-4e947fc6e60f | button | Updated copies of signed SWMS have been submitted after onboarding each worker | Yes,No
d064d5c0-d0e0-5fe2-a4de-7727e0a3ff4a | checkpoint | Workers are trained and competent
973bcb55-6152-5f6d-a2b0-4d5902cff6f6 | button | Copy of current training register has been submitted | Yes,No
58d3b39a-17b8-56a7-9770-52ce522e2ef8 | button | Copies of licences, qualifications, training records for any courses attended during the month | Yes,No
3495576f-5639-59ab-a767-a607784a3cf2 | button | VOC (Lendlease Template) for concrete saw/angle grinders and Plant to be submitted for all workers before operation | Yes,No
aef74d7b-d587-5e34-9266-884de37191d4 | checkpoint | I have submitted copies of daily pre-start inspection records for the month
d77f5e32-8a3c-5a96-97b8-96e1ee4e803b | checkpoint | I have attached a copy of the up-to-date Plant & Equipment Register
863d56e4-a279-57b2-a68e-d4b15f9c5577 | checkpoint | Copy of current and up to date Electrical Register has been submitted ( 3 monthly unless new tools added)
1c11da09-d5b8-50be-807f-7a10f77c3645 | checkpoint | I have attached a copy of the Fall Prevention Register
f73063a9-6e9f-572b-981e-bc4461355341 | checkpoint | Lifting gear to be inspected, tested and tagged
e9a421ee-a73c-5e73-8691-a5ecb3c66c99 | button | I have submitted to Lendlease and attached below a copy of lifting equipment quaretly testing register | Yes,No
92bd2845-9677-5a10-9f62-2f292143cd1c | button | I have submitted annual inspection certificates to Lendlease | Yes,No
d8e7b937-09da-531f-a96c-18f76041589f | button | Monthly inspection register has been sent to Lendlease as per Lendlease Lifting and Slinging Guideline | Yes,No
ae92f7c6-9451-56f7-ae90-9960f5122f4b | checkpoint | I have attached copy of Hazardous Substances Register highlighting any chemicals brought on site this reporting period.
a02a0ab0-ff4d-53ee-8a92-1c3a98928fa7 | note | NOTE: Subcontractors are required to use Chemwatch to log all chemicals utilised
ba1f906f-1a0c-5a9f-a883-1abf31d17b82 | checkpoint | A copy of the Ladder register has been submitted this month
3d903859-b52d-52dd-aabf-1957c83c9f42 | checkpoint | I have attached a copy of Safety Data sheets for chemicals brought onto site within this reporting period (this month)
23484093-b5c0-5552-a60d-8d92e054fe12 | checkpoint | Temporary Works Design Register
75720ec4-cb43-5a56-a617-c22bb12e8de3 | note | NOTE Temporary Works Design Register must be submitted prior to mobilisation capturing of all Temporary works to be implemented by the trade
fcd4c867-242a-5081-80f1-6d415a64ea0b | button | I have attached the updated Temporary Works Design Register | Yes,No
5d21287a-0bce-5c38-a159-cd6673bf2998 | button | I have attached Evidence of Engineering Certification | Yes,No
d80834eb-8560-5715-b772-28441493f097 | button | I have attached Evidence of 3rd Party review of engineering | Yes,No
92ddcd9e-8e9b-5040-844d-c86a13562740 | signoff | Signatures
54b61932-c1fe-5b18-9a20-c6abcec6b8dd | checklist | POLICY-005 Safe Work Procedure |  | POLICY-005 Safe Work Procedure
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
90e555f1-b7db-5342-8f6e-ab9bb0160482 | checkpoint | Task Details
35e1d1ba-0df8-5940-a259-bccb2e916c8f | note | Use this form to record your safe work procedure after analysing a particular task in your workplace.
fb9e0a76-393d-592a-91df-e815f04daa63 | textbox | Work Area:
88a56175-6e66-5759-acca-aff345430919 | textbox | Task:
da1bc784-0a9f-5d8c-920c-1ef0c5a72b5d | textbox | Safety Risk: e.g. electricity, moving parts, noise
73bf96f4-9e1e-51a1-a557-4789936e6b2d | checkpoint | Personal Protective Equipment (PPE)
6455ae14-9591-5d78-a126-6b32f61c8232 | note | The following PPE must be worn, and precautions taken, when doing this task:
9f713af5-73c1-59dc-b084-7a3c2cf3b600 | tickbox | Work Gloves
6ec63488-d4c6-5096-8d62-8158b75870b4 | tickbox | Safety Glasses
64c63526-5a83-5c7d-a3fa-bbb76c5b5c62 | tickbox | Steel Cap Boots
83f78842-c3cd-59b1-9ff7-a8a0017d78dc | tickbox | Ear Protection
72bcb4cb-bf42-5039-b494-9375956a3b79 | tickbox | High Visibility Vest
30b3c185-f375-5785-99bd-75f1c6181665 | tickbox | Head Protection
943a7197-78bf-5b79-99b5-476d057fb450 | tickbox | Respiratory Mask
dee2c30b-edc0-5cd4-aaeb-4bf5a219de4e | tickbox | Face Mask
16c50b5b-5bd7-5e8b-bdcd-08c57fc113d6 | tickbox | Protective Clothing
7a9b8916-016c-5db4-a6f5-12378ee517c0 | tickbox | Wash your Hands
cc546369-bca4-51b6-ab24-8e4406ba760e | checkpoint | Supervisor Signoff
4570fb2e-7310-5ac1-a58f-8ade9076d7c2 | signoff | BY SIGNING I CONFIRM I HAVE APPROVED THIS SAFE WORK PROCEDURE
6faa1732-cd0c-59fd-9f51-6c60dff51223 | checklist | REPORT-002 Hazard |  | REPORT-002 Hazard
8111ace1-1386-5c1f-8290-3df28e3c8d3f | section | Details
7016619e-d9e9-575d-a598-04fc8176f882 | checkpoint | Hazard Report
43f0228c-2fe3-5c6e-85e3-84048cef3fea | note | GM Fire employees shall complete a Hazard Report in the event they identify a hazard that may result in injury or incidents to person(s), property/plant, the public or the environment.
82bf4eeb-5f0e-5f93-8ead-f55641b15686 | note | The principal contractor will be informed immediately and provided with a copy of this report.
423d5ed9-def2-5985-8cad-6c2afa7e0d08 | checkpoint | Hazard
c157c7de-d92d-505c-adbd-f9a7620ee7c6 | textbox | What is the hazard?
e23dd611-f6df-5b35-a2ee-6c2f1af58ca8 | checkpoint | Contributing factor
9664582b-bef9-5594-8875-1f56cd1aab82 | note | What are the contributing factors?
655bdfbb-ee2b-5728-aae5-5d3b6624ae50 | tickbox | Environment such as noise, slip or trip
9eb4f112-dc84-55ca-95ee-606b2ae625f4 | tickbox | Equipment/ materials i.e. wrong or inadequate
bdecd7f1-1e7e-59b7-8cff-fa37b4488ea3 | tickbox | Work Systems i.e. inadequate training
f9ec5884-395b-5fc3-8193-6f73553c064e | tickbox | People i.e. production pressures, lack of communication, lack of procedures
90dff80b-44cc-5e29-b4ee-fe7e1df7551e | tickbox | Other
d7af76c9-77a3-5b3d-85f2-229e182aed20 | textbox | If 'Other' please specify:
5b8936dd-da50-5d1e-a2b4-e9a5b6b57cc3 | checkpoint | Corrective Action
43a01400-3788-576b-a07c-ee5c2b0958e7 | textbox | What are we going to do to fix the problem?
dc1a0db9-5b08-56a1-8f09-eb0c829dcf7b | textbox | Who
7cb0663d-55b6-50d9-816f-cf668d5aa4df | textbox | When
09c0367c-9df2-5a1e-b57f-ce79d5be231a | checkpoint | Completed By
e8cad4f8-a779-54c4-8306-b65b38b7a52b | signoff | Signature
c2f28b0e-e821-54c1-a0ba-ee5986254ed9 | checklist | REPORT-003 Chemicals Review |  | REPORT-003 Chemicals Review
8111ace1-1386-5c1f-8290-3df28e3c8d3f | section | Details
76fb3e05-0ac8-4a4f-bb63-d30ea883739f | checkpoint | Details
fcbbdfbf-a580-58e2-aca3-6db3938b62ef | date | Date:
3d0346a2-15c4-5dd1-83d7-39fc0feb5a90 | textbox | Time:
eefd7d21-c3a8-5249-9155-dcea38b4b61b | checkpoint | Existing Register
96c307f7-229a-58ec-8971-6703204bb9aa | date | Last Revised on (date):
e98ad3cc-027f-5273-ad68-b11ab5b72cea | note | Upload a photo of the "Register-006 Hazardous Chemicals" as it is on site today.
586de132-0677-5158-8fb0-c38150ef6201 | checkpoint | Chemicals on Site
c1791c45-bbc2-5226-98ec-daa09d584a45 | textbox | Location where Chemicals are being stored:
64ef467f-1d6e-5a89-a833-62bedc96024f | note | Upload a photo of each Chemical on site
8cbd2a0e-3c28-53bd-b9da-5a65540b2443 | checkpoint | SDS
0dbf4695-dd94-54f8-b2bb-e4da68cc1f63 | button | Have any of the SDS sheets expired? | Yes, No
edcab06a-642e-5627-89fb-26a64e7739af | note | If 'yes', cease use of Chemical and contact GM Fire Management immediately.
c1c991c6-f8b7-58b3-bc66-63d765265e0f | note | Upload a photo of ALL Safety Data Sheets (SDS) on site.
58bfb4fd-b3d4-5f94-a67a-e067a225bcd0 | checkpoint | Declaration
c387a439-caf3-57d6-9d2f-ee67f6d50db0 | button | All Chemicals on site have been approved for use by the Principal Contractor | Yes, No
4f739c58-52c1-51f6-b261-1f8b7f974967 | button | All Chemicals are stored securely | Yes, No
6d438445-ff59-5c63-922f-bb4443e6bf75 | button | Any Chemicals that are no longer required on site have been removed and or disposed of as per WHSE guidelines | Yes, No
0da0ee29-0ac0-5051-ad4a-3e439a9e4b19 | signoff | BY SIGNING I CONFIRM I AM THE REPSONSIBLE PERSON FOR HAZARDOUS CHEMICALS ON THIS SITE, AND THAT ALL INFORMATION I HAVE PROVIDED IN THIS REPORT IS CURRENT AND TRUE.
42c7df9a-ccb8-5d7f-9abf-a956b1f84163 | checklist | REPORT-006 Incident Investigation |  | REPORT-006 Incident Investigation
8111ace1-1386-5c1f-8290-3df28e3c8d3f | section | Details
6412ac75-35b3-555b-a89e-87d89553cfa8 | checkpoint-no-value | Incident Investigation Report
26c7a877-82ff-5d4d-9964-4e831bec896a | note | GM Fire shall complete an Incident Investigation Report in the event of any injury involving medical attention or off site treatment or in the event of any incidents involving a near miss, property/plant damage or injury to the public or the environment.
c7009061-5139-5526-a062-83adc69dbabf | note | The principal contractor will be informed immediately in the event of the above. Following discussions with the principal contractor, a decision will be made as to who will conduct the incident investigation. The principal contractor will be provided with a copy of the completed Incident Investigation Report.
0bb42031-c4a8-5bcf-80ff-6fc5304ee4f4 | checkpoint | Class of Incident
319b1c6b-9f44-55ea-b16c-b1a07631b0a3 | tickbox | Injury
0adde8bb-4f35-5400-993c-c7d0180c2af2 | tickbox | Property/Plant Damage
621668cf-7542-5404-a731-45e940e7d4ee | tickbox | Near Miss
95d75d3d-669b-5354-b3b0-96b4a129a1c0 | tickbox | Environmental
67776edd-303c-58ed-b6a4-4c93c3ad56de | tickbox | Other
c5515547-5acf-5223-adaf-ff810432bbba | textbox | If Other - Please explain
e433ee97-85b5-52fa-97a9-25ca60ea13bc | button | Reported to Princpal Contractor | Yes,No
857bb4fc-18cf-5306-a76e-802c247b752f | textbox | Details:
e1d07f73-ecd2-514f-8842-5a2e0effd57f | button | Further Action Required | Report to Authorities,Other
820f14d5-50a0-5c15-96c5-71e6e32d06c6 | textbox | If Other - Please explain
bc36afa9-00da-5f53-99b5-0b99d61a7935 | checkpoint | Details of Incident
92284681-efd2-53d4-8e0b-d46de0d7e437 | date | Date of Incident
673f8d24-ff72-5e07-b453-93880d52a9f4 | textbox | Time of Incident
325ed646-43a2-5fc3-9425-0bef6e03fe7f | button | am/pm | am,pm
4b70799d-acc0-5966-a907-0ef28ba3f126 | textbox | Witness Name
541505a5-4428-5a09-a1c7-efa380a6cf43 | textbox | Witness Contact
fdfff4a4-8f76-588d-97bd-e1944521b0f4 | textbox | Nature of Incident
725a55af-18c7-57c8-afe2-bfa092de1b6a | textbox | Location of Incident
3f3be10a-9abd-53e3-82f0-2667d7e71aa8 | textbox | Description of Incident
b482344c-2e6d-577b-9ddb-70e3d053f88b | textbox | Details of damage to equipment/property?
5acc9a29-5ef8-55dc-93ab-9320efe0254e | checkpoint | Injured Person/s (if applicable)
24e6a102-3cb8-5740-9562-2f6fcc5871ca | textbox | Name
c68b8d90-60e8-5111-8e35-d7857559c628 | textbox | Address
e678a59a-6b1f-5756-b6cf-2d17da084cb1 | date | Date of Birth
66d64f8b-744b-59a5-8649-41a77a1b3902 | textbox | Occupation
f3631539-86a5-543a-ad2e-dad8be5e4b52 | textbox | Employer
df6586a3-039d-5599-8263-333b90fa2c9b | textbox | Referred/transferred to
2653d5b4-f6f4-5d10-b061-5710923ec319 | section | What factors contributed to the incident?
673b3686-24cc-52e8-a200-da491c74d4d4 | checkpoint | Environment:
5bebb027-96f0-5460-890a-132a143a47e3 | tickbox | Noise
5e04e3c6-c511-54d9-855b-61b79ba33d83 | tickbox | Layout / design
be7367f6-b65c-5e31-9806-b57e064484b1 | tickbox | Lighting
b344a257-3875-58bf-9242-ae1b70d9c52a | tickbox | Dust / fume
c1b98094-8764-57ae-8d8f-23524f9f5e83 | tickbox | Vibration
c6079cb7-cfed-539d-a3de-4ffe5242c1a5 | tickbox | Slip / trip hazard
85c76db0-7b13-5e0b-b320-9a0f6543aa2d | tickbox | Damaged / unstable floor
1e95cef6-f5ed-5510-89c5-ba7214c48c16 | tickbox | Other
7af769cf-fdc6-5763-a34f-36b7668432b1 | textbox | Other (if applicable):
da263eea-7753-5dda-9253-36aae5136ab1 | checkpoint | Equipment/materials:
fe1e78dd-509e-5b53-8078-3c13e8d0020a | tickbox | Wrong equipment for the job
48449b5b-94f5-56fd-aa68-28179f2a1234 | tickbox | Equipment failure
34dbaa91-66eb-5b35-86e6-12b7080c0add | tickbox | Inadequate maintenance
340c7cf0-23ea-5aaf-be3e-08341656325a | tickbox | Material / equipment too heavy / awkward
d44177e4-2535-597e-9309-931a3a8d12ee | tickbox | Inadequate guarding
3d7d49b4-0c2b-5d53-bfdc-aa67787549d7 | tickbox | Inadequate training provided
000690e7-a449-5a80-a869-a79c71c27c48 | tickbox | Other
e2a3d872-b06f-56d7-868a-7dfc157a60c7 | textbox | Other (if applicable):
29bb93fe-1a56-5a6a-a4d8-caafbdc08848 | checkpoint | Work systems:
5dd9bf85-df05-50a5-9d39-ba8c92524aee | tickbox | Hazard not identified
2fbf68fc-22c1-530f-9cb2-b87b25344ca7 | tickbox | No / inadequate risk assessment conducted
0387a054-0cba-5d62-97d1-4479ebe8b41d | tickbox | No / inadequate safe work procedure
d37a698b-994a-54ae-81f2-b04aa7a1df63 | tickbox | No / inadequate controls implemented
c6ba7810-1a06-5766-8b22-30f4fdc6cfd1 | tickbox | Hazard not reported
8f15171b-ea63-518f-a1d3-40a0cdb8bb86 | tickbox | Inadequate training / supervision
22ddaef3-e684-5031-82f2-eabc39055e20 | tickbox | Other
df7a8e40-28bc-528b-b28a-0b6efe49c3d3 | textbox | Other (if applicable):
13eb0e36-06f7-5153-ba71-5b36d7104644 | checkpoint | People:
68c29607-73a8-59a9-918a-e8a1a7758f3b | tickbox | Procedure not followed / no procedure exists
f49a9eb6-f469-5486-a041-424512d20bb0 | tickbox | Drugs / alcohol
315224a4-528b-59d0-b752-048abb08d4dc | tickbox | Fatigue
2ed0f27c-86d8-5e84-a4f2-361debecd863 | tickbox | Time / production pressures
1cf8af67-af67-5409-bca2-d1a6cdab08ea | tickbox | Change of routine
91dc8070-c2b8-5f0c-bd24-be694c6f87a7 | tickbox | Distraction / personal issues / stress
06712e9c-8051-58f7-8676-16be7955cabe | tickbox | Lack of communication
feefc030-bfe5-5354-a12e-104f9508da2b | tickbox | Other
c3685b47-7234-5973-bc9c-d337e162b8f6 | textbox | Other (if applicable):
1c21ef12-b1aa-5192-a53b-a50ba28212cd | section | Corrective actions:
e23dd611-f6df-5b35-a2ee-6c2f1af58ca8 | checkpoint | Contributing factor
34fb92e3-cc81-5b39-9cc4-3570d31ea806 | textbox | (from above list)
73874509-bac9-555d-8853-d738436ac006 | textbox | What are we going to do to fix the problem?
da26fb44-6d60-52fb-870e-90b8c5ffd716 | textbox | Who
f5d8b083-01e8-5841-aea1-53e16258b921 | textbox | When
585d5a57-d317-5a2c-8c86-399f10c406d3 | date | Completion date
09c0367c-9df2-5a1e-b57f-ce79d5be231a | checkpoint | Completed By
11f31f0b-4a44-5a8b-8133-2e07b430d536 | textbox | Name
9346513a-1500-5fae-b25b-d6e769dd31d7 | textbox | Position
40b6d092-dcdd-58fd-840d-c4a54e7f5c2d | date | Date
e8cad4f8-a779-54c4-8306-b65b38b7a52b | signoff | Signature
a4212db3-265b-5d19-9d4c-fb8f4780e6bf | checklist | REPORT-010 Request Corrective Action |  | REPORT-010 Request Corrective Action
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
8111ace1-1386-5c1f-8290-3df28e3c8d3f | checkpoint | Details
297d7da6-d94b-5611-bd0c-702c41cc33b1 | date | Date:
eedfd367-e843-5c3e-9193-ab41c84ef7aa | textbox | Time:
7a3ad93f-82ff-58bd-8541-95c08d4b5a25 | textbox | Location:
1207ac55-2622-5c8f-951b-2639b0dc564e | textbox | Supervisor Name:
d5aaa5eb-093f-5332-af20-a8b65033877e | checkpoint | Corrective Action Report
8935e3f9-ddeb-55d4-a028-6925bb83b863 | textbox | Principal Investigator
d0e213ca-26d1-5132-b6f3-d05c03ab33d5 | note | Non-Conformance is:
1ae631a5-072b-53cf-91df-6dd2aea39da5 | tickbox | Minor
de4f5de6-b1c9-550b-8bd5-3a7b53fda615 | tickbox | Major
bd4c3acf-a07e-5421-93fa-20e23a4a5b31 | tickbox | Critical
ddfa40b8-8d09-56f1-a1da-f91e07948d85 | textbox | Details of Non-Conformity Identified
db9b8c8d-7035-5210-8db8-53f6d5fc9674 | button | What is the likelihood of Fatality? | Very likely, Likely, Unlikely, Highly Unlikely
8687753c-2eb2-584f-b974-2298103b5684 | button | What is the likelihood of Major Injuries? | Very likely, Likely, Unlikely, Highly Unlikely
a0ddfdb1-ac2a-55ba-805f-904b06bf787a | button | What is the likelihood of Minor Injuries? | Very likely, Likely, Unlikely, Highly Unlikely
5ab5854b-b2a6-57e3-bf06-6738c14f36b6 | button | What is the likelihood of Negligble Injuries? | Very likely, Likely, Unlikely, Highly Unlikely
a1447274-b77a-579d-813e-8403ec194660 | note | Add photo evidence if applicable.
5d294295-86ae-51e1-92b2-e35eee764d2a | checkpoint | Corrective Action Plan
a567af7e-c8e7-580f-a2d1-bb2fbe30ed4a | textbox | Describe corrective action
b7d89de9-a208-53f8-875e-fef30341ce39 | textbox | Is this plan permanent or temporary? | Pernament, Temporary
167dc1ac-6bf6-5cec-95fb-38014a1058a3 | date | What is the proposed completion date?
42c21dbd-9bff-5051-bd1f-f936237b2320 | checkpoint | Signoff
2923664c-ab55-5c48-87d4-1901f7c5ef27 | signoff | BY SIGNING I CONFIRM I HAVE COMPLETED THIS REPORT TO THE BEST OF MY KNOWLEDGE
47a05a8f-01d6-5308-b319-09c8bfef63a9 | checklist | Ω (DEPRECATED) CHECK-006 Daily Prestart (v1) |  | CHECK-006 Daily Prestart
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
af98ba3f-7105-4c3e-be07-e2ab6454306d | checkpoint | CLOCK IN
c58e65ab-a72b-4fed-85ca-080ec1fa3336 | signoff | Sign here to CLOCK IN to your shift
0b4ad232-5674-51d3-9408-aef0b58a609d | checkpoint | Details:
c67a5ad6-470a-5e2f-997a-f5f60b5e37f6 | date | DATE:
be60c24b-9584-50b3-85e7-c97aac850d9f | textbox | TIME:
5309490c-3518-5494-8898-6b41003721aa | textbox | SUPERVISOR NAME:
694414d8-1e1b-5f09-a0ec-7b8d590ad762 | checkpoint | Issues
29d3d625-f08c-54b1-bf3c-b22dfa3fbd75 | button | Are there any issues arriving from yesterday? If YES, detail in comments below. | Yes,No
88bc1641-daee-577f-b7e3-efc84c9a3236 | note | NOTE: If this requires a change to the SWMS then please ensure this is captured and relevant personnel inducted.
0662f670-ac3d-5439-af86-c1336a2b3861 | checkpoint | PLANNED WORK ACTIVITIES / TASKS
89e3b170-750e-51d8-a682-a426806358d3 | textbox | ACTIVITY / TASK
63009163-b71f-5d74-88ab-182d0339fbec | note | SWMS that relate to today's task/s
3217cd42-d7b4-5c06-8925-f508bd3b2eb4 | tickbox | 001 – Working with elevated work platforms
4e6ff252-595a-527a-99b7-8b0d317de7fb | tickbox | 002 – Wiring Rough In Minor
cd7e73e3-d703-52b7-9d32-c59cb15791e0 | tickbox | 003 – Fit off fire alarm system
b8ad95df-8b35-52b0-9faa-5efb930c096d | tickbox | 006 – Installation of pipe and fittings
2fc333ec-8649-5094-9bac-e7db22722260 | tickbox | 007 – Manual handling
793477a1-ebab-528d-ac0f-4cf5e41a28fa | tickbox | 009 – Pressure testing of pipework
abf682f7-668c-584c-add3-69603f01ffe9 | tickbox | 051 – Using platform ladders
aab532fe-44ab-58ce-84b2-320c641c1eca | tickbox | 060 – Inhalation of Respirable Crystalline Silica
55efd7fe-fc29-5217-af4c-3858f7a3124e | tickbox | 061 – Working in Major Area of Concern
774a66c3-3fea-5200-a769-32e4e0d72e01 | tickbox | Task-specific Safe Work Procedure
23c8da75-1795-5395-a9d2-b738a880bbe9 | checkpoint | Is a SWMS in place for ALL high-risk construction work and work procedures in place for all other works?
018251a3-fdc4-5187-821b-085ee9060fc3 | note | IF NO, STOP AND DEVELOP!
ebf4ce4a-0774-58f0-a144-522ec96b5a15 | checkpoint | Are you subcontracting out any works today and will you be interacting with other trades?
95fe8c17-73e5-5a12-84ab-0e88db6ce7aa | textbox | If YES, please list
279dbae7-8c1f-5553-98d3-d60918e8eade | checkpoint | Permits
ccbee4d0-b0fc-50f9-aba7-187627b00d3a | button | Isolation Permit | Yes, No
e9e5dd68-707a-5644-8f38-af984c59f3e6 | button | Have conditions changed since permit approval? If YES, please note changes below. | Yes, No
498988e2-fa90-543d-abe2-62bbc0b59d3d | button | Hot Works | Yes,No
49f83c80-5eec-5445-acf1-c5c9e01af072 | button | Permit to cut or drill | Yes,No
26129dde-acee-57f3-b54c-c083077e591c | button | MAC Permit | Yes,No
1d20b088-7c9c-5436-8f27-c1ecd33f79fd | note | Please list Permit numbers with description below, and upload photo/ attach file if available.
cae12b06-72bd-55e9-a701-9b47a7fdd5d7 | checkpoint | Environmental Risk
d043a4ae-8752-53fc-bcd7-920e72521388 | note | What controls are in place to manage environmental risk on site, specific for today; e.g. Wash out areas, maintenance of sediment fences and drains, monitoring of dust?
be468b16-df19-537b-854e-46bbd3df7b89 | tickbox | Clean up the general area
03b3f67c-e939-50e1-8cb2-87e19dbe9fd7 | tickbox | M-Class vacuum
054df62a-5657-559a-8159-5ed36c7947b6 | tickbox | Fit test and appropriate fit mask
3640b7ac-10ad-5ec3-ab6e-ae1284393ae1 | tickbox | Spill kit onsite
9bbc93b8-7fb5-5515-8c51-902ff1a50612 | tickbox | Other - detail below
903e1008-c734-5d92-8e65-be1215f53964 | checkpoint | Checklist for Activities
f1e2b79e-aefd-53e7-bcd3-7868bdf06e49 | number | Number of people in your Work Group
57c8c5eb-69d5-5928-bcc8-b3fe0690aa3a | button | Daily Risk Assessment Completed | Yes,No
d198e689-340f-595d-aa6c-5796b9e55eea | button | Qualifications/training of staff adequate for work activities | Yes,No
a89c730d-f0a5-5583-9141-f6861600debc | button | Plant and Equipment on/off site | Yes,No
c2abc099-5048-5862-be7e-69276e515d47 | button | Equipment safe to use | Yes,No
c35b1cc8-2353-5462-9376-b66fbffbe2eb | button | Work area inspected and safe for staff to enter and work in today | Yes,No
446e2139-b3e3-5032-b3b7-4b2ecf6682f2 | button | Appropriate and adequate PPE supplied to work teams (SWMS/SDS) | Yes,No
1297b9fc-83fc-5f03-8c96-a7ef0df8cad5 | button | Weather conditions for work to be conducted assessed | Yes,No
50775e4c-331c-5bcf-9d61-90de79b49eb6 | number | How many workers have been allocated for today’s clean up?
31b028e3-39b4-5b10-96c0-301d4210e7d4 | button | Pre-start communicated to all work teams including all trades & subcontractors | Yes,No
32acab0e-b839-50e4-92ee-ec700a394dd0 | button | I acknowledge that all Plans on my Dropbox shared file are up to date and I have confirmed this with management | Yes,No
f21451ba-8bea-5c8f-a381-24f716ce840c | checkpoint | Builders Briefing Notes
96ad1a92-eed7-5574-b446-3263c628aa29 | note | Attach a photo of the builders brief
2bcc0a89-8c1f-5fe5-958d-a1f1ba7233a4 | checkpoint | General Notes
1c629449-37f4-4cd8-a865-4ea5fefe42fe | checkpoint | Mental Health Check-in
cd31bf4e-e2d5-5d58-b35c-fd75f58de3c1 | note | Prior to commencing work, ask your fellow workers: Are You OK?
0c6ae895-4776-5618-ae00-20be5d041a11 | note | Mates in Construction 1300 642 111
bd2c90e5-3cd6-5a5f-aefc-f4f34c1caf48 | note | Beyond Blue 1300 22 4636
3ecf9d4d-a367-5b79-a67e-d473daee966d | note | Gambling Help 1800 858 858
065e825a-d2be-5f52-accd-f30095264611 | note | Drinkwise 1300 858 584
462a3bfd-f982-5f3f-95bf-2a3e5632bbde | note | GM Fire Management 07 3519 7573
42c21dbd-9bff-5051-bd1f-f936237b2320 | checkpoint | Signoff
ad0d0126-8a7e-5cc0-84b3-32f1ee14e2ef | note | Remember to clock in and out of your shift.
2c27aaf3-a648-56ea-92c9-e1e22f200a26 | signoff | By signing I confirm I have have partipicated in this Prestart and I understand my roles and responsibilities today.