## Project Structure
Folder Structure |  |  |  | Checklists | #NAME?
Site QA
Switchboard's
Exterior
|  |  | DB-C | Switchboards
|  |  | DB-C1 | Switchboards
Block 2
|  |  | MSB-2 | Switchboards
|  |  | T1 | Switchboards
|  |  | T2 | Switchboards
|  |  | T3 | Switchboards
|  |  | T4 | Switchboards
|  |  | T5 | Switchboards
|  |  | T6 | Switchboards
|  |  | T7 | Switchboards
Block 3
|  |  | MSB-3 | Switchboards
|  |  | T1 | Switchboards
|  |  | T2 | Switchboards
First Fix
Block 2
|  |  | Service room | First Fix Electrical
|  |  | T1 | First Fix Electrical
|  |  | T2 | First Fix Electrical
Block 3
|  |  | Service room | First Fix Electrical
|  |  | T1 | First Fix Electrical
|  |  | T2 | First Fix Electrical
|  |  | T3 | First Fix Electrical
|  |  | T4 | First Fix Electrical
|  |  | T5 | First Fix Electrical
|  |  | T6 | First Fix Electrical
|  |  | T7 | First Fix Electrical
Exterior
|  |  | Pole lighting | First Fix Electrical
|  |  | signs | First Fix Electrical
Second Fix
Block 2
|  |  | Service room | Second Fix
|  |  | T1 | Second Fix
|  |  | T2 | Second Fix
Block 3
|  |  | Service room | Second Fix
|  |  | T1 | Second Fix
|  |  | T2 | Second Fix
|  |  | T3 | Second Fix
|  |  | T4 | Second Fix
|  |  | T5 | Second Fix
|  |  | T6 | Second Fix
|  |  | T7 | Second Fix
Exterior
|  |  | Pole lighting | Second Fix
|  |  | signs | Second Fix
FEL SM Weekly Site Checklist
| 2024-11-04 |  |  | FEL SM Weekly Site Checklist
| 2024-11-11 |  |  | FEL SM Weekly Site Checklist
| 2024-11-18 |  |  | FEL SM Weekly Site Checklist
| 2024-11-25 |  |  | FEL SM Weekly Site Checklist
| 2024-12-02 |  |  | FEL SM Weekly Site Checklist
| 2024-12-09 |  |  | FEL SM Weekly Site Checklist
| 2024-12-16 |  |  | FEL SM Weekly Site Checklist
| 2024-12-23 |  |  | FEL SM Weekly Site Checklist
| 2024-12-30 |  |  | FEL SM Weekly Site Checklist
| 2025-01-06 |  |  | FEL SM Weekly Site Checklist
| 2025-01-13 |  |  | FEL SM Weekly Site Checklist
| 2025-01-20 |  |  | FEL SM Weekly Site Checklist
| 2025-01-27 |  |  | FEL SM Weekly Site Checklist
| 2025-02-03 |  |  | FEL SM Weekly Site Checklist
| 2025-02-10 |  |  | FEL SM Weekly Site Checklist
| 2025-02-17 |  |  | FEL SM Weekly Site Checklist
| 2025-02-24 |  |  | FEL SM Weekly Site Checklist
| 2025-03-03 |  |  | FEL SM Weekly Site Checklist
| 2025-03-10 |  |  | FEL SM Weekly Site Checklist
| 2025-03-17 |  |  | FEL SM Weekly Site Checklist
| 2025-03-24 |  |  | FEL SM Weekly Site Checklist
| 2025-03-31 |  |  | FEL SM Weekly Site Checklist
| 2025-04-07 |  |  | FEL SM Weekly Site Checklist
| 2025-04-14 |  |  | FEL SM Weekly Site Checklist

## First Fix Electrical
type | name
checklist | QA - First Fix
section | Flush Boxes
checkpoint | Fire Rated or Acoustic
checkpoint | Height as per plan
checkpoint | Location as per plan
checkpoint | Intumescent Pad In Place
section | Cabling
checkpoint | Power cables installed correctly
checkpoint | Lighting cables installed correctly
checkpoint | Equipment cables installed correctly
checkpoint | Circuits clearly labelled
checkpoint | Separation between Data and Power at 300mm or as specified
checkpoint | All cables secured via cable ties with ends cut
section | Cable Ladder
checkpoint | Minimum 25% spare capacity left on cable tray
section | QA - Lights
checkpoint | Setout Correct
checkpoint | Cabling in correct location
checkpoint | Emergency/ Exit Lighting
checkpoint | Nogging installed for Electrical Services
section | Seismic Bracing
checkpoint | For Lighting
checkpoint | Cable Tray
checkpoint | Switchboard
section | Conduits
checkpoint | Correct size installed
checkpoint | Location as per plan
checkpoint | All conduits glued & watertight
checkpoint | Clean inside and in good condition
checkpoint | Stainless screws used
section | Photos

## Switchboards
section | Switchboard
checkpoint | Spatial certificate signed if required
checkpoint | Fixings installed in wall correctly if board is wall mounted
checkpoint | All clearances sighted to ensure location is compliant
checkpoint | All cables correctly installed in protection device and earth and neutral bars and fully secured
checkpoint | Cables neatly dressed
checkpoint | Phase tabs on chassy covered
checkpoint | All earths and neutrals labelled to match phase numbers
checkpoint | Switchboard is clean on the inside and outside
checkpoint | Masking blanks installed
checkpoint | DB legend installed
checkpoint | Feisst label on the door installed
section | Photos

## Second Fix Electrical
type | name | values
checklist | QA - Second fix
section | Power Outlets
checkpoint | Correct type installed
checkpoint | Correctly installed with terminations all secured properly
checkpoint | Outlet Installed level
checkpoint | Circuit Tested and results recorded
checkpoint | Description Labelled on the outlet face with vivid and with dymo labeller on cover plate and ensure label is level
section | Light Switches
checkpoint | Correct type installed
checkpoint | Correctly installed with terminations all secured properly
checkpoint | Light switch Installed level
checkpoint | Circuit Tested and results recorded
checkpoint | Description Labelled on the outlet face with vivid and with dymo labeller on cover plate and ensure label is level
section | Light Fixtures
checkpoint | Correct type installed
checkpoint | Correctly installed with terminations all secured properly
checkpoint | Tested for operation
checkpoint | Correctly installed with stainless screws & 90 / 45 angle
section | Photos

## SM Weekly Checklist
type | name
checklist | FEL SM Weekly Site Checklist
section | Monday
checkpoint | Prestart Meeting with Team
checkpoint | Review Tasks for the week
checkpoint | Identify Targets Including Hours
checkpoint | Approve hours by 9AM for previous week
checkpoint | Review SWMS
checkpoint | Site Toolbox Meeting
checkpoint | SSSP in Order
checkpoint | Materials organized for week ahead
checkpoint | Plans printed with any relevant notes added
checkpoint | Submit Toolbox minutes to main contractor and FEL office
checkpoint | Job Cards up to date and submitted
checkpoint | Team tasks for week ahead filled out on whiteboard