## Specific Levels
PREMIER FIRE - DGC - BC059
FIRE PROTECTION SERVICES – HYDRANT |  | ITP Prepared By: Troy Turner Project Manager |  |  |  |  | Persons Consulted In The Development: TT, CM, JP
QUALITY CONTROL CHECK LIST |  |  | Form: |  |  | REV:
Level: |  |  |  | Area:
Principal Activity: FIRE HYDRANT SYSTEM
Activity | Date | Premier Installer Check |  | Premier Design Check | Multiplex Sign | Client Sign | Comments
Initial Design
FIRST FIX - FLOOR HYDRANT
Pipework Fabrication
Delivery inspection
Fittings to Spec
Pipe and weld quality
Cut sheets and plans align with pipe delivered to site
Installation Inspection
Installed to approved drawing
Compliance with AS2419
Check Hydrant Landing Valves - Type and material - Joints and connections - Position and spacing / obstruction -fixing and supports in accordance with AS2419 | [6 empty] | Note number of units per floor attach photo
Check Hose Reel - Type and material - Joints and connections - Position and spacing / obstruction -fixing and supports in accordance with AS2419 | [6 empty] | Note number of units per floor attach photo
Isolation Valve installation - Type and material - Joints and connections - Position and spacing / obstruction -fixing and supports in accordance with AS2419 | [6 empty] | Note number of units per floor attach photo Valve numbering
Valves Set Installation - Type and material - Finish - Make and model no. - Capacity/output - Joints and connections - Supports - Position - Accessories - Controls and electrical services -Signage, Labeling, Locks and Straps
Compliance Check 100mm around valve Handle Hydrant on 45 degree Couplin Bolts not impeding operation
Council Inspection Rough In
SECOND FIX - ZONE PRESSURE TEST AT TOP OF ZONE
Hydraulic Pressure Test AS2419 | [6 empty] | Hydrostatic pressure testing of 1700KPA for a 2 hour period as required in AS2419,S10.2.2. Oniste testing installation @ 1700KPA - Add photos - - PASS / FAIL/ NA - SIGN OFF
THIRD FIX - FINAL SIGN OFF
Signage, Locks and Straps
Asset register and Test Tag NO.
Block Plan Installation
Commissioning
As Built Complete

## Every Other Level
PREMIER FIRE - COAST - BC074
FIRE PROTECTION SERVICES – HYDRANT |  | ITP Prepared By: Troy Turner Project Manager |  |  |  |  | Persons Consulted In The Development: TT, CM, JP
QUALITY CONTROL CHECK LIST |  |  | Form: |  |  | REV:
Level: |  |  |  | Area:
Principal Activity: FIRE HYDRANT SYSTEM
Activity | Date | Premier Installer Check |  | Premier Design Check | Multiplex Sign | Client Sign | Comments
Initial Design
FIRST FIX - FLOOR HYDRANT
Pipework Fabrication
Delivery inspection
Fittings to Spec
Pipe and weld quality
Cut sheets and plans align with pipe delivered to site
Installation Inspection
Installed to approved drawing
Compliance with AS2419
Check Hydrant Landing Valves - Type and material - Joints and connections - Position and spacing / obstruction -fixing and supports in accordance with AS2419 | [6 empty] | Note number of units per floor attach photo
Check Hose Reel - Type and material - Joints and connections - Position and spacing / obstruction -fixing and supports in accordance with AS2419 | [6 empty] | Note number of units per floor attach photo
Isolation Valve installation - Type and material - Joints and connections - Position and spacing / obstruction -fixing and supports in accordance with AS2419 | [6 empty] | Note number of units per floor attach photo Valve numbering
Valves Set Installation - Type and material - Finish - Make and model no. - Capacity/output - Joints and connections - Supports - Position - Accessories - Controls and electrical services -Signage, Labeling, Locks and Straps
Compliance Check 100mm around valve Handle Hydrant on 45 degree Couplin Bolts not impeding operation
Council Inspection Rough In
SECOND FIX - FINAL SIGN OFF
Signage, Locks and Straps
Asset register and Test Tag NO.
Block Plan Installation
Commissioning
As Built Complete