## Project Checklist Templates
Id | Type | Name | Values | Prompting Name
f41b8df3-c072-4362-9137-1d18cd4dffe6 | checklist | Dry Fire System Installation ITP |  | Dry Fire System Installation ITP
5de5b069-803c-4906-8c34-69f5c1fdc21e | section | Installation Inspection
d51bb312-192e-47bc-a2d1-bd611628e792 | checkpoint | Area clear, tidy and accessible
e9a41ec7-08b9-4468-8b5d-a0c4dce6ef94 | checkpoint | Installed to approved drawing
7551f448-0420-5f7e-b969-75a61baceca3 | note | Compliance with AS1670, AS1668, BCA 2015
07804155-7085-57e0-92b2-db933c828cb4 | textbox | Drawing Document number and revision:
db8ce281-d7c3-497a-ab30-723ca7ddfe49 | checkpoint | Check Cabling
439b0b4c-1b1c-4bcd-9331-1c80fdcdadf4 | checkpoint | Conduits installed
24e6b1d8-ba89-431e-a4e5-5a00b563918d | section | Cabling Rough In
d0f25d18-146c-4d8d-b24d-06bc8b780050 | checkpoint | Cabling roughed into RCP and interface locations and Cable continuity checks have been conducted prior to ceiling sheeting.
fb7e870d-cfcc-4a35-93a8-c694cc9cc403 | checkpoint | Fire Rating completed prior to ceiling sheeting
76448c4b-a2fa-4b37-99b4-d474075dd5d5 | checkpoint | Are wires clearly drawn and submitted for AS BUILTS/AS CONSTRUCTED drawings
9cb7643b-3b3c-4756-aec7-96a371dfee5d | checkpoint | Riser Cable Tray Installation & cables fed
1dd33d18-835a-509c-b40f-116cc2ab414e | button | Fire rated cabling to floor LOOP, WIP, SPEAKER | Yes, No, N/A
961a2bbf-6421-51d7-9e3e-9b22254f0a16 | button | Cable supported to tray | Yes, No, N/A
a05f7480-de80-5f01-9037-63c96e2b05c1 | button | Cable connections | Yes, No, N/A
ae02779b-33cd-4a79-be05-ea387eaa68c1 | checkpoint | Fire rating of penetrations in riser
8ebb14bc-fbf3-44ea-9183-1eacd954ad49 | section | Final Fit Off
d29819fc-fd4b-4b7a-897a-8dc2ca1fe124 | checkpoint | Thermal and Smoke Detectors
e6493061-4ca1-4a77-b2b8-1ad9ed3c189e | checkpoint | Check Thermal and Smoke Detectors installed in accordance with AS1670, AS1668, BCA
c8f9245d-6ad0-51be-928c-016436af534a | button | Spacing, no paints / marks & fit for purpose | Yes,No,N/A
472ae419-0217-4847-a9a5-0614220470a8 | checkpoint | Check Speakers installed in accordance with AS1670, BCA
5dcdceda-904e-5922-b13a-a118a5954a61 | button | Spacing, no paints / marks & fit for purpose | Yes,No,N/A
91fbaaee-534b-4b64-b557-51222192e230 | checkpoint | WIP & ECP installed in accordance with AS1670, BCA
e1946b82-0624-5749-ad36-76e337b3eafa | button | Spacing, no paints / marks & fit for purpose | Yes,No,N/A
ec3c62b7-daff-46ec-acfa-70e054a0989d | checkpoint | Check Interfaces as noted above are installed in accordance with AS1670, AS1668, BCA
dcbadf85-7aac-5062-81a6-3f6d1c04ff50 | button | Fit for purpose | Yes,No,N/A
8755e4c6-d5b5-453a-be58-782d0a6a783e | checkpoint | Cabling Test to be conducted after fit off to confirm end of line resistance and/or loop continuity
b7f4bcaa-570b-4640-8b51-95a3993c2863 | checkpoint | Final Client Sign Off - All work completed as per ITP
4e2cba33-6efb-4f7e-aba2-d8476151878c | checklist | Fire Detection System Commissioning |  | Fire Detection System Commissioning
d446c8dc-6a8d-46c3-bd58-615b176cf689 | checkpoint | Area accessible & ready
804aeb86-c1bd-5881-8d30-4d54b1946285 | textbox | Drawing Document number and revision:
79186537-6902-4c78-a453-d94ebb37c06a | checkpoint | Floor inspect to confirm all system works are complete
63b1808a-885c-4f54-bd1d-bb4aa6f7fd17 | checkpoint | All faults and isolations cleared for area
c5172652-6519-472c-8445-bff03e8dca19 | checkpoint | Installation of only approved sample equipment which is fit for purpose
82a47118-54af-5a8d-9432-b8f679b0fa18 | note | Installed to approved drawing
6edcb82b-8984-5032-8b95-8476f1a34246 | note | Compliance with AS1670, AS1668, BCA 2015
86dace21-5428-4fb0-8127-5eacd4562bf1 | checkpoint | Joints, connections, terminations, separation of cables, Fixing, supports, position & spacing / obstruction correct
104046a2-5cf7-4235-ac2a-9851fa7eab2a | checkpoint | Signage & Labelling installed, block plans reviewed
e113d6cf-5fa2-4297-afd3-8eef5305d18b | checkpoint | Test Thermal and Smoke Detectors in accordance with AS1670, AS1668, BCA
f43ea9df-7272-4c8a-a999-09c3956618fa | checkpoint | Test Speakers/ Visual in accordance with AS1670, BCA
e3cf42b5-a250-4d07-96c8-4ddbc392c3cd | checkpoint | Test WIP & ECP in accordance with AS1670, BCA
c0b59251-4dd4-4860-aa07-0525c30d396b | checkpoint | Test all interfaces in accordance with AS1670, AS1668, BCA
d645487c-8ca9-5660-b800-82a190657ac3 | note | Interfaces to be tested: Sprinkler system, hydrant system, fire graphics, mech (fans/dampers/boards/MSSB), security, background music, prohibitive signage, vacuum waste, boom gates, BMS, IBAMS
ac8cae1a-c7c3-5094-b947-0eb4f4273cb3 | textbox | Number of devices tested
f0f253bf-2f88-5b98-a69f-e27542ad3cee | textbox | Number of Interface tested
6481c515-a288-4bff-a04d-de9af112bb3e | checkpoint | Emergency warning System.
10b0c3cf-5b35-526f-806f-b61d264d7cb2 | textbox | Max reading
ae17e9df-387f-57ec-9cf2-82da6227faec | textbox | Min Reading
8ec8ea1c-acc4-5d1c-a659-0b52f36a16d0 | textbox | WIP Reading
565b66fd-5046-43a9-9757-b0fa90b2c253 | checkpoint | ASE Commissioning
b17727b1-15be-46ce-8462-acfa5a91f52c | checkpoint | Final Client Sign Off - All work completed as per ITP
efdd6c8b-7005-4e8b-8df0-a6c3bdc38df2 | checklist | Sprinkler System Commissioning |  | Sprinkler System Commissioning
18165268-97ff-4099-be72-45b007be5bca | checkpoint | Floor inspect to confirm all system works are complete
d914be16-9869-43cc-888a-1eea0cd0d2ed | checkpoint | Installation of only approved sample equipment
e930a39b-3516-51c2-985c-e42e59e1eaa9 | note | Installed to approved drawing
532d9f83-29ad-5fc5-8b3d-4f742a3516dc | note | Compliance with AS2118
a056b2f9-77a0-58f4-b584-25be687b64e3 | textbox | Operating temperature (fast response, colour of liquid in bulb)
0137fe30-ae66-43dc-919d-a90be0e6387f | checkpoint | Escutcheon plates installed
08b2504a-84c1-440b-a7f5-1b9e5710c120 | checkpoint | Joints, connections,position & spacing / obstruction correct
58db82e2-1d35-4f22-ab59-841ecdd19da2 | checkpoint | Shields/guards provided (where specified)
6fa7c605-98b2-4d7a-a51e-6f6b5e52a39f | checkpoint | Fixings and supports in accordance with AS2118
b3c04d23-c76f-4072-9f21-930a029c9b86 | checkpoint | Sprinkler Support Systems are installed to not impede other services installed
c380083b-4a4a-4095-a94c-5b095a8d5e2d | checkpoint | Controls and electrical services
32c6b10d-f2f4-47b9-a883-219ad407f2be | checkpoint | Signage & Labelling, Locks & Straps installed, block plans reviewed
1a57d6e6-3365-43f5-ac47-13f3c1b6a2cf | checkpoint | Seismic Restraint & paint assessed
269e6ef1-5643-49ee-9cdd-10902276e34f | checkpoint | Check operation of isolation valve & FIP interface
6efd0759-4fac-4bc5-97d1-291ea2236d83 | checkpoint | Inspect and test gauge operation
6fca6ecb-2aff-4247-8aaa-f40ad1f03023 | checkpoint | Check operation of drain for sprinkler system
6cb7d86c-45c5-491c-9e50-3103b9de26a4 | checkpoint | Check operation of manual test drain confirm FSW activation to FIP
fac670f4-8564-4fc1-809b-389435aa3d9d | checkpoint | Check operation of solenoid test drain confirm FSW activation to FIP
bc0e4b19-0a83-4e09-ad9b-201bd9dd733e | checkpoint | Final Client Sign Off - All work completed as per ITP
fbb2ab35-12db-4d3e-9bf7-6a063ecb258a | checklist | Sprinkler System Installation ITP |  | Sprinkler System Installation ITP
f3c71b20-5930-48f6-82da-c288d979cd4c | section | First Fix
33c4d0ef-17c8-440a-920b-99cb9c82d0f6 | checkpoint | Area clear, tidy and accessible
9b1fa6d3-0be9-540d-9b84-86d5c1a87376 | textbox | Drawing Document number and revision:
4a6c5ee4-bc36-4193-adaa-932324f0ddb1 | checkpoint | Delivery inspection
b8e65acb-a27c-49fa-8222-a9cab34fe0d5 | checkpoint | Pipework to spec and approved sample
72e15332-856a-44e7-8cdb-e44c749365ea | checkpoint | Fittings to spec and approved sample, piping & weld quality reviewed
9661ec17-ee75-41c8-a319-e86aba7b677a | checkpoint | Cut sheets and plans align with pipe delivered to sit
a10289d4-6478-55c3-95b0-0c6a309e8d6c | note | Installation of only approved sample equipment
56c38e89-1df9-5a54-bec1-3fdea0ce5219 | note | Installed to approved drawing
bb003f0f-4171-5380-b4ad-909e06c316d2 | note | Compliance with AS2118
ed85c28b-df6f-4444-97a6-7362edc5a9a1 | checkpoint | Operating temperature (fast response, colour of liquid in bulb)
6d73c858-eff1-4ceb-82a4-ffe7d4defef8 | checkpoint | Joints, connections, supports, position & spacing / obstruction correct
fdfac899-a445-4de5-9bab-af8a3af2e2d5 | checkpoint | Shields/guards provided (where specified)
4c81dac8-e5e1-597a-819f-61d0f836eafe | note | Fixings and supports in accordance with AS2118
33f869b2-46ba-4cf9-82e5-41a7dd2f5df8 | checkpoint | Valves Set Installed as per approved sample
4d6456c7-9130-4771-9008-128662379564 | checkpoint | Joints, connections, supports and position correct - any accessories installed if required
788102e9-2d37-4b3b-b15e-3777a9454fac | checkpoint | Controls and electrical services
a53e0211-6743-467a-b9d8-4df7107eb593 | checkpoint | Signage, Labelling, Locks and straps
f6929950-e9b5-4292-90fd-0ea48bcae03c | checkpoint | Seismic Restraint Installed as per the design
4184bf23-9679-43d4-9c1d-83e78d3ab9d5 | checkpoint | Painting of exposed Pipework
93bd415b-9f5f-489b-b6f6-365908137102 | section | Second Fix
83daf3a4-b3da-4ec2-a514-82c5ae6d3a69 | checkpoint | Check Sprinkler Heads
404f4871-c74c-5364-a2b7-8248437f1a0e | textbox | Type and material
2bf44338-838b-5df9-90f3-6b663135803e | textbox | Operating temperature (fast response, colour of liquid in bulb)
fc97af1a-a669-4c6f-9c2f-30eb94b2cba5 | checkpoint | Joints, connections, supports, position & spacing / obstruction correct
3a04857d-566b-465e-b545-c3d9ef0b0dac | checkpoint | Shields/guards provided (where specified)
3a0ddb58-81f2-4054-83f2-2da68e55ab8d | checkpoint | Escutcheon plates added
ee5386a1-c199-4de8-8eeb-7132414c4e77 | checkpoint | Sprinkler Support Systems are installed to not impede other services installed
af95b747-dcaf-57f2-9aa4-1e3cc4a11a54 | note | Installed to approved drawing
293c9e4d-5949-5a08-b7ca-b14f9a2926c9 | note | Compliance with AS2118
b5c01f6c-c91a-4c48-bd06-683d6788f1c1 | checkpoint | Seismic Restraint Installed as per the design
ff979bac-d4e4-4a79-bf89-68d87034e40e | checkpoint | Fire Rating completed prior to ceiling sheeting
45aeb8bc-2033-4a42-af36-906f7ff2f1d5 | checkpoint | Sprinkler heads have been installed straight prior to ceiling sheeting PFS advise any heads found not straight will not be at our expense to rectify - please take photos
420ae990-4eb9-421e-b2d8-bf28501c0dc6 | section | Final Fit Off
cd631276-5511-4ff8-bcf0-75fddddcd767 | checkpoint | Check Sprinkler Heads
6aa56402-fc6a-5fb8-baaf-f7238d2b4cbf | textbox | Type and material
7c60e1bd-33a4-42e3-a46f-ebf329966387 | checkpoint | Operating temperature (fast response, colour of liquid in bulb)
061c653f-f355-4e0a-98e1-8a178d2d778a | checkpoint | Joints, connections, supports, position & spacing / obstruction correct
0ad25c9e-cf67-4975-9f07-b94241e91fb1 | checkpoint | Shields/guards provided (where specified)
58ce73e7-89c2-43cd-b8af-32231d7d3402 | checkpoint | Escutcheon plates added
f4008a00-8984-583d-9ed9-d211120ad0f4 | note | Installed to approved drawing
e853bb29-cf04-571d-9be2-cc74ed8a21f2 | note | Compliance with AS2118
38e7e4e7-ad8a-4f68-b4b9-55c3e71f3db0 | section | Hydraulic Pressure Test
ab3f66e4-1448-4262-a625-1168dd4f6230 | checkpoint | 1600 kPa or 400 kPa in excess of the maximum static working pressure, whichever is greater, for a period of not less than 2 hours
b735ed22-40bf-588a-b074-287888b9d9b0 | textbox | Start Time:
7dde926a-0a04-59ac-85e7-d4c947e4022c | textbox | Pressure:
8aa658fd-5a32-490f-8d02-54fa75ad457b | checkpoint | Attach picture of pressure test gauge:
c964e201-e038-57e4-98a0-bfa6eb7a7ee1 | textbox | Finish Time:
e8522d6f-a7d7-5978-9d2c-b8f0445d2b29 | textbox | Pressure:
4347998a-59d3-46b9-b4b7-2975914796de | checkpoint | Final Client Sign Off - All work completed as per ITP
d29772d7-5542-4a50-a16c-70e852fb575e | checklist | Sprinkler System Installation ITP (OLD) |  | Sprinkler System Installation ITP
5c5eb496-e388-49d0-a7ab-64f6841a0730 | section | First Fix
63e0e11d-1d0e-48a1-b53e-490207f72738 | checkpoint | Area clear, tidy and accessible
93c2c091-9a0e-509b-9b06-150edffdb872 | textbox | Drawing Document number and revision:
e3e7cca0-9966-4e3e-87f9-3ef9483fcadd | checkpoint | Delivery inspection
276bceee-448b-41c8-95cf-57d3b2334129 | checkpoint | Pipework to spec and approved sample
601c2542-44ce-434c-b564-f10e5c05dd26 | checkpoint | Fittings to spec and approved sample, piping & weld quality reviewed
daf5a521-40a1-440e-9484-0ddd23a9a53b | checkpoint | Cut sheets and plans align with pipe delivered to sit
17c7a3a0-9c02-591b-a158-7af7dec527e9 | note | Installation of only approved sample equipment
9e77959b-371c-5f51-8515-82bb19a5b28b | note | Installed to approved drawing
2833dcd1-fbb0-57b0-a845-6444c6b7b101 | note | Compliance with AS2118
5697f24c-1f3f-4a8f-bb9b-eaf4306d62e1 | checkpoint | Operating temperature (fast response, colour of liquid in bulb)
44a891ed-e3fc-41a7-88cb-89a01c294394 | checkpoint | Joints, connections, supports, position & spacing / obstruction correct
8d7a174f-2f3a-41e4-ab15-7111cfee4a89 | checkpoint | Shields/guards provided (where specified)
e5d41d87-fe48-5b13-aeef-b49004846ff0 | note | Fixings and supports in accordance with AS2118
d288ca10-593e-4020-b2a7-6fa7e0def96c | checkpoint | Valves Set Installed as per approved sample
9c12c3df-a9d7-407f-a37b-bade20cfb846 | checkpoint | Joints, connections, supports and position correct - any accessories installed if required
581e5c67-b7ab-43f5-96bf-c63f7df12d15 | checkpoint | Controls and electrical services
b0c63e74-2ca9-4b07-a883-31957ec46d4c | checkpoint | Signage, Labelling, Locks and straps
b1db0d10-2a17-4f84-bcb5-f6a79f852cce | checkpoint | Seismic Restraint Installed as per the design
f4af38d7-9f5c-4380-b46d-ee2fb597789f | checkpoint | Painting of exposed Pipework
8fef757b-90af-45e8-9ea4-a63ac4b7a9a0 | section | Second Fix
0763cafd-2c06-4b19-95c1-3500379b435f | checkpoint | Check Sprinkler Heads
9eaac0f3-f910-5bda-b507-8cb1a4127553 | textbox | Type and material
5415829f-2703-5cda-a45c-0d979d86674f | textbox | Operating temperature (fast response, colour of liquid in bulb)
971fd59f-7ae7-4d65-a017-63ef3e314a69 | checkpoint | Joints, connections, supports, position & spacing / obstruction correct
0fd89131-a35e-4d2b-b5e2-6fa2c4e2db0e | checkpoint | Shields/guards provided (where specified)
c3d8d96c-15c7-4fa9-a86b-4d1219ee3252 | checkpoint | Escutcheon plates added
82600a06-1456-46d2-a393-5bab7e446029 | checkpoint | Sprinkler Support Systems are installed to not impede other services installed
0da264eb-724a-513a-a3d4-8576c31bb897 | note | Installed to approved drawing
948e61a8-1ff8-54e8-9cd0-83dbe03756aa | note | Compliance with AS2118
71b1ae35-7fa5-46a0-9562-5d9728e1fc3e | checkpoint | Seismic Restraint Installed as per the design
b44a0890-1a67-424e-98ea-72492f724101 | checkpoint | Fire Rating completed prior to ceiling sheeting
190254a7-d4c6-4528-923a-229059c9f876 | checkpoint | Sprinkler heads have been installed straight prior to ceiling sheeting PFS advise any heads found not straight will not be at our expense to rectify - please take photos
938a217b-38d6-4ae3-90cc-fa674281fcd2 | section | Final Fit Off
188dcc85-2e01-456b-815c-2c86aa08d039 | checkpoint | Check Sprinkler Heads
0bf01102-164f-5b6b-8647-779f2091e01a | textbox | Type and material
567b4be1-a5d7-4060-86bc-aca27a2f2692 | checkpoint | Operating temperature (fast response, colour of liquid in bulb)
8c8e97bc-9d9a-4bb8-b7a0-1f0dde581d7e | checkpoint | Joints, connections, supports, position & spacing / obstruction correct
2cbc80e9-fe4e-4273-a2ba-50b6983d6728 | checkpoint | Shields/guards provided (where specified)
5809206d-3793-4327-a58b-1e99a60775da | checkpoint | Escutcheon plates added
8daf0db2-d596-5fe2-bcc0-236e1cda98e8 | note | Installed to approved drawing
1cab930d-141b-5a40-aa0c-2d6ad8237d46 | note | Compliance with AS2118
ec53327c-d00d-4808-b282-8d89af37d3aa | section | Hydraulic Pressure Test
1ecb52c2-ab5d-45b9-94d4-538e21714c2c | checkpoint | 1.4MPa or 1400kpa in excess of the maximum static working pressure (whichever is greater) for a period of 2 hours)
9d893189-f63c-52b7-9854-705725302f0a | textbox | Start Time:
892d6a52-cc26-51e9-af69-9bcbbcd910a7 | textbox | Pressure:
d299033e-de31-4053-8ba8-92e622424ace | checkpoint | Attach picture of pressure test gauge:
eede0a1c-6aab-5fee-8d2f-865585d236b8 | textbox | Finish Time:
e7d4ba2a-7d2d-5c3d-82f5-f887fbf9dd02 | textbox | Pressure:
a2e1091d-42aa-41ee-a8fb-869ee5cc2142 | checkpoint | Final Client Sign Off - All work completed as per ITP