## zres_siteapp_NEW
Id | Type | Name | Values | Prompting Name | Postfix | Resource Id
de22cee4-995f-4441-b470-f43beee5a193 | checklist | Hydrant ITP |  | Wet fire – Hydrants
8a8712af-bc89-443d-9ced-6164e114bd38 | section | First Fix - Floor Hydrant
0e635a6d-2058-4a43-83c6-e9105e275ccd | checkpoint | Pipework Fabrication
4d944f32-cee9-54ca-a7b4-1517b7eea257 | note | Delivery inspection
56fe4978-fc5a-58b6-af25-33809d5a8db9 | note | Fittings to Spec
55b5d277-8193-5e4a-a0bb-fa98b8400b1c | note | Pipe and weld quality
ab96d01b-4feb-5acd-8cbc-742bc9b549ce | note | Cut sheets and plans align with pipe delivered to site
4e8b6fb4-4a4f-4e38-8c5e-a5568d6e5e93 | checkpoint | Installation Inspection
256cf654-f6eb-565b-bb17-dbe2f54107c8 | note | Installed to approved drawing
b9cdfb0f-49f9-5f67-88e3-e7b830e28a69 | note | Compliance with AS2419
b737fca9-e58f-40c9-86e6-0daeb695fe22 | checkpoint | Check Hydrant Landing Valves
8037552a-3463-5160-9788-9e290b0fd4cd | note | – Type and material
1c9a4014-c460-51b0-9bba-c80fbda6f911 | note | – Joints and connections
1286cd12-0248-5bf0-9bad-b163048ee979 | note | – Position and spacing / obstruction
5fca279a-fad1-543c-a000-6ecf9ce80316 | note | – Fixing and supports in accordance with AS2419
3b4ff582-3f7e-52c0-b95b-15f2c9000138 | note | Note number of units per floor attach photo
3c2e60b3-0115-4b91-b156-16cebb4d2aa8 | checkpoint | Check Hose Reel
427f1771-efcf-5d5c-a7fe-1ca43bfb4988 | note | – Type and material
3b462fb0-6efd-5c45-9283-f86c166e17c1 | note | – Joints and connections
8f99c41c-dda4-5799-9bfa-2508111efc16 | note | – Position and spacing / obstruction
b2e2b3c9-3b05-5ebc-b3fb-09b8c1a5e8d9 | note | – Fixing and supports in accordance with AS2419
065c912f-1d94-5218-8144-1d8387b25177 | note | Note number of units per floor attach photo
c0a38290-a387-4690-9f40-78f5b57833ef | checkpoint | Isolation Valve installation
7cf5bd88-9645-5a96-882d-81678074ce27 | note | – Type and material
b702080d-8eea-5bd7-aaad-b98fb10337fa | note | – Joints and connections
17dd0141-5d13-51d6-a64e-bf1a3d605d67 | note | – Position and spacing / obstruction
ae8e8382-4f2f-5bb4-af1f-fb7f02978ba2 | note | – Fixing and supports in accordance with AS2419
5ba4cede-158e-50d9-8a12-6ec4908ee07e | note | Note number of units per floor attach photo
7b78d106-f390-5ad9-89cb-e8e11527b123 | note | Valve numbering
bfe5d462-00c0-473a-8a9d-06e056aa9ab4 | checkpoint | Valves Set Installation
4a3a53e1-3f9e-59dd-8c67-127f1272e9c8 | note | – Type and material
263de852-d527-526c-ade7-709178244815 | note | – Finish
d3395774-de01-57a4-9afd-9c9c246448b3 | note | – Make and model no.
3cdf4989-f236-5504-9487-7499a8c0547f | note | – Capacity/output
8f90930e-1412-59a9-b1c0-09789395a570 | note | – Joints and connections
7c5e6022-8e4e-5b2d-aa3a-1b2a1db7f1f2 | note | – Supports
6fc14f3d-ee82-5bca-bfdc-7f5d1ae9fa8f | note | – Position
cc3ccac1-4555-52bd-8172-0fc5650d8767 | note | – Accessories
b1becd3f-fac9-5ced-9c71-9f5f49aa2aea | note | – Controls and electrical services
10bbf383-6953-52dc-b713-e5b4033d253b | note | – Signage, Labeling, Locks and Straps
8ff80756-208b-40d6-b6f7-9513b42e3a20 | checkpoint | Compliance Check
801df30c-4f70-5379-9974-c9ea60f18d76 | note | 100mm around valve Handle
c4c93741-f5f0-5cbe-ab4f-517b6dadf7e1 | note | Hydrant on 45 degree
2d1bc8b6-00ac-51f5-9681-ac5f7ee5f5bd | note | Couplin Bolts not impeding operation
14f5d9c0-3de5-4ffb-afa4-aea417c862b2 | checkpoint | Council Inspection Rough In
87e6c785-d553-417c-b42b-03a9b056dcba | section | Second Fix - Final Sign Off
f8385064-c3cb-4cca-b17e-d41ca24f5649 | checkpoint | Signage, Locks and Straps
661efd5b-3fe6-4ce1-9e96-9a2d9ab45a11 | checkpoint | Asset register and Test Tag NO.
b0077433-5fc8-4115-97ff-39b6b3ee8998 | checkpoint | Block Plan Installation
d8d5e0c5-c27d-4972-808a-fff3f3db074e | checkpoint | Commissioning
856701c3-ef2b-4857-a4d7-89d457a9a4b8 | checkpoint | As Built Complete
ce5579ba-4fbd-44a4-9a31-0b69585e5cd6 | checklist | Hydrant ITP (Specific Levels) |  | Wet fire – Hydrants
83a57b76-3d65-4931-8894-3fea0e448237 | section | First Fix - Floor Hydrant
7073d5a5-b345-4bf6-8177-c8b745e1b70b | checkpoint | Pipework Fabrication
077c0e30-d83a-5b34-bb45-98641df945e7 | note | Delivery inspection
14a6c278-c2f3-5445-abcd-2fd128b7ac5e | note | Fittings to Spec
4d4a61ac-d869-5ac2-8cf1-843f4f0efd84 | note | Pipe and weld quality
f006a226-6b1f-5954-b98b-a8e4d034f809 | note | Cut sheets and plans align with pipe delivered to site
be6d4b17-dca5-4308-b385-14b9ad08ec8c | checkpoint | Installation Inspection
3b83936c-a23a-53da-a630-b1bacc9f0033 | note | Installed to approved drawing
03912498-7c18-5834-8853-71c828423448 | note | Compliance with AS2419
4c1ed2e9-dfb2-4e53-9fb1-6f45efb649cc | checkpoint | Check Hydrant Landing Valves
5467cc79-566a-50b4-881d-287eac783811 | note | – Type and material
20180542-a6cd-516a-bea6-a8349fb0e5e4 | note | – Joints and connections
2c422694-b596-5f12-bb18-4f592209766d | note | – Position and spacing / obstruction
f4069747-80c8-5a89-8012-6898d9d0d550 | note | – Fixing and supports in accordance with AS2419
78bbae37-f156-5a7b-aa03-74fa7da6dc36 | note | Note number of units per floor attach photo
54385082-a1bf-4d08-b700-b7f8301e498a | checkpoint | Check Hose Reel
eca62e8f-d7ea-5baa-91e1-645a6b23c5d5 | note | – Type and material
f438fcce-1138-55b5-9521-be29c065c088 | note | – Joints and connections
4029994c-add7-580d-9aec-a6fda9ab8fb7 | note | – Position and spacing / obstruction
fa773792-b0c7-5c3d-8601-3cfbd095f1e2 | note | – Fixing and supports in accordance with AS2419
dd1fcca5-e9b3-535d-a161-d8e450bacbea | note | Note number of units per floor attach photo
85b17ab0-b4ef-449d-8646-c1c72cba9332 | checkpoint | Isolation Valve installation
09399d3f-dc6d-5372-a4c7-fdcd233be156 | note | – Type and material
12e197ff-fc1b-57a3-8870-28de2f66e403 | note | – Joints and connections
d35f97cf-ed3d-5824-920d-777adb1b942b | note | – Position and spacing / obstruction
474978fd-a644-5fe2-8ccf-c10f22323a93 | note | – Fixing and supports in accordance with AS2419
7f21597a-f037-51f3-ba65-5d9a141e1bf6 | note | Note number of units per floor attach photo
710309e8-af5a-5b10-a09e-e55ee98fc9d0 | note | Valve numbering
7f947e1b-f1d7-46d1-b338-80b23749bfff | checkpoint | Valves Set Installation
4c1e6448-2e24-5807-87a9-ff08f9969559 | note | – Type and material
dff8ead1-ec4d-57e6-9f00-a75fb751b6fc | note | – Finish
0d48c89d-74fe-5f41-9175-d47ba39e635f | note | – Make and model no.
773302c1-0839-52dc-9b8f-8b7c07ae3db9 | note | – Capacity/output
0efb2f50-dfd3-518d-9498-d57caed0b975 | note | – Joints and connections
b0d42ad2-43f4-501b-8b3a-b700235306ff | note | – Supports
d54fb0c8-6cc7-54f8-9749-0d5bf18b603f | note | – Position
83d5bb77-1cbc-5215-981b-9cb2d8b3aabf | note | – Accessories
649825d9-e10d-5db0-b92e-40dd197f157c | note | – Controls and electrical services
8c5c3e84-d05d-567d-aedf-11d75d2ad3f3 | note | – Signage, Labeling, Locks and Straps
d9e09e61-158c-44b0-b664-7f790a8a2a6b | checkpoint | Compliance Check
26e43eab-bdbf-53bd-aea4-ac74fd0bb621 | note | 100mm around valve Handle
2fd71af1-c870-53b6-95db-62e785baaaa0 | note | Hydrant on 45 degree
69dcb844-2314-59a8-aa36-d2c380fb7bb3 | note | Couplin Bolts not impeding operation
4f451fdf-27c8-4430-9d13-069358a8bb84 | checkpoint | Council Inspection Rough In
97edd52f-dcff-40b3-9320-d0e49fd5de47 | section | Second Fix - Zone Pressure Test at top of zone
66620055-2841-4c8c-8b08-34b91ed53d07 | checkpoint | Pipework Fabrication
2850bff5-d660-563d-9bab-44431974e9dc | note | Delivery inspection
6fe95979-e290-54a6-8e64-42bd5b9f2893 | note | Fittings to Spec
f5f346f7-a8fe-5e89-b5ac-ccebe36a7ce0 | note | Pipe and weld quality
1f9ae2bc-e37e-5b82-bb01-6347f4dd2cbf | note | Cut sheets and plans align with pipe delivered to site
96965578-f82f-4221-a919-5b037042f7bb | checkpoint | Hydraulic Pressure Test AS2419
57808ee0-b150-599f-8d21-e5491bd05c22 | note | Hydrostatic pressure testing of 1700KPA for a 2 hour period as required in AS2419,S10.2.2. Oniste testing installation @ 1700KPA
fa16eb22-6c9f-5038-a45d-7b4313d94266 | note | Add photos
b01ca210-2919-4c0c-b44b-970872c8646b | signoff | SIGN OFF
f1ccc662-5e70-4687-9d92-6257f0cf4ecb | section | Third Fix - Final Sign Off
b636551f-7d00-43bb-ba3e-3452a4938c51 | checkpoint | Signage, Locks and Straps
f7731713-3747-4178-bc98-23a4998217ed | checkpoint | Asset register and Test Tag NO.
8156d421-35a3-4855-a3fa-eafb9b63d3e4 | checkpoint | Block Plan Installation
6775cf35-2586-4df3-9164-6a948727af04 | checkpoint | Commissioning
1b94dc0b-40bc-467a-be00-20001fbb17b1 | checkpoint | As Built Complete