## Project Structure
Folder Structure |  | Ref | Equipment |  | Checklists
Site QA
Design and Equipment
|  | Design |  |  | 6.2 Design and Documentation
|  | Equipment |  |  | 6.3 Equipment Selection Checklist
Level 5 - Patient Rooms and General Spaces
FCU L5.01
|  |  | FCU |  | 6.20 Fan Coil Unit Installation Checklist
|  |  | Ductwork |  | 6.6 Ductwork Installation Checklist
FCU L5.02
|  |  | FCU |  | 6.20 Fan Coil Unit Installation Checklist
|  |  | Ductwork |  | 6.6 Ductwork Installation Checklist
FCU L5.03
|  |  | FCU |  | 6.20 Fan Coil Unit Installation Checklist
|  |  | Ductwork |  | 6.6 Ductwork Installation Checklist
FCU L5.04
|  |  | FCU |  | 6.20 Fan Coil Unit Installation Checklist
|  |  | Ductwork |  | 6.6 Ductwork Installation Checklist
FCU L5.05
|  |  | FCU |  | 6.20 Fan Coil Unit Installation Checklist
|  |  | Ductwork |  | 6.6 Ductwork Installation Checklist
FCU L5.06
|  |  | FCU |  | 6.20 Fan Coil Unit Installation Checklist
|  |  | Ductwork |  | 6.6 Ductwork Installation Checklist
FCU L5.07
|  |  | FCU |  | 6.20 Fan Coil Unit Installation Checklist
|  |  | Ductwork |  | 6.6 Ductwork Installation Checklist
FCU L5.08
|  |  | FCU |  | 6.20 Fan Coil Unit Installation Checklist
|  |  | Ductwork |  | 6.6 Ductwork Installation Checklist
FCU L5.09
|  |  | FCU |  | 6.20 Fan Coil Unit Installation Checklist
|  |  | Ductwork |  | 6.6 Ductwork Installation Checklist
FCU L5.10
|  |  | FCU |  | 6.20 Fan Coil Unit Installation Checklist
|  |  | Ductwork |  | 6.6 Ductwork Installation Checklist
FCU L5.11
|  |  | FCU |  | 6.20 Fan Coil Unit Installation Checklist
|  |  | Ductwork |  | 6.6 Ductwork Installation Checklist
FCU L5.12
|  |  | FCU |  | 6.20 Fan Coil Unit Installation Checklist
|  |  | Ductwork |  | 6.6 Ductwork Installation Checklist
|  |  | Filters |  | 6.32 Filters Checklist
FCU L5.13
|  |  | FCU |  | 6.20 Fan Coil Unit Installation Checklist
|  |  | Ductwork |  | 6.6 Ductwork Installation Checklist
FCU L5.14
|  |  | FCU |  | 6.20 Fan Coil Unit Installation Checklist
|  |  | Ductwork |  | 6.6 Ductwork Installation Checklist
BEF L5.01
|  |  | Fan |  | 6.25 Fan Installation Checklist
|  |  | Ductwork |  | 6.6 Ductwork Installation Checklist
REF L5.01
|  |  | Fan |  | 6.25 Fan Installation Checklist
|  |  | Ductwork |  | 6.6 Ductwork Installation Checklist
REF L5.02
|  |  | Fan |  | 6.25 Fan Installation Checklist
|  |  | Ductwork |  | 6.6 Ductwork Installation Checklist
Fire / Smoke Dampers
|  |  | Test Certificates |  | Document Attachment
MFSD-L5.04
|  |  |  | Fire Penetration Register | 6.7.1 Fire Penetration Register
|  |  |  | Fire / Smoke Damper | 6.7.2 Fire / Smoke Damper Installation Checklist
MFSD-L5.05
|  |  |  | Fire Penetration Register | 6.7.1 Fire Penetration Register
|  |  |  | Fire / Smoke Damper | 6.7.2 Fire / Smoke Damper Installation Checklist
MFSD-L5.06
|  |  |  | Fire Penetration Register | 6.7.1 Fire Penetration Register
|  |  |  | Fire / Smoke Damper | 6.7.2 Fire / Smoke Damper Installation Checklist
MFSD-L5.07
|  |  |  | Fire Penetration Register | 6.7.1 Fire Penetration Register
|  |  |  | Fire / Smoke Damper | 6.7.2 Fire / Smoke Damper Installation Checklist
MFSD-L5.08
|  |  |  | Fire Penetration Register | 6.7.1 Fire Penetration Register
|  |  |  | Fire / Smoke Damper | 6.7.2 Fire / Smoke Damper Installation Checklist
MFSD-L5.09
|  |  |  | Fire Penetration Register | 6.7.1 Fire Penetration Register
|  |  |  | Fire / Smoke Damper | 6.7.2 Fire / Smoke Damper Installation Checklist
MFSD-L5.10
|  |  |  | Fire Penetration Register | 6.7.1 Fire Penetration Register
|  |  |  | Fire / Smoke Damper | 6.7.2 Fire / Smoke Damper Installation Checklist
MFSD-L5.11
|  |  |  | Fire Penetration Register | 6.7.1 Fire Penetration Register
|  |  |  | Fire / Smoke Damper | 6.7.2 Fire / Smoke Damper Installation Checklist
MFSD-L5.12
|  |  |  | Fire Penetration Register | 6.7.1 Fire Penetration Register
|  |  |  | Fire / Smoke Damper | 6.7.2 Fire / Smoke Damper Installation Checklist
MFSD-L5.13
|  |  |  | Fire Penetration Register | 6.7.1 Fire Penetration Register
|  |  |  | Fire / Smoke Damper | 6.7.2 Fire / Smoke Damper Installation Checklist
MFSD-L5.14
|  |  |  | Fire Penetration Register | 6.7.1 Fire Penetration Register
|  |  |  | Fire / Smoke Damper | 6.7.2 Fire / Smoke Damper Installation Checklist
MFSD-L5.15
|  |  |  | Fire Penetration Register | 6.7.1 Fire Penetration Register
|  |  |  | Fire / Smoke Damper | 6.7.2 Fire / Smoke Damper Installation Checklist
FD-L5.01
|  |  |  | Fire Penetration Register | 6.7.1 Fire Penetration Register
|  |  |  | Fire / Smoke Damper | 6.7.2 Fire / Smoke Damper Installation Checklist
FDD-L5.02
|  |  |  | Fire Penetration Register | 6.7.1 Fire Penetration Register
|  |  |  | Fire / Smoke Damper | 6.7.2 Fire / Smoke Damper Installation Checklist
Pipework
|  |  | Water Pipe |  | 6.9 Water Pipework Installation Checklist
|  |  | Pressure Pipe |  | 6.10 Pipe Pressure Test Report Checklist
|  | Electrical |  |  | 6.8 Electrical Installation
|  | Controls |  |  | 6.11 Controls / BMS Installation
Level 5 - Theatres
|  | OT1 |  |  | 6.6 Ductwork Installation Checklist
Setup 1
|  |  | Ductwork |  | 6.6 Ductwork Installation Checklist
|  |  | Filters |  | 6.32 Filters Checklist
|  |  | CAV L5.01 |  | 6.33 VAV Unit Installation Checklist
|  | OT2 |  |  | 6.6 Ductwork Installation Checklist
Setup 2
|  |  | Ductwork |  | 6.6 Ductwork Installation Checklist
|  |  | Filters |  | 6.32 Filters Checklist
|  |  | CAV L5.02 |  | 6.33 VAV Unit Installation Checklist
|  | OT3 |  |  | 6.6 Ductwork Installation Checklist
Setup 3
|  |  | Ductwork |  | 6.6 Ductwork Installation Checklist
|  |  | Filters |  | 6.32 Filters Checklist
|  |  | CAV L5.02 |  | 6.33 VAV Unit Installation Checklist
|  | OT4 |  |  | 6.6 Ductwork Installation Checklist
Setup 4
|  |  | Ductwork |  | 6.6 Ductwork Installation Checklist
|  |  | Filters |  | 6.32 Filters Checklist
|  |  | CAV L5.02 |  | 6.33 VAV Unit Installation Checklist
Pipework
|  |  | Water Pipework |  | 6.9 Water Pipework Installation Checklist
|  |  | Pipe Pressure |  | 6.10 Pipe Pressure Test Report Checklist
|  | Controls |  |  | 6.11 Controls / BMS Installation
Level 6 Plant Room and Roof
AHU L6.01
|  |  | AHU |  | 6.23 AHU Installation Checklist
|  |  | Ductwork |  | 6.6 Ductwork Installation Checklist
|  |  | Filters |  | 6.32 Filters Checklist
RAF L6.01
|  |  | Fan |  | 6.25 Fan Installation Checklist
|  |  | Ductwork |  | 6.6 Ductwork Installation Checklist
|  |  | VSD |  | 6.37 Variable Speed Drive Checklist
|  |  | Filters |  | 6.32 Filters Checklist
AHU L6.02
|  |  | AHU |  | 6.23 AHU Installation Checklist
|  |  | Ductwork |  | 6.6 Ductwork Installation Checklist
|  |  | Filters |  | 6.32 Filters Checklist
RAF L6.02
|  |  | Fan |  | 6.25 Fan Installation Checklist
|  |  | Ductwork |  | 6.6 Ductwork Installation Checklist
|  |  | VSD |  | 6.37 Variable Speed Drive Checklist
|  |  | Filters |  | 6.32 Filters Checklist
AHU L6.03
|  |  | AHU |  | 6.23 AHU Installation Checklist
|  |  | Ductwork |  | 6.6 Ductwork Installation Checklist
|  |  | Filters |  | 6.32 Filters Checklist
RAF L6.03
|  |  | Fan |  | 6.25 Fan Installation Checklist
|  |  | Ductwork |  | 6.6 Ductwork Installation Checklist
|  |  | VSD |  | 6.37 Variable Speed Drive Checklist
|  |  | Filters |  | 6.32 Filters Checklist
AHU L6.04
|  |  | AHU |  | 6.23 AHU Installation Checklist
|  |  | Ductwork |  | 6.6 Ductwork Installation Checklist
|  |  | Filters |  | 6.32 Filters Checklist
RAF L6.04
|  |  | Fan |  | 6.25 Fan Installation Checklist
|  |  | Ductwork |  | 6.6 Ductwork Installation Checklist
|  |  | VSD |  | 6.37 Variable Speed Drive Checklist
|  |  | Filters |  | 6.32 Filters Checklist
L5 OA Duct
|  |  | Ductwork |  | 6.6 Ductwork Installation Checklist
Pipework
|  |  | Water Pipework |  | 6.9 Water Pipework Installation Checklist
|  |  | Pipe Pressure |  | 6.10 Pipe Pressure Test Report Checklist
|  | Electrical |  |  | 6.8 Electrical Installation
|  | Controls |  |  | 6.11 Controls / BMS Installation
Commissioning / Handover
|  | Pre |  |  | 6.43 Pre Commissioning Checklist
|  | Commissioning |  |  | 6.44 Commissioning Checklist
|  | Handover |  |  | 6.45 Handover Checklist

## Checklists
type | name | values
checklist-flat | 6.2 Design and Documentation
checkpoint | Client brief and scope of works received
checkpoint | All client documents the latest issue per contract
checkpoint | Confirmation of building fabric and glazing received
checkpoint | Confirmation of all design parameters received
checkpoint | Cooling and heating loads complete
checkpoint | Ventilation systems calculations complete
checkpoint | Shop drawings complete
checkpoint | Shop drawings approved by client
checkpoint | Electrical shop drawings complete
checkpoint | Electrical drawings approved by client
checkpoint | BMS FD and tech submission complete
checkpoint | BMS FD and tech submission approved by client
checkpoint | Design certification issued and attached
checklist-flat | 6.3 Equipment Selection Checklist
checkpoint | System flow rate checks completed
checkpoint | System static calculations complete
checkpoint | Equipment selections comply with contract
checkpoint | Equipment schedules prepared
checkpoint | Equipment interfaces to other services correct
checkpoint | Equipment issued to and approved by client
checklist-flat | 6.4 Supplier / Subcontractor Order Checklist
checkpoint | Attach any relevant photos or documents
select | Offer based on latest specification | Yes, No, N/A
select | Offer based on latest drawings and schedules | Yes, No, N/A
select | Offer complies with all statutory requirements | Yes, No, N/A
select | Offer includes all contract insurance requirements | Yes, No, N/A
select | Offer includes delivery to site | Yes, No, N/A
select | Offer includes warranty requirements as per contract | Yes, No, N/A
select | Offer includes maintenance requirements as per contract | Yes, No, N/A
select | Offer includes O&M manual requirements as per contract | Yes, No, N/A
select | Offer includes QA requirements | Yes, No, N/A
select | Offer includes testing and commissioning | Yes, No, N/A
select | Offer includes site safety requirements | Yes, No, N/A
select | Offer includes materials handling | Yes, No, N/A
select | Offer includes EWPs, Boom Lifts etc | Yes, No, N/A
select | Offer includes provision of samples | Yes, No, N/A
select | Offer includes all certification required | Yes, No, N/A
select | Offer inclusions / exclusions accepted | Yes, No, N/A
checkpoint | Purchase order issued
checklist-flat | 6.6 Ductwork Installation Checklist
checkpoint | Area ready and accessible for work
checkpoint | Size, position & height checked against drawing
checkpoint | Spigots installed and left open
checkpoint | Joints completed and correct method used
checkpoint | Stiffening checked
checkpoint | Correct joint sealant used
checkpoint | Hangers (including booker rod cut back) checked
checkpoint | Flexible connections to equipment sealed and aligned
checkpoint | Flexible ductwork installed and correctly supported
checkpoint | Fire rating correct and complete
checkpoint | Access panels installed as per drawings and closed
checkpoint | VCD’s & MVCD’s open & marked
checkpoint | Internal insulation correct type, thickness, extent and complete
checkpoint | External insulation correct type, thickness, extent and complete
checkpoint | Kitchen exhaust duct graded towards hoods and drains
checkpoint | Kitchen exhaust duct installed with access panels (every 3 meters & change in direction) and drains
checkpoint | Ductwork exposed to weather has joints capped
checkpoint | Ductwork exposed to weather has top of duct cross broken or is installed to allow water run off.
checkpoint | Equipment connections exposed to weather capped connections weather proofed (flashings)
checkpoint | Grilles installed
checkpoint | Roof discharges / intakes secured and weather proofed
checklist-flat | 6.7.1 Fire Penetration Register
checkpoint | Fire installation details (pass once details entered)
text | Item no
text | Level
text | Grid ref
text | Penetration detail
text | Penetration construction
text | Penetration thickness (mm)
text | Size (W x H mm)
text | Integrity (FRL)
text | Service
text | System description
label | Upload photographs below
checkpoint | Manufacture details - pass once details entered
text | DTS/test report/certificate reference
checkpoint | Installation checklist - pass once details entered
checklist | 6.7.2 Fire / Smoke Damper Installation Checklist
checkpoint | Opening in fire rated construction built correctly
select | Fire damper orientation | Vertical ,Horizontal
select | Damper type | Curtain , Drop lock, Motorised, Intumescent, Smoke
checkpoint | Does the structure match that for which damper was tested
checkpoint | Check damper orientation (i.e. upside down or not)
checkpoint | Damper airflow direction checked
checkpoint | Is the damper mechanism within wall structure
checkpoint | Is the damper expansion material fitted between damper and penetration
checkpoint | Check that the fusible link is fitted and has the correct temperature rating
checkpoint | Check damper blades are fully open
checkpoint | Check damper closure is not impeded (drop test)
checkpoint | Confirm an access panel in the duct is provided and allows access to reset damper
checkpoint | If motorised, is the actuator fixed to the damper body (attach photo)
checkpoint | Confirm break away bolts / fixings have been used (plastic or aluminium) [attach photo]
checkpoint | Are retaining angles fitted and twice the width of gaps (attach photo)
checkpoint | Is the damper labelled with information as required by AS 1682.1 (attach photo)
checkpoint | Attach photo(s) around damper with flanges off, confirming clearances as required by AS 1682.1
checkpoint | Attach photo(s) inside damper through access panel of blades, linkage etc.
checkpoint | Attach photo(s) with flanges on.
checkpoint | Commissioning report attached
checklist-flat | 6.8 Electrical Installation
section | Field Wiring
checkpoint | Area ready and accessible for work
checkpoint | Are cable sizes as per approved drawings
checkpoint | Is correct cable type being used
checkpoint | Is correct cable support method being used
checkpoint | Are isolators installed at equipment
checkpoint | Are isolators labelled
checkpoint | Are flexible connections to equipment installed
checkpoint | Are terminations complete to equipment
section | Switchboard
checkpoint | Area ready and accessible for work
checkpoint | Are mechanical switchboards installed
checkpoint | Are cable sizes as per approved drawings
checkpoint | Are terminations complete at all switchboards
checkpoint | Are terminations for other services complete (e.g. fire trips / submains)
checkpoint | Are switchboards clean
checkpoint | Pre-energisation tests complete
checkpoint | All labels installed
checkpoint | Power available
checkpoint | Has client been notified that the switchboards are live and warning signage installed.
checkpoint | All testing complete
checkpoint | As installed drawings received
checkpoint | Certification received
checklist-flat | 6.9 Water Pipework Installation Checklist
checkpoint | Area ready and accessible for work
checkpoint | Size, position, height, checked against drawings
checkpoint | Bracketing checked (to accommodate springs where applicable)
checkpoint | Clearance for insulation & sheathing as per specification
checkpoint | Insulation blocks correct size
checkpoint | Isolating valves installed
checkpoint | Balancing valves installed
checkpoint | Control valves installed
checkpoint | Flexible connections to equipment installed
checkpoint | BMCS points installed
checkpoint | Air bleeds installed
checkpoint | Anchors & Guides checked against specification
checkpoint | Air Vents checked against specification
checkpoint | Expansion tanks / makeup installed installed– refer 6.35
checkpoint | Dosing pot installed - refer 6.36
checkpoint | Buffer tank installed - refer 6.38
checkpoint | System full of water and air bleed out
checkpoint | Water appropriately chemically treated
checkpoint | Drain down points checked against specification
checkpoint | Pressure Test complete– refer 6.10
checkpoint | Pipe sleeves & fire seals checked against specification
checkpoint | Insulation complete
checkpoint | Sheathing complete
checkpoint | Fire rating complete
checkpoint | Pipework labelling checked
checkpoint | Commissioning report attached
checklist | 6.10 Pipe Pressure Test Report Checklist
section | Checks
checkpoint | System test pressure checked against specification
checkpoint | Allowable drop kPa checked against specification
checkpoint | Duration hour / minute checked against specification
checkpoint | Marked up schematic attached
checkpoint | Marked up layout attached
checkpoint | Test record
checkpoint | Test start - pass once entered
text | Specified system test pressure
text | Test location
text | Test pressure required at testing location to achieve system test pressure
text | Date test commenced
text | Time test commenced
checkpoint | Initial pressure kPa - pass once entered
text | Initial pressure (kPa)
checkpoint | Test finish - pass once entered
text | Date test completed
text | Time test completed
checkpoint | Final pressure kpa - pass once entered
text | Final pressure (kPa)
checkpoint | Test passed
checklist-flat | 6.11 Controls / BMS Installation
section | Field Wiring
checkpoint | Area ready and accessible for work
checkpoint | Are cable sizes as per approved drawings
checkpoint | Is correct cable type being used
checkpoint | Is correct cable support method being used
checkpoint | Are temperature sensors installed
checkpoint | Are all other field devices installed
checkpoint | Are damper motors installed
checkpoint | Are control valve actuators installed
checkpoint | Are VAV controllers installed
checkpoint | Are flexible connections to equipment installed
checkpoint | Are terminations complete to equipment
section | BMS Panels / system
checkpoint | Area ready and accessible for work
checkpoint | Are BMS panels installed
checkpoint | Are cable sizes as per approved drawings
checkpoint | Are terminations complete at all panels
checkpoint | Are terminations for other services complete (e.g. fire, hydraulics, electrical)
checkpoint | Are panels clean
checkpoint | Has point to point check been completed
checkpoint | Have HLI points been migrated from other devices (eg chillers)
checkpoint | Are labels installed on field devices
checkpoint | All labels installed in panels
checkpoint | Power available to panels
checkpoint | Has client been notified that the panels are live and warning signage installed.
checkpoint | Are all graphics complete
checkpoint | Has internet connection been provided and tested
checkpoint | All testing complete
checkpoint | All testing documentation received
checkpoint | All O&M data received
checklist-flat | 6.12 Goods Received and Inspected
checkpoint | Delivery docket number
text | Order number
checkpoint | Supplied as ordered - type and quantity
checkpoint | Delivered free of any damage
select | Any damage reported to supplier | Yes, No, N/A
checkpoint | Goods accepted for incorporation into works
checklist-flat | 6.20 Fan Coil Unit Installation Checklist
checkpoint | Area ready and accessible for work
checkpoint | Model number correct & recorded
checkpoint | Serial number recorded
checkpoint | Equipment installed in correct location
checkpoint | Vibration isolation installed
checkpoint | Clearance & access checked
checkpoint | Internal supports & spring mounts checked
checkpoint | Shipping brackets removed
checkpoint | Seismic restraints installed
checkpoint | Flexible connections installed and aligned to duct connections
checkpoint | Acoustic insulation installed
checkpoint | Safety tray installed
checkpoint | Filters installed
checkpoint | Drains connected and run to tundish
checkpoint | Traps, drains, flow from trays checked without unit running
checkpoint | Unit labelled in accordance with equipment schedule / drawings
checkpoint | Pipe connections completed
checkpoint | Electrical connections complete
checkpoint | Control connections complete
checkpoint | Commissioning report attached
checkpoint | Access for maintenance adequate and safe
checklist-flat | 6.21 Water Cooled Package Unit Installation Checklist
checkpoint | Area ready and accessible for work
checkpoint | Model number correct & recorded
checkpoint | Serial number recorded
checkpoint | Equipment installed in correct location
checkpoint | Vibration isolation installed
checkpoint | Fan & compressor checked
checkpoint | Internal supports & spring mounts checked
checkpoint | Shipping brackets removed
checkpoint | Flexible connections installed and aligned to duct connections
checkpoint | Acoustic insulation installed
checkpoint | Safety tray installed
checkpoint | Filters installed
checkpoint | Drains connected and run to tundish
checkpoint | Traps & drains, flow from trays checked without unit running
checkpoint | Unit labelled in accordance with equipment schedule / drawings
checkpoint | Pipe connections completed
checkpoint | Electrical connections complete
checkpoint | Control connections complete
checkpoint | Commissioning report attached
checkpoint | Access for maintenance adequate and safe
checklist-flat | 6.22 Split AC\VRV Unit Installation Checklist
section | Indoor unit
checkpoint | Area ready and accessible for work
checkpoint | Model number correct & recorded
checkpoint | Serial number recorded
checkpoint | Equipment installed in correct location
checkpoint | Vibration isolation installed
checkpoint | Fan coil unit checked
checkpoint | Shipping brackets removed
checkpoint | Flexible connections installed and aligned to duct connections
checkpoint | Acoustic insulation installed
checkpoint | Safety tray installed
checkpoint | Filters installed
checkpoint | Drains connected and run to tundish
checkpoint | Traps & drains, flow from trays checked without unit running
checkpoint | Unit labelled in accordance with equipment schedule / drawings
checkpoint | Clearance & access checked
checkpoint | Pipe connections completed
checkpoint | Electrical connections complete
checkpoint | Control connections complete
section | Outdoor unit
checkpoint | Area ready and accessible for work
checkpoint | Condenser checked
checkpoint | Model number correct & recorded
checkpoint | Serial number recorded
checkpoint | Equipment installed in correct location
checkpoint | Installed to manufacturers instructions & approved detail
checkpoint | Vibration isolation installed
checkpoint | Fan/coil guards fitted correctly
checkpoint | Shipping brackets removed
checkpoint | Coil fins not damaged
checkpoint | Unit labelled in accordance with equipment schedule / drawings
checkpoint | Pipe connections completed
checkpoint | Electrical connections complete
checkpoint | Control connections complete
checkpoint | Commissioning report attached
checkpoint | Access for maintenance adequate and safe
checklist-flat | 6.23 AHU Installation Checklist
checkpoint | Area ready and accessible for work
checkpoint | Plinths installed
checkpoint | Model number correct & recorded
checkpoint | Serial number recorded
checkpoint | Equipment installed in correct location
checkpoint | Vibration isolation installed
checkpoint | Clearance & access checked
checkpoint | Internal supports & spring mounts checked
checkpoint | Shipping brackets removed
checkpoint | Flexible connections installed and aligned to duct connections
checkpoint | Filters installed
checkpoint | Drains connected and run to tundish
checkpoint | Traps, drains, flow from trays checked without unit running
checkpoint | Unit labelled in accordance with equipment schedule / drawings
checkpoint | Pipe connections completed
checkpoint | Electrical connections complete
checkpoint | VSD installed
checkpoint | Internal lights installed and operational
checkpoint | Control connections complete
checkpoint | Commissioning report attached
checkpoint | Access for maintenance adequate and safe
checklist-flat | 6.25 Fan Installation Checklist
checkpoint | Area ready and accessible for work
checkpoint | Model number correct & recorded
checkpoint | Serial number recorded
checkpoint | Equipment installed in correct location
checkpoint | Vibration isolation installed
checkpoint | Clearance & access checked
checkpoint | Belts, pulleys, guards fitted
checkpoint | Fan airflow direction checked
checkpoint | Flexible connections installed and aligned to duct connections
checkpoint | Acoustic insulation installed
checkpoint | Unit labelled in accordance with equipment schedule / drawings
checkpoint | Filters installed
checkpoint | Electrical connections complete
checkpoint | Control connections complete
checkpoint | VSD installed
checkpoint | Commissioning report attached
checkpoint | Access for maintenance adequate and safe
checklist-flat | 6.26 Heat Exchanger Checklist
checkpoint | Area ready and accessible for work
checkpoint | Plinths installed
checkpoint | Model number correct & recorded
checkpoint | Serial number recorded
checkpoint | Equipment installed in correct location
checkpoint | Vibration isolation installed
checkpoint | Pipe connections completed
checkpoint | Control connections complete
checkpoint | Unit labelled in accordance with equipment schedule / drawings
checkpoint | Commissioning report attached
checkpoint | Access for maintenance adequate and safe
checklist-flat | 6.27 Cooling Tower Installation Checklist
checkpoint | Area ready and accessible for work
checkpoint | Plinths and supports installed
checkpoint | Model number correct & recorded
checkpoint | Serial number recorded
checkpoint | Equipment installed in correct location
checkpoint | Vibration Isolation installed
checkpoint | Installed to manufacturers instructions
checkpoint | Condenser water connections completed
checkpoint | makeup water connections completed
checkpoint | Drain and overflow connections completed and run to sewer
checkpoint | Water level set correctly
checkpoint | Access covers in place and sealed
checkpoint | Sump head above pumps
checkpoint | Air intake clearances adequate
checkpoint | Balance line installed
checkpoint | Belts, pulleys, guards fitted
checkpoint | Internal supports & spring mounts checked
checkpoint | Discharge Ductwork/Attenuation
checkpoint | Electrical connections complete
checkpoint | VSD installed
checkpoint | Control connections complete
checkpoint | Water treatment installed
checkpoint | Side stream filtration installed
checkpoint | Unit labelled in accordance with equipment schedule / drawings
checkpoint | Unit registration submitted to Council by end user / owner
checkpoint | Unit labelled in accordance with Council requirements
checkpoint | Commissioning report attached
checkpoint | Access for maintenance adequate and safe
checklist-flat | 6.28 Pump Installation Checklist
checkpoint | Area ready and accessible for work
checkpoint | Plinths installed
checkpoint | Model number correct & recorded
checkpoint | Serial number recorded
checkpoint | Correct inertia base
checkpoint | Equipment installed in correct location
checkpoint | Vibration Isolation installed
checkpoint | Pump alignment completed (by manufacturer)
checkpoint | Bearings greased
checkpoint | Gland seals piped
checkpoint | Condensate tray fall checked
checkpoint | Condensate tray pipework checked
checkpoint | Pipe connections completed
checkpoint | No external forces on pump from pipework etc
checkpoint | Electrical connections complete
checkpoint | VSD installed
checkpoint | Control connections complete
checkpoint | Unit labelled in accordance with equipment schedule / drawings
checkpoint | Commissioning report attached
checkpoint | Access for maintenance adequate and safe
checklist-flat | 6.29 Chiller Installation Checklist
checkpoint | Area ready and accessible for work
checkpoint | Plinths installed
checkpoint | Model number correct & recorded
checkpoint | Serial number recorded
checkpoint | Equipment installed in correct location
checkpoint | Vibration Isolation installed
checkpoint | Installed to manufacturer's instructions
checkpoint | Pipe removal & clearances for tube clean / withdrawal
checkpoint | Pipework connections complete
checkpoint | Relief valve connections complete
checkpoint | Flow switches installed
checkpoint | Electrical connections complete
checkpoint | Control connections complete
checkpoint | Sensors, controllers, switches fitted to chiller and pipes
checkpoint | Corrosion protection to vessels installed
checkpoint | Refrigerant leak detection installed
checkpoint | Unit labelled in accordance with equipment schedule / drawings
checkpoint | Water balance completed, power on, and controls ready.
checkpoint | Unit commissioned by manufacturer
checkpoint | Commissioning report attached
checkpoint | Access for maintenance adequate and safe
checklist-flat | 6.30 Boiler Installation Checklist
checkpoint | Area ready and accessible for work
checkpoint | Plinths installed
checkpoint | Model number correct & recorded
checkpoint | Serial number recorded
checkpoint | Equipment installed in correct location
checkpoint | Vibration Isolation installed
checkpoint | Installed to manufacturers instructions
checkpoint | Combustion air / mechanical ventilation available
checkpoint | Condensate drain off boiler vessel installed
checkpoint | Flue installed c/w correct discharge
checkpoint | Correct flue size
checkpoint | Fan installed correctly (if required)
checkpoint | Flue drain installed
checkpoint | Relief valve connections complete
checkpoint | Provision to disconnect the flue for servicing & inspection
checkpoint | Drain and test points to boiler flues
checkpoint | Gas pipework, valve train installed and tested
checkpoint | Correct boiler inlet gas pressure ≤7 kPa - checked against manufacturer literature
checkpoint | Heating water pipework completed
checkpoint | Electrical connections complete
checkpoint | Control connections complete
checkpoint | Sensors, controllers, switches fitted to flue and pipes
checkpoint | Unit labelled in accordance with equipment schedule / drawings
checkpoint | Water balance completed, power on, gas available and controls ready.
checkpoint | Unit commissioned by manufacturer
checkpoint | Commissioning report attached
checkpoint | Access for maintenance adequate and safe
checklist-flat | 6.31 Side Stream Filtration Checklist
checkpoint | Area ready and accessible for work
checkpoint | Model number correct & recorded
checkpoint | Serial number recorded
checkpoint | Equipment installed in correct location
checkpoint | Pipework connections complete
checkpoint | Electrical connections complete
checkpoint | Control connections complete
checkpoint | Unit labelled in accordance with equipment schedule / drawings
checkpoint | Unit commissioned
checkpoint | Access for maintenance adequate and safe
checklist-flat | 6.32 Filters Checklist
checkpoint | Type and no off correct
checkpoint | Dimensions correct
checkpoint | Installed to manufacturers instructions
checkpoint | Tested and certified by manufacturer (HEPA filters only)
checkpoint | Test report attached (HEPA filters only)
checklist-flat | 6.33 VAV Unit Installation Checklist
checkpoint | Model number correct & recorded
checkpoint | Serial number recorded
checkpoint | Correct location & orientation checked
checkpoint | Heating / coils checked (if applicable) |  | `
checkpoint | Coil fins not damaged
checkpoint | Electric heater checked (if applicable)
checkpoint | Heater element cleared of debris
checkpoint | Element fins not damaged
checkpoint | Element installed correctly
checkpoint | Heater size/stages correct (checked against schedule)
checkpoint | Insulation checked
checkpoint | Velocity probes installed
checkpoint | Ductwork connected
checkpoint | Power connected
checkpoint | Pipework connected
checkpoint | Controls installed and connected
checkpoint | Commissioning report attached
checkpoint | Access for maintenance adequate and safe
checklist-flat | 6.34 Fume Cupboard Checklist
checkpoint | Area ready and accessible for work
checkpoint | Model number correct & recorded
checkpoint | Serial number recorded
checkpoint | Correct location
checkpoint | Unit labelled in accordance with equipment schedule / drawings
checkpoint | Cupboard fitted with power, gas and water outlets as specified
checkpoint | Cupboard fitted with lighting as specified
checkpoint | Extraction Fan installed
checkpoint | Ductwork connected
checkpoint | Power connected
checkpoint | Pipework connected
checkpoint | Controls installed and connected
checkpoint | Final Commissioning of unit by manufacturer
checkpoint | Certificate of Compliance provided by manufacturer
checkpoint | Commissioning report attached
checkpoint | Access for maintenance adequate and safe
checklist-flat | 6.35 Expansion Vessel Checklist
checkpoint | Model number correct & recorded
checkpoint | Serial number recorded
checkpoint | Correct location
checkpoint | Unit labelled in accordance with equipment schedule / drawings
checkpoint | Wall Mounted Auto Refill Unit unit installed
checkpoint | Complete with Pressure Reducing Fill Valve and Pressure Gauge
checkpoint | Pipework connected
checkpoint | Electrical connections to makeup system complete
checkpoint | Relief valve connections complete
checkpoint | Drain connections complete
checklist-flat | 6.36 Chemical Dosing Pots Checklist
checkpoint | Correct location
checkpoint | Pipework connected to correct system
checkpoint | Drain pipework completed
checklist-flat | 6.37 Variable Speed Drive Checklist
checkpoint | Model number correct & recorded
checkpoint | Serial number recorded
checkpoint | Correct location
checkpoint | Unit labelled in accordance with equipment schedule / drawings
checkpoint | Electrical connections completed
checkpoint | Control connections completed
checkpoint | Screened cable used between VSD and equipment
checkpoint | Isolator installed to line side only
checkpoint | Unit commissioned
checkpoint | Access for maintenance adequate and safe
checklist-flat | 6.38 Buffer Tank Checklist
checkpoint | Area ready and accessible for work
checkpoint | Plinths installed
checkpoint | Capacity correct
checkpoint | Instruments installed
checkpoint | Pipework installation complete
checkpoint | Air bleed installed to top of tank
checkpoint | Insulation complete
checkpoint | Access for maintenance adequate and safe
checklist-flat | 6.42 Refrigeration Pipe Work Checklist
checkpoint | Refrigerant Type checked
select | Refrigerant type | R410A, R134A, R32, R454B, R404,other
checkpoint | Size, position, height, checked against drawings
checkpoint | Bracketing correct
checkpoint | Clearance for insulation & sheathing as per specification
checkpoint | Nitrogen being used during brazing
checkpoint | Pressure Test complete– refer 6.10
checkpoint | Insulation correct type and thickness
checkpoint | Fire rating complete
checkpoint | Systems Vacuumed to 500 Microns
checkpoint | Systems charged with specified quantity of refrigerant Gas
checklist-flat | 6.43 Pre Commissioning Checklist
checkpoint | Ductwork installation complete
checkpoint | Pipework installation complete
checkpoint | Electrical installation complete
checkpoint | Controls installation complete
checkpoint | All required building works complete
checkpoint | Permanent power available
checkpoint | Permanent water makeup available
checkpoint | Systems ready to commission
checklist-flat | 6.44 Commissioning Checklist
checkpoint | Air balance complete
checkpoint | Air balance commissioning results received
checkpoint | Water balance complete
checkpoint | Water balance commissioning results received
checkpoint | Electrical commissioning complete
checkpoint | Electrical commissioning records received
checkpoint | Controls commissioning complete
checkpoint | Controls commissioning records received
checkpoint | Fire mode testing complete
checklist-flat | 6.45 Handover Checklist
checkpoint | Air balance witnessed
checkpoint | Air balance commissioning results issued
checkpoint | Water balance witnessed
checkpoint | Water balance commissioning results issued
checkpoint | Electrical commissioning witnessed
checkpoint | Electrical commissioning records issued
checkpoint | Controls commissioning witnessed
checkpoint | Controls commissioning records issued
checkpoint | Fire mode testing witnessed
checkpoint | Fire damper certification complete and issued
checkpoint | Fire rating certification issued
checkpoint | Installation certification issued
checkpoint | Greenstar documentation issued
checkpoint | O&M issued
checkpoint | Client training completed
checklist | Document Attachment
checkpoint | Attach any relevant documents