## Resources
Rich Type | Id | Warnings | type | name | values | prefix | postfix | Usage Count | User Addable | Template Name | Template Id
checklist-sectioned |  |  | checklist | PCR Precast Panels |  |  |  |  | Yes | ITP - PCR Precast Panels | 04b4613e-3e12-4e59-b202-14c658f1244f
checkpoint-group |  |  | section | Pre Construction
checkpoint-status |  |  | checkpoint | Review of proposed work
label | 90971f68-c589-5034-aace-8cadd1aa9ba3 |  | note | SPECIFICATION REFERENCE - 1235 SHOP DRAWINGS - ITEM 1.10
label | c3f03c04-e42d-5650-87ce-2e576b2f46fb |  | note | TEST REQUIRED - Shop drawings to be reviewed and permission to proceed given.
label | b424a43e-bd77-57e1-970d-f96d1a3eef5f |  | note | INSPECTION BY - Named reviewer or contract administrator
label | 58d0a3c6-87bf-5400-a3c4-9ac3a029eef7 |  | note | TASK TIMING OR TASK FREQUENCY - Start of task
label | 4d6c6c95-a76e-5421-84ba-f8acc29623f7 |  | note | ACCEPTANCE CRITERIA - Shop drawings to be accepted by the reviewer. Building Information Model (BIM) is being used for the construction works.
label | 6781d82e-2789-507f-b92a-a49dfa3889a6 |  | note | UCCL - H
label | 0a46422f-a10a-5318-a713-6376f57a3924 |  | note | Client - A
holdpoint |  |  | signoff | HOLD POINT
checkpoint-group |  |  | section | Materials
checkpoint-status |  |  | checkpoint | Concrete Mix Design
label | ecd61321-8720-5261-a720-0cbc4834e962 |  | note | SPECIFICATION REFERENCE - Ruakaka BESS-Concrete Pads Project Specification 6-P0304.03
label | 1b221014-db3c-5509-99bc-468c4888a8ca |  | note | TEST REQUIRED - Supplier Documentation
label | 0c7fd34a-910d-52ce-b09d-d1e35c64ac49 |  | note | INSPECTION BY - UCCL, MEL
label | 4de78805-ac55-5f90-a5f0-c33384551190 |  | note | TASK TIMING OR TASK FREQUENCY - Each Mix Design used prior to use
label | 87e1b469-a0a3-5e78-8105-52b37c84eda8 |  | note | ACCEPTANCE CRITERIA -
label | e8d517da-ebb5-53ca-915d-8654a0748450 |  | note | Foundations (including retaining wall footing) -
label | 8c020611-2a8b-52bd-a36a-0a087901b509 |  | note | ○ Aggregate: 19mm
label | 2e75d0ee-53df-59a6-a745-8c0e4b6e6a60 |  | note | ○ 28 day strength: 35MPa
label | 17aa18d7-c9e7-5425-a41e-fc0a784ebd7d |  | note | Precast retaining wall -
label | be03edaf-7bad-5927-bdc3-534276b29d5a |  | note | ○ Aggregate size: 19mm
label | 5114cdda-ffda-59f3-8230-6218b4d9bd44 |  | note | ○ 28 day strength: 35MPa
label | 2bf8779c-6962-5aa2-a7a8-9cce6c0a64cc |  | note | UCCL - S
label | fe179974-949a-5e30-a0ac-7e96aa3883ed |  | note | Client - R
checkpoint-status |  |  | checkpoint | Certificates
label | 90f6b821-0051-5e97-ac86-702c0140c547 |  | note | SPECIFICATION REFERENCE - 1.12 Certificates
label | d62cb850-45a4-5895-9f45-f1d1b56c9fab |  | note | TEST REQUIRED - Portland cement to NZS3121,
label | f45dee64-d170-5c38-a5b9-75172d8072fd |  | note | INSPECTION BY - UCCL
label | bf39dc02-af40-55ec-b33b-96ba0c4b9e26 |  | note | TASK TIMING OR TASK FREQUENCY - Each Batch
label | 1e6895bb-27a5-5cb4-baf3-c7e49bd123f4 |  | note | ACCEPTANCE CRITERIA - NZS 3122
label | 26550d26-ed26-5d5d-bee3-8082e7e2484e |  | note | UCCL - S
label | 3aa57f6a-29bc-55f4-ab44-7cc005f24683 |  | note | Client - R
checkpoint-status |  |  | checkpoint | Reinforcement
label | 8af77fe3-82b9-5806-876f-e6271db8287c |  | note | SPECIFICATION REFERENCE - RUK-UMC-DS-01-12
label | 88f0bf85-8db1-5de3-ad2e-83df6d42c9d2 |  | note | TEST REQUIRED - Supplier Documentation, photos of spacings
label | 66dc8b1e-87d2-5593-b233-ca48e0b26c88 |  | note | INSPECTION BY - UCCL, MEL
label | 5ee0131c-ba1c-50eb-857e-12d5d81146bc |  | note | TASK TIMING OR TASK FREQUENCY - Prior to pouring
label | 19047ae2-53ac-5a86-ae5e-29a8a51d5f0b |  | note | ACCEPTANCE CRITERIA - Reinforcement of precast retaining wall to be YD12-200 vertical and horizontal with D12-200 starters. Reinforcement of in-situ strip footing to be 2/YD12 with R6-300 stirrups
label | c1d053f4-e978-5ac3-a7e2-7803d7c19a5a |  | note | UCCL - V
label | c361bb89-8b03-5afb-8c91-8f082ebef02b |  | note | Client - R
checkpoint-status |  |  | checkpoint | Strip Footing
label | 1d1690b9-4fe0-5ae1-9f9f-bd3649512870 |  | note | SPECIFICATION REFERENCE - RUK-UMC-DS-01-12
label | 850b9caa-b009-55e6-be7e-16061e5e68e6 |  | note | TEST REQUIRED - Photos
label | 8be4b4c8-3ce9-5f9d-b7cf-fbad8435113a |  | note | INSPECTION BY - UCCL, MEL
label | cc87971a-d712-5cd1-9ca3-615957069aa8 |  | note | TASK TIMING OR TASK FREQUENCY - Prior to pouring
label | e02c6b40-d077-515d-b399-a0c23890c565 |  | note | ACCEPTANCE CRITERIA - Reinforcement to have maximum 75mm clearance and minimum 50mm clearance.
checkpoint-status |  |  | checkpoint | Cast in Items - Nuts, Bolts and Studs
label | 7f901713-8f2e-5641-8f49-f17d9ec7572c |  | note | SPECIFICATION REFERENCE - RUK-UMC-DS-01-10
label | bb3fe136-9965-52a3-8b28-1a8d32ffbbdd |  | note | TEST REQUIRED - Supplier Documentation
label | ac420068-ce92-52ac-b4d8-b570f39ebe4b |  | note | INSPECTION BY - UCCL
label | fea0706d-82b6-5b97-943b-3deb662d4e9b |  | note | TASK TIMING OR TASK FREQUENCY - Prior to Ordering
label | efb94585-dc69-55e9-b9c9-ca7b8e469bf0 |  | note | ACCEPTANCE CRITERIA - EA bolts to be M16 Hilti RE-500
label | 3e4df94b-08cb-5cbe-825b-d45d1ab1cdd3 |  | note | UCCL - V
label | 5cecbb65-f52a-5e37-82d7-d81cc7a6bcd6 |  | note | Client - R
checkpoint-status |  |  | checkpoint | Air content test
label | d697b482-3d7d-55d9-b02b-93c8985d250b |  | note | SPECIFICATION REFERENCE - 1.13
label | 933ec03f-4a49-579c-88e7-a67c53f4fdfe |  | note | TEST REQUIRED - Supplier Documentation/IANZ Laboratory
label | 72e12ed2-e01a-55b5-a6cb-502ea2875159 |  | note | INSPECTION BY - UCCL
label | 105ec323-c8af-5150-8765-dd6980e3eb87 |  | note | TASK TIMING OR TASK FREQUENCY - Each Batch
label | b61951cf-3caa-5f1f-a6be-62562849c557 |  | note | ACCEPTANCE CRITERIA - NZS3109
label | ced32456-be0a-5663-a182-216c69ebfcc0 |  | note | UCCL - V
label | f7fcfb4f-0413-581f-97b8-efcc28215bbd |  | note | Client - R
checkpoint-status |  |  | checkpoint | Slump Test
label | 190fc0e8-1a66-543c-b274-90cdf7b41244 |  | note | SPECIFICATION REFERENCE - 1,13
label | 6a4ed469-ae55-5ecd-b615-689874eba5f8 |  | note | TEST REQUIRED - Supplier Documentation/IANZ Laboratory
label | 3cdd467e-aa19-5200-b260-846a5d390e1c |  | note | INSPECTION BY - UCCL
label | 3d785d39-ace3-5ed6-93d1-2c7b8eabe1dc |  | note | TASK TIMING OR TASK FREQUENCY - Each Batch
label | f7c4dee2-050c-5c48-bb2e-7f5bb79bad95 |  | note | ACCEPTANCE CRITERIA - NZS3109
label | 7cb63f91-88a9-5715-8b8b-660bb319af42 |  | note | UCCL - V
label | a56eca6e-03e9-5999-a0ff-507d1204e516 |  | note | Client - R
checkpoint-status |  |  | checkpoint | Conduct 7 day strength test
label | 65d4ddc3-4d52-57a2-b576-c5a629213358 |  | note | SPECIFICATION REFERENCE - 3105 - concrete requirements - 1.11
label | 28413179-905b-56de-912f-11d20ae3758f |  | note | TEST REQUIRED - 7 day strength test
label | 851260e5-804c-56e0-af2c-ac7da8372d3a |  | note | INSPECTION BY - UCCL
label | edf81496-d60f-5a99-8188-5b3e95d8cbdd |  | note | TASK TIMING OR TASK FREQUENCY - 7 day after casting
label | 284a9b4b-a6b9-51eb-9587-644c88828dfc |  | note | ACCEPTANCE CRITERIA - 60 % of the specified strength
label | 1f795a71-c068-5cd5-9a8e-3e374f26b274 |  | note | UCCL - V
label | 80ba9af2-b821-51a6-9377-dea0e322182c |  | note | Client - SU
checkpoint-group |  |  | section | Pre Construction - Site works
checkpoint-status |  |  | checkpoint | Strip Footing
label | aa3b2a3c-5705-5ce9-80a5-32112348dc24 |  | note | TEST REQUIRED - Photos
label | f7461b92-83ad-56de-a4e7-d740e8ffb55c |  | note | INSPECTION BY - UCCL
label | 9d178e1f-b992-51ec-bbe5-9c4254c37a96 |  | note | TASK TIMING OR TASK FREQUENCY - Prior to placing site concrete
label | 58c925e4-c0e6-5a9c-85ed-581e14b7aa1e |  | note | ACCEPTANCE CRITERIA - Strip footing to be 400mm wide and 200mm deep
label | b4303b52-38e6-598b-8856-3177f9fc2926 |  | note | UCCL - V
label | 40e48b53-9676-5ced-8995-e2f6c85181d8 |  | note | Client - Su
checkpoint-status |  |  | checkpoint | Subgrade Strength
label | f2c9afaa-1305-52b0-8ea9-41191d8b4347 |  | note | TEST REQUIRED - Scala Penetrometer Records
label | 8bc5c238-0a52-5dfc-b47b-4ed3f940a04e |  | note | INSPECTION BY - UCCL
label | 9fc70161-85bb-5594-b892-f9019cff094a |  | note | TASK TIMING OR TASK FREQUENCY - Prior to placing site concrete
label | 9cc52c11-e453-5853-87ea-99898d9411d6 |  | note | ACCEPTANCE CRITERIA - Subgrade to meet 3 blows/ 100mm with scala testing
label | d2874a53-4d98-5eab-a533-5174ffc499f5 |  | note | UCCL - V
label | 75ba43dc-ed3d-508a-96d0-71707b1f8083 |  | note | Client - W
checkpoint-status |  |  | checkpoint | Formwork
label | ce8e6150-48ae-5751-ab95-8e88274bb4ac |  | note | SPECIFICATION REFERENCE - 3105 - concrete requirements - 1.14
label | a2f43b72-5be2-5ccf-8a3e-5e8dd3c89e3c |  | note | TEST REQUIRED - Quality shape and size of formwork
label | 9d7a142f-b98b-5146-a5fe-eb54a5f544c8 |  | note | INSPECTION BY - UCCL
label | 844ff17d-7134-5e1b-9feb-7033f20ec2f7 |  | note | TASK TIMING OR TASK FREQUENCY - Prior to placing concrete
label | 234c1768-e088-59c0-b757-195f59e3bce4 |  | note | ACCEPTANCE CRITERIA - All formwork to meet the specification required for the unit being constructed
label | 3e8226e4-a47f-5a45-9751-fdebf07ae14e |  | note | UCCL - V
label | 10318f2c-200e-5f43-a31d-1e6e70c638e1 |  | note | Client - W
checkpoint-status |  |  | checkpoint | Site Concrete
label | a253c37b-145e-550b-9caa-1ca4c0011cb0 |  | note | TEST REQUIRED - Visual inspection
label | 43d050f5-426c-57dc-8016-e1c3b2ff67a3 |  | note | INSPECTION BY - UCCL
label | 9b713fa3-8f70-5d34-8c26-c14ca3feb3d4 |  | note | TASK TIMING OR TASK FREQUENCY - Each Foundation
label | 66858838-14ac-5696-9f7f-4db8d854c52b |  | note | ACCEPTANCE CRITERIA - Site concrete to be placed at the thicknesses shown on the drawings and finished to a height of +/- 10mm
label | 80320c8f-40ea-5117-9944-286d13d635e1 |  | note | UCCL - V
label | 09fbdba6-7da5-54a6-a751-781add55708f |  | note | Client - Su
checkpoint-status |  |  | checkpoint | Setout
label | 913c2e06-e16a-50da-882e-3a5ea50e968d |  | note | TEST REQUIRED - Survey
label | 66286942-ce7c-575d-b780-2555f755dc5f |  | note | INSPECTION BY - UCCL
label | 33fbabfd-7fef-52f0-bba4-7e7665c90c12 |  | note | TASK TIMING OR TASK FREQUENCY - Each string
label | 494bfd6c-8194-5978-8fa2-6a684afa7eb9 |  | note | ACCEPTANCE CRITERIA - Foundations and embedded items shall be set out following the tolerances, heights and positions shown in each foundations respective drawing.
label | 158e09d5-b163-5f54-ba99-842100fc1353 |  | note | UCCL - V
label | e65a2c7f-93b1-581f-a1f8-8b61a19cbd65 |  | note | Client - Su
checkpoint-group |  |  | section | Prepour Inspection
checkpoint-status |  |  | checkpoint | Pre pour inspection
label | 4683cd77-1e12-5f5c-b3ba-af37ddb1a706 |  | note | TEST REQUIRED - Visual Inspection
label | cffadeee-43d2-571e-a6b5-9aec92bcdf8e |  | note | INSPECTION BY - UCCL, MEL, WSP
label | a8ded5d7-940d-5602-8999-842e000d9125 |  | note | TASK TIMING OR TASK FREQUENCY - Prior to placing structural concrete
label | 2455849d-412f-5e7e-9b13-ddb249da27da |  | note | ACCEPTANCE CRITERIA - Pre pour inspection sheet to be completed prior to placing concrete. WCL to be notified of pours for inspection at least 24 hours prior to placing concrete.
label | dd9ffde7-fa42-5fe0-85e4-3bcca949d1f0 |  | note | UCCL - H
label | 143be7b8-573a-5ddb-9c7c-6105af9d5c58 |  | note | Client - W
holdpoint |  |  | signoff | HOLD POINT
checkpoint-group |  |  | section | Postpour Inspection
checkpoint-status |  |  | checkpoint | Post pour inspection
label | 766b27fb-ae58-50c7-81c0-2c4968f8a90e |  | note | TEST REQUIRED - Visual Inspection
label | 07a8e286-d0a1-5f63-a7e7-52dff494aa7f |  | note | INSPECTION BY - UCCL
label | 071f8f3f-e76a-5ab9-95c4-5ed9fdc4e0b8 |  | note | TASK TIMING OR TASK FREQUENCY - Following placement of concrete
label | 5f979d12-0636-5c49-8d63-f9593e150a0f |  | note | ACCEPTANCE CRITERIA - Post pour inspection sheet to be completed following each pour.
label | 6d4f4e80-c4a4-57f3-8e1e-51bfafda2595 |  | note | UCCL - A
label | 75d3c291-5419-5204-b4a8-5201d2574f42 |  | note | Client - Su
checkpoint-group |  |  | section | Post Construction
checkpoint-status |  |  | checkpoint | As Built & Final Design Documentation
label | 44c39f02-c31f-5da4-a408-f61c146522d4 |  | note | TEST REQUIRED - Surveying
label | 7e518672-2e3c-502b-be7b-06187a1720db |  | note | INSPECTION BY - UCCL
label | b9733ad1-5c49-5a4b-b50c-21a2e4ec4aa3 |  | note | TASK TIMING OR TASK FREQUENCY - Completion of PCS slab
label | 79d450d4-f014-5c68-b9cc-a413bb1e9f55 |  | note | ACCEPTANCE CRITERIA - Confirmation From Engineer on as built records & redline mark ups
label | 03c1733e-8f04-5e50-86b6-54a987364d2b |  | note | UCCL - S
label | 4de6442e-fcd9-5699-97ca-5f7853785813 |  | note | Client - R
checkpoint-status |  |  | checkpoint | Records of:
label | ec15f4c5-57c3-5c40-bc01-bf136c1e8243 |  | note | SPECIFICATION REFERENCE - Products and materials selected for alternatives specified, Approved substitutions and accepted alternatives, Other approved changes and deviations to items specified.
label | 664a008e-4103-528b-a91e-06d5af8aa092 |  | note | INSPECTION BY - UCC
label | 2eab88c5-f9cf-5cd0-94be-6b8cbe9548af |  | note | TASK TIMING OR TASK FREQUENCY - Completion of PCS slab
label | 79d793d4-f2b4-5a93-83b9-49aba8d142c5 |  | note | ACCEPTANCE CRITERIA - Confirmation From Engineer of all records
label | 42b0de5a-9064-5450-a6b7-7be1038da2aa |  | note | UCCL - S
label | b31b8e5a-d11f-503e-a6d0-f2dfb0eb3dd5 |  | note | Client - R
checkpoint-status |  |  | checkpoint | Producer statement
label | be73ee90-38b8-562f-b213-87512bb9c24d |  | note | SPECIFICATION REFERENCE - 3105 - concrete requirements - 1.14
label | a3e41b33-993c-5845-b787-bf3567f40738 |  | note | TEST REQUIRED - Submit a producer statement for precast units
label | db6614e7-baaa-5a6c-8fb6-74545a24685e |  | note | INSPECTION BY - UCCL
label | 3a3d7785-3f4b-5877-be7c-f12ecbef9c3f |  | note | TASK TIMING OR TASK FREQUENCY - Completion of PCS slab
label | 70d7e15a-72c2-5fac-ae7f-59ef141b2020 |  | note | ACCEPTANCE CRITERIA - Producer statement to verify the products meet the requirements specified.
label | 3522cf61-dd2b-58dc-b902-53d30db21ac6 |  | note | UCCL - S
label | b7423bec-e70d-5cc2-9fa7-81be1d473f39 |  | note | Client - R
checkpoint-status |  |  | checkpoint | Completion Inspection inc. Construction Defects Report
label | 3cb3accd-9e6c-5a1c-96e7-a0c61be9a5e0 |  | note | TEST REQUIRED - Completion inspection on each foundation by CEL
label | ea37f2a1-2ecd-5461-931e-1611a9204e7c |  | note | INSPECTION BY - UCCL
label | 7491a335-3edb-5770-8a32-be5ac13e0be9 |  | note | TASK TIMING OR TASK FREQUENCY - Completion of PCS slab
label | 8d41eae4-f6c6-5ccd-98f2-acbc3e45743f |  | note | ACCEPTANCE CRITERIA - Provided a completed construction defect report that that details any remedial measures taken, & snag lists closed out
label | cae72324-8123-52be-91bc-f6bd7a8ec96c |  | note | UCCL - S
label | da8b5e49-e321-5af1-8e70-18ed677727be |  | note | Client - R
checkpoint-status |  |  | checkpoint | Identification of panels
label | f94ae277-4d89-5a20-8618-66f888e94e40 |  | note | TEST REQUIRED - Panel identification location
label | 1b097c8e-038d-5915-9351-968738c40fb3 |  | note | INSPECTION BY - UCCL
label | 0eb9019a-75e4-57f3-a762-a40e9231f2f6 |  | note | TASK TIMING OR TASK FREQUENCY - Completion of PCS slab
label | 1b7f50c5-25a3-535f-b381-75ea6e4b6dbb |  | note | ACCEPTANCE CRITERIA - Panels to be marked and identified as to which pour they're from and final location.
label | 5bcd180a-6f36-502e-b75c-3f70e1f8845a |  | note | UCCL - V
label | b54678a1-a429-5944-80e5-0b350e9a2e62 |  | note | Client - R