## res
type | name | values | prefix | postfix | usage count | user addable | template name | Resource Id
checklist | DTM-ITP-009- Traffic Signals | itp |  |  |  |  | DTM-ITP-009- Traffic Signals Rev1
section | 1 - Preliminary Works
checkpoint | 1.1 - Check for correct documentation
label | FREQUENCY: Prior to commencing any activity
label | ACCEPTANCE CRITERIA: Ensure that all employees and subcontractors are:
label | – using the correct and complete set of drawings
label | – all drawings are the latest revision
label | REFERENCE DOCUMENTS: Drawings and drawing registers
label | INSPECTION/TEST METHOD: Visual inspection
label | RECORD OF CONFORMITY: This ITP signed off
label | HP*
label | RESPONSIBILITY: Fulton Hogan Engineer
date | Date Completed:
checkpoint | 1.2 - Implementation of all measures and controls
label | FREQUENCY: Prior to commencing any activity
label | ACCEPTANCE CRITERIA: All necessary measures and controls are being implemented, that is: PSP, EMP, TMP/TGS, JSEA, SWMS & WP
label | REFERENCE DOCUMENTS: PSP, EMP, TMP, JSEA, SWMS, WP
label | INSPECTION/TEST METHOD: Visual Inspection
label | RECORD OF CONFORMITY: This ITP signed off
label | HP*
label | RESPONSIBILITY: Fulton Hogan Engineer
date | Date Completed:
checkpoint | 1.3 - Ensure correct materials are being used
label | FREQUENCY: Each Product/ Supplier
label | ACCEPTANCE CRITERIA: Hold Point 730.07, Written acceptance of conditions must be supplied to Department of State Growth prior to purchase for equipment outside of this Specification
label | ○ Electrical Conduit:All conduits installed underground for electrical wiring, traffic signals and traffic services shall be heavy duty grade , rigid orange, UPVC conduit to AS/NZS 2053.2
label | ○ Communications Conduit: Rigid white UPVC communication conduit complying with AS/NZS 2053.2
label | ○ Pit Lids: Cable pit lids shall be in accordence with DSG standard drawings from Table 733.071.
label | ○ Bedding and Backfill Material: Materials used for bedding shall be free from perishable matter and shall conform with the appropriate grading and plasticity index requirements specified in Table 733.061
label | ○ Cable pits shall be in accordence to 730.10. and DSG standard drawings from Table 733.071
label | ○ Detector pits shall be in accordence to DSG Stand drawing SD-101-023
label | REFERENCE DOCUMENTS: 730.07
label | INSPECTION/TEST METHOD: Verify
label | RECORD OF CONFORMITY: This ITP signed off, Materials List Submited for Approval
label | HP
label | RESPONSIBILITY: Fulton Hogan Engineer/Superintendant
date | Date Completed:
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 1.4 - Pre-installation
label | FREQUENCY: Prior to Works commencing
label | ACCEPTANCE CRITERIA: A Pre-installation site walk is to be completed with the Electrical subcontractor, Civil Contractor, Superindentant and DSG SM Representative.
label | ○ The Contractor shall not commence installation of the traffic signal pedestals, poles, controller bases or pits until the pre-installation report has been approved.
label | REFERENCE DOCUMENTS: 730.08
label | INSPECTION/TEST METHOD: Verify
label | RECORD OF CONFORMITY: Signed Pre-installation report by all parties
label | HP
label | RESPONSIBILITY: Fulton Hogan Engineer/ Superintendant/DSG SM/Elect Subcontractor
date | Date Completed:
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 1.5 - Set Out
label | FREQUENCY: Prior to commencing any activity
label | ACCEPTANCE CRITERIA: Survey activities undertaken to ensure and validate that all works meet level and location requirements. The establishment and integrity of the survey network shall be verified before commencing any survey and set out activity. IFC and latest available revision used.
label | ○ Where alternative foundations, conduits or pit locations are proposed, they shall be approved by the Superintendent prior to the Contractor installing items.
label | REFERENCE DOCUMENTS: 730.11
label | INSPECTION/TEST METHOD: Verify
label | RECORD OF CONFORMITY: This ITP signed off
label | HP*
label | RESPONSIBILITY: Fulton Hogan Engineer/ Superintendant
date | Date Completed:
checkpoint | 1.6 - Proving Services
label | FREQUENCY: Prior to commencing works
label | ACCEPTANCE CRITERIA: Underground services shall be proved by clearly marking the location of the service on the ground and physical exposure of relevant services at appropriate locations, in accordance with service authority requirements.
label | REFERENCE DOCUMENTS: 160.12B
label | INSPECTION/TEST METHOD: Verify
label | RECORD OF CONFORMITY: This ITP signed off
label | HP
label | RESPONSIBILITY: Fulton Hogan Engineer/QAV
date | Date Completed:
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 1.7 - Excavations within 3m of poles or stays, Exacavtions within 1m of Underground Assets
label | FREQUENCY: Prior to commencing works
label | ACCEPTANCE CRITERIA: Advice must be sought for any excavations within 3m of poles or stays, or 1m of Underground assets of TasNetworks.
label | REFERENCE DOCUMENTS: 160.12A
label | INSPECTION/TEST METHOD: Verify
label | RECORD OF CONFORMITY: This ITP signed
label | WP
label | RESPONSIBILITY: Fulton Hogan Engineer/ TasNetworks
date | Date Completed:
checkpoint | 1.8 - Boring proposal
label | FREQUENCY: Prior to boring
label | ACCEPTANCE CRITERIA: Detailed proposal for any boring under carriageways submitted to superintendent two weeks prior to programmed commencement
label | REFERENCE DOCUMENTS: 733.03
label | INSPECTION/TEST METHOD: Verify
label | RECORD OF CONFORMITY: This ITP signed
label | HP
label | RESPONSIBILITY: Fulton Hogan Engineer/ Superintendant
date | Date Completed:
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 1.9 - Submission of Mix Design
label | FREQUENCY: Prior to commencing
label | ACCEPTANCE CRITERIA: Hold Point
label | ○ Concrete mix design complies with requirements of Section 610 and appears on the Register of State Growth approved concrete mixes.
label | ○ Submit for review by the Superintendent not less than 4 weeks prior to the placement of concrete.
label | REFERENCE DOCUMENTS: 610.07
label | INSPECTION/TEST METHOD: Correspondence of receipt of mix design
label | RECORD OF CONFORMITY: Superintendent HP Release on Procore
label | HP
label | RESPONSIBILITY: Fulton Hogan Engineer/ Superintendant
date | Date Completed:
holdpoint | AUTHORITY HOLDPOINT
section | 2 - Conduits and Pits
checkpoint | 2.1 - Excavation/Boring & Trenching
label | FREQUENCY: Prior to Backfill
label | ACCEPTANCE CRITERIA: Where conduits are laid under carriageway pavements, the minimum cover from top of conduit to the pavement surface shall be 1200 mm for freeways and arterial roads, and 600 mm for local roads.
label | ○ In areas where ground conditions preclude a minimum cover of 600mm, Superintendent may agree to alternative arrangements providing comparable level of protection
label | ○ Saw cut edge of trench within road pavement
label | REFERENCE DOCUMENTS: 733.03
label | INSPECTION/TEST METHOD: Verify
label | RECORD OF CONFORMITY: This ITP signed
label | IP
label | RESPONSIBILITY: Fulton Hogan Engineer/ Superintendant/DSG SM
date | Date Completed:
checkpoint | 2.2 - Installation of Conduits
label | FREQUENCY: Each Lot
label | ACCEPTANCE CRITERIA: All conduits to terminate in a pit in accordance with the arrangement in DSG Standard Drawings (Table 733)
label | ○ Conduits for detector cables installed as per TC-1207 and TC-1320
label | ○ No bends in continuous sections of conduit shall be permitted. Changes in conduit direction shall only occur at a pit.
label | ○ Cables laid in continuous unjoined lengths between relevant standard points of connection
label | ○ Changes in conduit direction or depth made by natural set or wept bend – no elbows or tees
label | ○ Through conduits shall be suitably aligned as they enter and leave pits to aid pulling cables
label | ○ Conduits shall not be subject to construction loadings
label | REFERENCE DOCUMENTS: 733.04
label | INSPECTION/TEST METHOD: Verify
label | RECORD OF CONFORMITY: This ITP signed WP
label | IP
label | RESPONSIBILITY: Fulton Hogan Engineer
date | Date Completed:
checkpoint | 2.3 - Installation of Draw Cords
label | FREQUENCY: Each Lot
label | ACCEPTANCE CRITERIA: All conduits shall be provided with a draw string secured at the ends
label | REFERENCE DOCUMENTS: 733.05
label | INSPECTION/TEST METHOD: Verify
label | RECORD OF CONFORMITY: This ITP signed
label | IP
label | RESPONSIBILITY: Fulton Hogan Engineer
date | Date Completed:
checkpoint | 2.4 - Back Fill of Trenches - Open Trench
label | FREQUENCY: Each Lot
label | ACCEPTANCE CRITERIA: Bedding:
label | – Bedding material shall be placed and compacted for the full width of the trench to a depth of not less than 80 mm on an earth foundation or 200 mm on a rock foundation
label | – when conduits are positioned, additional 150mm layer shall be place and compacted above previous layer
label | ○ Filling:
label | – conduits under area to be paved backfilled with select back fill to subgrade level
label | – conduits under area not to be paved backfilled with select fill to 0.4m above top of conduit and common back fill above that
label | – conduits may be backfilled with stab sand.
label | REFERENCE DOCUMENTS: 733.06
label | INSPECTION/TEST METHOD: Verify
label | RECORD OF CONFORMITY: This ITP signed
label | IP
label | RESPONSIBILITY: Fulton Hogan Engineer
date | Date Completed:
checkpoint | 2.5 - Back Fill of Trenches - Inspection (Open Trench)
label | FREQUENCY: Each Lot
label | ACCEPTANCE CRITERIA: All conduit, pit and foundation works shall be inspected by the Superintendent and Department of State Growth TSM SME prior to the Contractor covering the works.
label | REFERENCE DOCUMENTS: 733.06
label | INSPECTION/TEST METHOD: Verify
label | RECORD OF CONFORMITY: This ITP signed
label | HP
label | RESPONSIBILITY: Fulton Hogan Engineer/SI/ DSG SM
date | Date Completed:
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 2.6 - Back Fill of Trenches - Grout & Inspection (Direction Bore Trench)
label | FREQUENCY: Each Lot
label | ACCEPTANCE CRITERIA: Before backfilling the bore access excavation, the pressure grouting shall be inspected by the superintendent or representative.
label | The annulus between the bore and the carrier conduits shall be filled by low thermal resistivity, flowable and pumpable grout mixture (comprising sand, cement and suitable additives such as flowable fill). The grout mixture shall be suitable for backfilling around conduits carrying high voltage electrical cables and shall have the following properties:
label | ○ low exothermic temperature generation during curing
label | ○ a thermal resistivity (TR) value of less than 1.2K.m/W when fully dried
label | ○ a maximum grout flow time through a standard flow cone test of 30 seconds in accordance with AS 1478.2
label | ○ compressive strength in the range of 0.5 to 2.0 MPa at 28 days
label | ○ a maximum heat of hydration of 35ºC when tested in an insulated 300mm x 300mm cube.
label | Grouting shall fill the voids at low injection pressures without causing deformation to the conduits within the bore holes. The ends of conduits shall be sealed watertight to prevent ingress of grout.
label | REFERENCE DOCUMENTS: 733.06
label | INSPECTION/TEST METHOD: Verify
label | RECORD OF CONFORMITY: This ITP signed
label | HP
label | RESPONSIBILITY: Fulton Hogan Engineer/SI/ DSG SM
date | Date Completed:
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 2.7 - Compaction
label | FREQUENCY: Each Lot
label | ACCEPTANCE CRITERIA: All pavement material shall have during compaction, uniform moisture content within the range 85% to 115% of the optimum moisture content as determined in the Modified Compaction test. All pavement layers shall be placed and compacted in layers to a density ratio of not less than 98%. The calculation of density ratio shall be based on Modified compactive effort.
label | REFERENCE DOCUMENTS: 733.06
label | INSPECTION/TEST METHOD: Verify
label | RECORD OF CONFORMITY: This ITP signed
label | TP
label | RESPONSIBILITY: Fulton Hogan Engineer
date | Date Completed:
checkpoint | 2.8 - Installation of marker tape
label | FREQUENCY: Each Lot
label | ACCEPTANCE CRITERIA: Marker tape at 100mm wide is to be installed 300mm above each line of conduits in all trenches where electrical and communications conduits are provided. When constructed in a shared trench, it must be ensured that the electrical warning tape is on top.
label | REFERENCE DOCUMENTS: AS/NZS 3000:2018
label | INSPECTION/TEST METHOD: Verify
label | RECORD OF CONFORMITY: This ITP signed
label | IP
label | RESPONSIBILITY: Fulton Hogan Engineer
date | Date Completed:
checkpoint | 2.9 - Cable Pits & Pit Lids
label | FREQUENCY: Each Lot
label | ACCEPTANCE CRITERIA: Cable pits constructed and installed as per drawings
label | ○ Cable pits for traffic signals constructed and installed as per DSG standard drawings from Table 733.071
label | ○ Cable pit lids shall be labelled in accordance with SD-101-022 as appropriate.
label | ○ Reinforced concrete apron installed around pits that aren’t within footpath area (unsealed area)
label | ○ Heavy pit lid provided where pit is located in trafficable areas
label | ○ All pits, junction boxes or terminal pits for electrical purposes shall be watertight
label | ○ Pits shall be constructed such that the level of the top of the pit lid matches surrounding finished surface level, top of pit wall is finished so that lid fits without movement
label | ○ All conduit connections to cable pits shall be neatly made and the ends of the conduits trimmed off and fitted with a conduit bush. The area between the conduit bush and pit wall shall be stopped with a suitable sealant that bonds to the pit wall and the conduit.
label | REFERENCE DOCUMENTS: 733.07
label | INSPECTION/TEST METHOD: Verify
label | RECORD OF CONFORMITY: This ITP signed
label | IP
label | RESPONSIBILITY: Fulton Hogan Engineer
date | Date Completed:
checkpoint | 2.10 - Asbestos Removal
label | FREQUENCY: Each Lot
label | ACCEPTANCE CRITERIA: Asbestos or suspected asbestos found on site that is not identified in the Project Specification shall be immediately reported to the Superintendent. The Contractor shall not disturb any asbestos or suspected asbestos unless approved by the Superintendent in writing.
label | REFERENCE DOCUMENTS: 733.07 (b)
label | INSPECTION/TEST METHOD: Verify
label | RECORD OF CONFORMITY: This ITP signed
label | HP
label | RESPONSIBILITY: Fulton Hogan Engineer/Superindentant
date | Date Completed:
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 2.11 - Pit Lid Surrounds
label | FREQUENCY: Each Lot
label | ACCEPTANCE CRITERIA: Before the pit lid surround or pre-formed collar is cemented into position an inspection by Department of State Growth Superintendent or representative must be carried out. Cable pit lids and frames, where required, shall be installed with an approved surround. The app types of pit lid surround are:
label | (i) a poured ‘in situ’ concrete apron (typically used where two or more pits are co-located)
label | (ii) a steel pre-formed collar that requires concrete in-filling ‘in situ’
label | (iii) a pre-formed composite material collar.
label | REFERENCE DOCUMENTS: 733.07 (c)
label | INSPECTION/TEST METHOD: Verify
label | RECORD OF CONFORMITY: This ITP signed
label | HP
label | RESPONSIBILITY: Fulton Hogan Engineer/Superindentant/DSG SM
date | Date Completed:
holdpoint | AUTHORITY HOLDPOINT
section | 3 - Posts/Pedestals
checkpoint | 3.1 - Determine footing required at location
label | FREQUENCY: Prior to Commencing
label | ACCEPTANCE CRITERIA: Check against IFC Drawings and standard drawings that the correct footing will be constructed each area
label | REFERENCE DOCUMENTS: IFC Drawings
label | INSPECTION/TEST METHOD: Visual Inspection
label | RECORD OF CONFORMITY: This ITP Signed
label | IP
label | RESPONSIBILITY: Fulton Hogan Engineer
date | Date Completed:
checkpoint | 3.2 - Excavation Levels
label | FREQUENCY: Each lot
label | ACCEPTANCE CRITERIA: Check levels conform to relevant drawing depending on type of pole to be installed.
label | REFERENCE DOCUMENTS: IFC Drawings
label | INSPECTION/TEST METHOD: Visual Inspection
label | RECORD OF CONFORMITY: This ITP Signed
label | IP
label | RESPONSIBILITY: Fulton Hogan Engineer
date | Date Completed:
checkpoint | 3.3 - Rag Bolt Assembly
label | FREQUENCY: Each location where rag bolts are required as apart of Standard Drawings
label | ACCEPTANCE CRITERIA: Check rag bolts are assembled as per DoSG Standard Drawings and/or manufacturers specifications (relevant to type of foundation required). Rag Bolt assembly shall comply with Standard Drawings TC-1200 and/or Table 730.111 drawings
label | REFERENCE DOCUMENTS: State Growth Standard Drawings - Rag Bolt Assembly TC-1200
label | INSPECTION/TEST METHOD: Visual Inspection
label | RECORD OF CONFORMITY: This ITP Signed
label | IP
label | RESPONSIBILITY: Fulton Hogan Engineer
date | Date Completed:
checkpoint | 3.4 - Pre-pour inspection
label | FREQUENCY: Prior to covering the works
label | ACCEPTANCE CRITERIA: All conduit, pit and foundation works shall be inspected by the Superintendent prior to the Contractor covering the works.
label | REFERENCE DOCUMENTS: 730.11
label | INSPECTION/TEST METHOD: Visual Inspection
label | RECORD OF CONFORMITY: This ITP Signed
label | HP
label | RESPONSIBILITY: Fulton Hogan Engineer/Superindentant/DSG SM
date | Date Completed:
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 3.5 - Pouring of concrete - foundations
label | FREQUENCY: Each Lot
label | ACCEPTANCE CRITERIA: All concrete works shall conform to VicRoads standard drawings and to be undertaken in accordance with Section 730.13 of the Specification and Section 610. Concrete to be a minimum concrete grade of VR330/32 or approved alternative.
label | REFERENCE DOCUMENTS: 730.13
label | INSPECTION/TEST METHOD: Document review & Site inspection
label | RECORD OF CONFORMITY: This ITP Signed
label | IP
label | RESPONSIBILITY: Fulton Hogan Engineer
date | Date Completed:
checkpoint | 3.6 - Sampling and Concrete Testing
label | FREQUENCY: Each Pour
label | ACCEPTANCE CRITERIA: Concrete Strength Grade shall be N32 to the requirements of AS 1379.
label | ○ Testing to be in accordance with AS 1012 and AS 1379. Each sample of concrete shall be testing for compressive strength and slump.
label | ○ Standard compression tests shall comprise of 3 cylinders ( 1x7day, 2x28day).
label | ○ Sampling shall be undertaken as for Table 730.131:
label | 1 Sample = 0-10m3
label | 2 Sample = 10-25m3
label | 3 Sample = 25-50m3
label | 4 Sample = 50-100m3
label | REFERENCE DOCUMENTS: 730.13
label | INSPECTION/TEST METHOD: Test
label | RECORD OF CONFORMITY: This ITP Signed
label | TP
label | RESPONSIBILITY: Fulton Hogan Engineer
date | Date Completed:
checkpoint | 3.7 - Standing of Pedestals and Poles
label | FREQUENCY: Each Lot
label | ACCEPTANCE CRITERIA: Pedestals and poles shall be installed in accordance with the following requirements:
label | (1) for all new and major remodels, all Type 2 pedestals shall be 2T
label | (2) for minor remodels 2T pedestals shall be used
label | (3) where specified, Type 3 pedestals shall be installed for pedestrian detectors
label | (5) pedestals and poles shall be fastened to the rag bolt assembly cast into the foundations, as detailed in Standard Drawing SD-101-003, with the nuts tightened to 150 Nm of torque
label | (6) pedestals and poles shall be installed such that they are vertical when fully loaded
label | (7) pedestals shall not be stood within 48 hours of casting of the foundations
label | (8) JUP, MA and JUMA poles shall not be stood within 7 days of the casting of the foundations
label | (9) JUP, MA and JUMA poles shall be installed such that the access door is on the face furthest from the traffic flow.
label | REFERENCE DOCUMENTS: 730.14 (A)
label | INSPECTION/TEST METHOD: Verify
label | RECORD OF CONFORMITY: Test Reports
label | IP
label | RESPONSIBILITY: Fulton Hogan Engineer
date | Date Completed:
checkpoint | 3.8 - Post pour Inspection
label | FREQUENCY: Each Lot
label | ACCEPTANCE CRITERIA: Complete post pour inspection. Cure concrete and inspect for cracks and defects
label | REFERENCE DOCUMENTS: 730.12 (d)
label | INSPECTION/TEST METHOD: Test
label | RECORD OF CONFORMITY: This ITP signed off
label | IP
label | RESPONSIBILITY: Fulton Hogan Engineer
date | Date Completed:
section | 4 - Lantern/Hardware Installation
checkpoint | 4.1 - Hardware Installation
label | FREQUENCY: Each Lot
label | ACCEPTANCE CRITERIA: Hardware shall be installed in accordance with the following requirements:
label | (1) all lanterns shall be mounted vertically, using standard straps securely fixed to mounting brackets or lugs
label | (2) upper mounting brackets shall be oriented and fixed to the top of pedestals in accordance with Standard Drawing SD-101-102
label | (3) two-way and four-way lower mounting brackets shall be fixed as required to provide suitable mounting points for the installation of lanterns
label | (4) the top and bottom of each lantern must be firmly attached to ensure that it will not rotate
label | (5) each lantern shall be attached so as to provide an unobstructed line of sight to the traffic which it controls, and such that the potential to be hit by vehicles is minimised
label | (6) external cables and conduits shall be fixed to pedestals, poles or supports using suitable plastic cable ties
label | (7) cable connections to lanterns shall be of sufficient length to hang below the cable entry point on the lantern (this is referred to as a drip loop), but not hang below the lower mounting strap, as shown in Standard Drawing SD-101-103, and shall be securely fixed by means of cable ties allowed; this will typically require the cables supplied with lanterns to be replaced with longer cables when installed on mast arm outreaches
label | (8) cable connections to lanterns shall be made with continuous lengths of cable; no joins shall be
label | (9) junction boxes, key switches, and all other electrical hardware shall comply with the relevant Australian Standards.
label | REFERENCE DOCUMENTS: 730.14 (c)
label | INSPECTION/TEST METHOD: Visual inspection
label | RECORD OF CONFORMITY: This ITP signed
label | IP
label | RESPONSIBILITY: Fulton Hogan Engineer
date | Date Completed:
checkpoint | 4.2 - Lantern Mounting Height
label | FREQUENCY: Each Lot
label | ACCEPTANCE CRITERIA: Lantern mounting heights shall be in accordance with the following requirements:
label | (1) mounting heights for lanterns on 2T pedestals shall be as specified in Standard Drawing SD-101-202
label | (2) lanterns installed on the vertical section of an MA, JUP and JUMA shall be mounted on lugs so as to give the same mounting heights for the respective lantern positions as specified in Standard Drawing SD-101-202
label | (3) lanterns on the outreach of an MA or JUMA shall be mounted in accordance with Standard Drawing SD-101-011
label | (4) 1 and 2 aspect lanterns shall be installed to achieve the mounting height of an aspect of the same colour as if it were part of a 3-aspect lantern
label | (5) 2 aspect bicycle lanterns shall be mounted at the same height as pedestrian lanterns
label | (6) aspects fitted with white or lunar white lenses shall be mounted at the same height as a green aspect
label | (7) lanterns mounted on poles not belonging to Department of State Growth shall be mounted at the same heights as specified in Standard Drawing SD-101-202
label | (8) internally illuminated signs shall be mounted at a height to provide a clearance of not less than 2.4 m from the finished surface level
label | (9) flashing yellow signals used at pedestrian crossings shall be mounted at the height specified in Standard Drawing SD-101-203.
label | REFERENCE DOCUMENTS: 730.14 (d)
label | INSPECTION/TEST METHOD: Visual inspection
label | RECORD OF CONFORMITY: This ITP signed
label | IP
label | RESPONSIBILITY: Fulton Hogan Engineer
date | Date Completed:
checkpoint | 4.3 - Lantern Mounting Locations and Allignment
label | FREQUENCY: Each Lot
label | ACCEPTANCE CRITERIA: Lantern mounting locations shall be in accordance with the following requirements:
label | (1) lanterns shall be mounted as indicated in Standard Drawing SD-101-102and SD-101-202
label | (2) pedestrian lanterns shall be mounted not more than 1 m from the projection of the nearest crosswalk line
label | (3) where 2 aspect bicycle lanterns are installed adjacent to pedestrian lanterns, the bicycle lanterns shall be located on the furthest side from the pedestrian crossing (i.e. left side of the pedestrian lantern when looking at the displays).
label | The alignment of lanterns shall be in accordance with the following requirements:
label | (1) vehicle lanterns shall be aligned so as to provide optimum visibility for approaching traffic considering road alignment, speed, visibility and other site characteristics
label | (2) generally, lanterns shall be aimed at a point on the centre of the approach, at a distance before the stop line as shown in Table 730.141.
label | (3) pedestrian lanterns shall be aimed at the mid-point of the cross walk on the opposite side of the carriageway to which it applies.
label | REFERENCE DOCUMENTS: 730.14 (e & f)
label | INSPECTION/TEST METHOD: Visual inspection
label | RECORD OF CONFORMITY: This ITP signed
label | IP
label | RESPONSIBILITY: Fulton Hogan Engineer
date | Date Completed:
checkpoint | 4.4 - Target Boards, Visors and Louvres
label | FREQUENCY: Each Lot
label | ACCEPTANCE CRITERIA: All target boards shall suit the housing type (metal, plastic) of lanterns and include a white border around the outside edge
label | ○ Target boards shall be fitted to all lanterns in accordance with Standard Drawing SD-101-103
label | ○ All visors for vehicle lanterns shall be type 3 with no cutaway.
label | ○ All visors for pedestrian and bicycle lanterns shall be type 4 with no cutaway.
label | ○ Refer to Department of State Growth Standard Drawing SD-101-104 for details of the visor types.
label | ○ Louvres shall not be installed on LED lanterns unless otherwise specified.
label | REFERENCE DOCUMENTS: 730.14 (g)
label | INSPECTION/TEST METHOD: Visual inspection
label | RECORD OF CONFORMITY: This ITP signed
label | IP
label | RESPONSIBILITY: Fulton Hogan Engineer
date | Date Completed:
checkpoint | 4.5 - Installation of Pedestrian Push Buttons
label | FREQUENCY: Each Lot
label | ACCEPTANCE CRITERIA: Pedestrian push buttons shall be installed in accordance with following requirements:
label | (1) pedestrian push button assemblies shall be mounted clear of any access openings and such that the centre of the button is 0.9 m above finished surface level, as shown in Standard Drawing SD-101-202
label | (2) Pedestrian push button shall be mounted within proximity of ramps, preferably in ramp wings to enable reachable access maximum distance is 300 mm as specified in Standard Drawing.
label | (3) the face of the button shall be in line with the direction of the associated walk lines
label | (4) the tactile arrow indicator shall be oriented to indicate the walk direction to which the button relates, with the arrow pointing up to indicate a straight ahead walk direction
label | (5) where a single button is mounted in a median, a double headed arrow plate shall be used with the arrow oriented horizontally and the front face of the button shall be parallel with the walk direction
label | (6) a label complying with Standard Drawing SD-101-402 shall be installed on the pedestal or pole directly above each pedestrian push button.
label | REFERENCE DOCUMENTS: 730.14 (h)
label | INSPECTION/TEST METHOD: Visual inspection
label | RECORD OF CONFORMITY: This ITP signed
label | IP
label | RESPONSIBILITY: Fulton Hogan Engineer
date | Date Completed:
checkpoint | 4.6 - Non-Commissioned Lanterns
label | FREQUENCY: Each Lot
label | ACCEPTANCE CRITERIA: The faces of all installed but not yet operating lanterns shall be covered.
label | ○ At sites that have not been switched on, all vehicle lanterns shall be covered with ‘NOT IN USE’ signs as shown in SD-101-403.
label | ○ At remodel sites, or sites where existing lanterns are operating, all non-operating lanterns shall be covered with a ‘NOT IN USE’ sign or other approved method.
label | REFERENCE DOCUMENTS: 730.14 (h)
label | INSPECTION/TEST METHOD: Visual inspection
label | RECORD OF CONFORMITY: This ITP signed
label | IP
label | RESPONSIBILITY: Fulton Hogan Engineer
date | Date Completed:
checkpoint | 4.7 - Inspection
label | FREQUENCY: Each Lot
label | ACCEPTANCE CRITERIA: All installed hardware shall be inspected by the Superintendent prior to works proceeding
label | REFERENCE DOCUMENTS: 730.14
label | INSPECTION/TEST METHOD: Visual inspection
label | RECORD OF CONFORMITY: This ITP signed
label | HP
label | RESPONSIBILITY: Fulton Hogan Engineer/SuperIndentant
date | Date Completed:
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 4.8 - ITS Installation
label | FREQUENCY: Each Lot
label | ACCEPTANCE CRITERIA: All ITS equipment shall be supplied and installed in accordance with 732.
label | REFERENCE DOCUMENTS: 732
label | INSPECTION/TEST METHOD: Visual inspection
label | RECORD OF CONFORMITY: This ITP signed
label | IP
label | RESPONSIBILITY: Fulton Hogan Engineer
date | Date Completed:
section | 5 - Electrical
checkpoint | 5.1 - Point of Supply
label | FREQUENCY: Each Lot
label | ACCEPTANCE CRITERIA: Point of Supply to be Installated as per 730.16 (a) to be captured on "DTM-ITP-005 - Service Relocations - TasNetworks".
label | ○ The Contractor shall lodge all relevant associated documentation to comply with the requirements of TasNetworks and WorkSafe Tasmania for the provision of a 240 v 50 Hz single phase power supply for final termination on not less than a 32 amp service fuse.
label | REFERENCE DOCUMENTS: 730.16 (a)
label | INSPECTION/TEST METHOD: Verify
label | RECORD OF CONFORMITY: This ITP signed
label | IP
label | RESPONSIBILITY: Fulton Hogan Engineer
date | Date Completed:
checkpoint | 5.2 - Connection of Traffic Signal Controller
label | FREQUENCY: Each Lot
label | ACCEPTANCE CRITERIA: The Contractor shall install a 2 or 3 core low voltage power supply cable in a Dia. 50 mm HDPE conduit between the point of supply and the controller base in accordance with the requirements of the supply authority.
label | ○ Sufficient cable shall be provided to reach 1.0 m above the controller base.
label | ○ An additional length of at least 1.5 m of the power supply cable shall be left coiled in the pit closest to the controller base.
label | ○ The active and neutral cores of the power supply cable shall have a cross sectional area not less than 6mm2
label | REFERENCE DOCUMENTS: 730.16 (b)
label | INSPECTION/TEST METHOD: Verify
label | RECORD OF CONFORMITY: This ITP signed
label | IP
label | RESPONSIBILITY: Fulton Hogan Engineer
date | Date Completed:
checkpoint | 5.3 - Site Cabling
label | FREQUENCY: Each Lot
label | ACCEPTANCE CRITERIA: All Cabling to be installed as per 730.17.
label | REFERENCE DOCUMENTS: 730.17
label | INSPECTION/TEST METHOD: Visual inspection
label | RECORD OF CONFORMITY: This ITP signed
label | IP
label | RESPONSIBILITY: Fulton Hogan Engineer
date | Date Completed:
checkpoint | 5.4 - Installation of Detector Loops
label | FREQUENCY: Each Lot
label | ACCEPTANCE CRITERIA: The Contractor shall arrange for the installation of vehicle detector loops in accordance with the drawings. Traffic Signals Maintenance can assist in the installation of vehicle detector loops as agreed.
label | ○ Where the road is to be resurfaced Sub-Pavement Loops (EZY Loops) shall be installed under the wear surface of the final bitumen seal.
label | REFERENCE DOCUMENTS: 730.17 (f)
label | INSPECTION/TEST METHOD: Visual inspection
label | RECORD OF CONFORMITY: This ITP signed
label | IP
label | RESPONSIBILITY: Fulton Hogan Engineer
date | Date Completed:
section | 6 - Comissioning and Testing
checkpoint | 6.1 - Testing of Electrical Works/PreCommisioning
label | FREQUENCY: All Electrical Works
label | ACCEPTANCE CRITERIA: Electrical installation testing in accordance with AS 3000 and AS 3017, including:
label | ○ continuity of all active conductors
label | ○ continuity of neutral and ELV conductors
label | ○ continuity of earthing system in accordance with Clause 8.3.3 of AS/NZS 3000
label | ○ insulation resistance test of all field cables in accordance with Clause 8.3.3 of AS/NZS 3000 wiring rules
label | The following reports (VRS 730) completed and made available to the Superintendent:
label | ○ Electrical Test Report
label | ○ Insulation Resistance Test of All Field Cables
label | ○ Power Consumption Record
label | ○ Continunity Test Report
label | Flash Test is to be carried out. Once the flash test has been confirmed as acceptable, the site is to run with the lamps circuit breaker isolated for seven days to confirm correct operation of site
label | REFERENCE DOCUMENTS: 730.22
label | INSPECTION/TEST METHOD: Verify
label | RECORD OF CONFORMITY: All Electrical Reports Listed
label | HP
label | RESPONSIBILITY: Fulton Hogan Engineer/Superindentant
date | Date Completed:
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 6.2 - Provision of Power
label | FREQUENCY: All Electrical Works
label | ACCEPTANCE CRITERIA: The Contractor shall arrange for the submission of all necessary paperwork, inspections, payment of fees, etc., to obtain connection to mains supply.
label | ○ The Contractor shall advise the Superintendent when power is available at the site.
label | ○ The Contractor shall arrange for the issuing of the Certificate of Electrical Compliance and be responsible for the submission of all necessary paperwork, inspections, payment of fees, etc., to obtain connection of mains supply to the site.
label | REFERENCE DOCUMENTS: 730.22 (b)
label | INSPECTION/TEST METHOD: Verify
label | RECORD OF CONFORMITY: This ITP signed
label | HP*
label | RESPONSIBILITY: Fulton Hogan Engineer
date | Date Completed:
checkpoint | 6.2 - Traffic Signal Controller Installation
label | FREQUENCY:
label | ACCEPTANCE CRITERIA: The Traffic Signal Controller is to be installed as per 730.23 following the successful release of all Holdpoints in 6.1, as outlined in 730.23 (a) and (b).
label | REFERENCE DOCUMENTS: 730.23
label | INSPECTION/TEST METHOD: Verify
label | RECORD OF CONFORMITY: This ITP signed
label | IP
label | RESPONSIBILITY: Fulton Hogan Engineer
date | Date Completed:
checkpoint | 6.2 - As-constructed drawings
label | FREQUENCY: At completion of works
label | ACCEPTANCE CRITERIA: Installed location and depth of conduits, and location of pits and pedestals, shall be accurately recorded on as-constructed drawings.
label | REFERENCE DOCUMENTS: 733.24 (f)
label | INSPECTION/TEST METHOD: verify
label | RECORD OF CONFORMITY: Red-line mark-up
label | IP
label | RESPONSIBILITY: Fulton Hogan Engineer
date | Date Completed:
checkpoint | 6.3 - Comissioning
label | FREQUENCY: At completion of works
label | ACCEPTANCE CRITERIA: Prior to switching the signals on, ‘flash’ test of the installation carried out by the Contractor and controller installer, to ensure that each lantern is connected to the correct cable core. Flash test witnessed by the Superintendent and confirmed as acceptable.
label | ○ Comissioning Report (Post Switch on)
label | ○ Power Cunsumption Record (After Switch on)
label | REFERENCE DOCUMENTS: 730.24 (g)
label | INSPECTION/TEST METHOD: verify
label | RECORD OF CONFORMITY: This ITP signed off
label | HP
label | RESPONSIBILITY: Fulton Hogan Engineer
date | Date Completed:
holdpoint | AUTHORITY HOLDPOINT
checkpoint | The signature below verifies that this ITP has been completed in accordance with the FH’s Quality system Procedures and verifies lot compliance with specifications.
textbox | QAV - Print Name:
textbox | QAV - Position:
textbox | Fulton Hogan - Print Name:
textbox | Fulton Hogan - Position:
date | Work Completed On:
signoff | Add Signature