## Resources
Rich Type | Id | Warnings | type | name | values | prefix | postfix | Usage Count | User Addable | Template Name | Template Id
checklist-sectioned |  |  | checklist | LM-FOR-50-ITR- 303.5 Fire Detection Fit Off (V160421) |  |  |  |  | Yes | LM-FOR-50-ITR- 303.5 Fire Detection Fit Off (V160421) | 02276c0f-fe45-4753-ab89-2c8586ee6f5e
checkpoint-group |  |  | section | Fit-Off
checkpoint-status |  |  | checkpoint | Have all devices been installed in the correct position with no obstructions
checkpoint-status |  |  | checkpoint | Have all detectors been installed in the correct position and addressed
checkpoint-status |  |  | checkpoint | Have all input/output modules been installed in the correct position and addressed, with all enclosures sealed
checkpoint-status |  |  | checkpoint | Have all magnetic door holders been installed correctly
checkpoint-status |  |  | checkpoint | Have all input/output devices been installed and addressed for security fire trips
checkpoint-status |  |  | checkpoint | Have all input/output devices been installed and addressed for mechanical fire trips
checkpoint-status |  |  | checkpoint | Have all input/output devices been installed and addressed for AS 1668 Fan Controls
checkpoint-status |  |  | checkpoint | Have the ELV and LV segregation rules been applied as per AS/CAS 009 (including 90 degrees crossovers) – Double check to make sure no other trades have been in after fire works
checkpoint-status |  |  | checkpoint | Have all cables and conduits been installed in the correct position for devices
checkpoint-status |  |  | checkpoint | Have all devices been terminated for testing purposes
checkpoint-group |  |  | section | Cable Feeds
checkpoint-status |  |  | checkpoint | Have all cable feeds been connected to the first device
checkpoint-status |  |  | checkpoint | Have all cable feeds been connected to the last device
checkpoint-status |  |  | checkpoint | Have cable feeds been connected at the panel
checkpoint-group |  |  | section | Visual Check
checkpoint-status |  |  | checkpoint | Check that no other services are run with or attached to fire detection cables
checkpoint-status |  |  | checkpoint | Check that no cables have been damaged
checkpoint-status |  |  | checkpoint | Check that all final cable locations are correct and match up with the “For Construction Drawings” and “Reflected Ceiling Plans”
checkpoint-status |  |  | checkpoint | Check that all address tags and labels are clear and readable
checkpoint-status |  |  | checkpoint | Have devices and address been noted on “As Constructed Drawings” for handover
checkpoint-status |  |  | checkpoint | Have all stickers been installed to fire rated walls and smoke walls for penetrations
checkpoint-status |  |  | checkpoint | Has photographic evidence been taken and recorded for all penetrations?
checkpoint-group |  |  | section | Completion
checkpoint-status |  |  | checkpoint | Sign Off below - pass once complete
holdpoint |  |  | signoff | Sign-Off - click to Add signature(s)
checklist-sectioned |  |  | checklist | LM-FOR-40-ITR-302.1 Fire Pump Installation |  |  |  |  | Yes | LM-FOR-40-ITR-302.1 Fire Pump Installation | 106538fd-81dc-441e-ab63-4f384175babc
checkpoint-group |  |  | section | Installation
checkpoint-status |  |  | checkpoint | Pump installation arrangement including suction and discharge pipe works are in accordance with the approved drawing/plan
checkpoint-status |  |  | checkpoint | Pump clearance is 1000 mm on all four sides and 600 mm between pumps
checkpoint-status |  |  | checkpoint | Concrete plinth/foundation height is minimum 150 mm from FFL and 150 mm wider on all four sides of pump base
checkpoint-status |  |  | checkpoint | Pump base is sitting squarely and bolted down Vibration mounts are properly anchored on plinth or inertia plinth
checkpoint-status |  |  | checkpoint | Pump suction and discharge pipework are completely installed and connected Supports are adequately provided
checkpoint-status |  |  | checkpoint | Control panels installed and bolted down, MFB have clear access around pump controller 1000mm Arc
checkpoint-status |  |  | checkpoint | Suction isolation valve installed is OS & Y type
checkpoint-status |  |  | checkpoint | Non-return valve is installed and located upstream of the isolation valve in pump discharge line
checkpoint-status |  |  | checkpoint | Pump circulation-relief valve for electric driven pump is installed and piped to drain or tank return line
checkpoint-status |  |  | checkpoint | Heat exchanger cooling water harness for diesel driven pump is installed and piped to drain or tank return line
checkpoint-status |  |  | checkpoint | Pressure gauge with gauge cock is installed min 2Ø downstream of discharge flange or reducer
checkpoint-status |  |  | checkpoint | Pressure reductions installed on manifold x2 for each stage with M/V’s and Annubar for each stage
checkpoint-status |  |  | checkpoint | Exhaust connected to pump and installed to approved discharge location
checkpoint-status |  |  | checkpoint | Full tanks have been filled with Diesel; Electric Pumps AND Controls ready for energisation
checkpoint-group |  |  | section | Completion
checkpoint-status |  |  | checkpoint | Sign Off below - pass once complete
holdpoint |  |  | signoff | Sign-Off - click to Add signature(s)
checklist-flat |  |  | checklist | Pre-start checklist (V.090322) |  |  |  |  | Yes | Pre-start checklist (V.090322) | 13be8bae-2cea-4e44-9340-7f67381b0ba9
checkpoint-status |  |  | checkpoint | Latest consented drawings checked & referenced
text | 0000d4e3-6038-554c-814f-5836653e7612 |  | textbox | Drawing & Revision #
checkpoint-status |  |  | checkpoint | Area clear, tidy and accessible
label | 1bbfadcc-3be9-599b-91eb-af1e9f25bd36 |  | note | Attach Photos/Comments below if any issues & send report to Builder
checklist-sectioned |  |  | checklist | LM-FOR-40-ITR-302.5 Booster Assembly |  |  |  |  | Yes | LM-FOR-40-ITR-302.5 Booster Assembly | 1771c09b-c617-46b3-8dd1-aa1c6b689dc9
checkpoint-group |  |  | section | Installation
checkpoint-status |  |  | checkpoint | All pipework are installed in the correct position and alignment in accordance with the approved drawing/plan
checkpoint-status |  |  | checkpoint | All pipework have been pressure tested and accepted in accordance to approved pressure testing procedure
checkpoint-status |  |  | checkpoint | Fire Brigade Booster is located within sight of the main entrance to the building
checkpoint-status |  |  | checkpoint | Concrete plinth provided for the booster location and hard stand for fire brigade pumping appliance
checkpoint-status |  |  | checkpoint | Feed Hydrant is located within 8 metres from fire brigade appliance hard stand
checkpoint-status |  |  | checkpoint | Fire water storage tank suction point (Storz) is located within 4 metres from fire brigade appliance hard stand
checkpoint-status |  |  | checkpoint | Fire water storage tank suction point (Storz) is located within 10 metres from fire brigade booster inlet connection
checkpoint-status |  |  | checkpoint | Centre distance between feed hydrant and booster inlet connection is 450 mm minimum and 5 m maximum
checkpoint-status |  |  | checkpoint | The height of Feed Hydrant Outlet and Booster Inlet Connection is minimum 750 mm and maximum 1200 mm from FFL
checkpoint-status |  |  | checkpoint | Valves face minimum 150-mm from door and valve handles are 100-mm from cabinet sides
checkpoint-status |  |  | checkpoint | The number of feed hydrant outlet installed is equal to number of fire brigade booster assembly inlets
checkpoint-status |  |  | checkpoint | The required number of fire brigade booster inlets installed is suitable for the system requirement or minimum of 2 inlets
checkpoint-status |  |  | checkpoint | Full flow non-return valve of correct size is installed in the proper location
checkpoint-status |  |  | checkpoint | Approved type of cabinet enclosure is installed as required
checkpoint-group |  |  | section | Completion
checkpoint-status |  |  | checkpoint | Sign Off below - pass once complete
holdpoint |  |  | signoff | Sign-Off - click to Add signature(s)
checklist-sectioned |  |  | checklist | LM-FOR-50-ITR-303.2 Ewis Installation |  |  |  |  | Yes | LM-FOR-50-ITR-303.2 Ewis Installation | 1f96bf87-83eb-46de-9265-38dd220fb47e
checkpoint-group |  |  | section | Cabling
checkpoint-status |  |  | checkpoint | Have all cable supports been installed in the correct position with no obstructions
checkpoint-status |  |  | checkpoint | Have all cables been cable tied to soffit / catenary wire with no sagging or obstructions
checkpoint-status |  |  | checkpoint | Have all cables been installed for speakers and horns
checkpoint-status |  |  | checkpoint | Have all cables been installed for warden intercom points
checkpoint-status |  |  | checkpoint | Have all cables been installed for emergency call points
checkpoint-status |  |  | checkpoint | Have all cables been installed for strobes
checkpoint-status |  |  | checkpoint | Have all cables been installed for background music inputs
checkpoint-status |  |  | checkpoint | Have all cables been installed for microphone inputs
checkpoint-status |  |  | checkpoint | Have the ELV and LV segregation rules been applied as per AS/CAS 009 (including 90 degrees crossovers)
checkpoint-status |  |  | checkpoint | Have all cables been installed in the correct position for devices
checkpoint-status |  |  | checkpoint | Have all cables been joined through for testing purposes or fitted with end of line devices
checkpoint-group |  |  | section | Cable Feeds
checkpoint-status |  |  | checkpoint | Have all cable supports been installed in the correct position with no obstructions
checkpoint-status |  |  | checkpoint | Have all cable feeds been installed in the correct position
checkpoint-status |  |  | checkpoint | Have all cables been tied to cable tray with steel ties with no sagging or obstructions
checkpoint-status |  |  | checkpoint | Have all cable trays been installed correctly and secured including joiners and bends
checkpoint-status |  |  | checkpoint | Have the modified cable trays been re-galvanized
checkpoint-group |  |  | section | Visual Check
checkpoint-status |  |  | checkpoint | Check that no other services are run with or attached to occupant/emergency warning cables
checkpoint-status |  |  | checkpoint | Check that no cables have been damaged
checkpoint-status |  |  | checkpoint | Check that all final cable locations are correct and match up with the “For Construction Drawings” and “Reflected Ceiling Plans”
checkpoint-status |  |  | checkpoint | Have all cable runs, cable trays and penetrations been mark on “As Constructed Drawings” for handover
checkpoint-status |  |  | checkpoint | Have all stickers been installed to fire rated walls and smoke walls for penetrations
checkpoint-status |  |  | checkpoint | Has photographic evidence been taken and recorded for all penetrations
checkpoint-group |  |  | section | Completion
checkpoint-status |  |  | checkpoint | Sign Off below - pass once complete
holdpoint |  |  | signoff | Sign-Off - click to Add signature(s)
checklist-sectioned |  |  | checklist | LM-FOR-50-ITR-303.3 Ewis Installation Fit Off |  |  |  |  | Yes | LM-FOR-50-ITR-303.3 Ewis Installation Fit Off | 21ded893-f6c2-4d9b-9fbf-5a475bd3aa01
checkpoint-group |  |  | section | EWIS Fit-Off
checkpoint-status |  |  | checkpoint | Have all devices been installed in the correct position with no obstructions
checkpoint-status |  |  | checkpoint | Have all speakers / horns been installed in the correct location
checkpoint-status |  |  | checkpoint | Have all warden intercom points been installed in the correct location
checkpoint-status |  |  | checkpoint | Have all emergency call points been installed in the correct location
checkpoint-status |  |  | checkpoint | Have all strobes been installed in the correct location
checkpoint-status |  |  | checkpoint | Have all background music points been installed in the correct location
checkpoint-status |  |  | checkpoint | Have all microphone points been installed in the correct location
checkpoint-status |  |  | checkpoint | Have the ELV and LV segregation rules been applied as per AS/CAS 009 (including 90 degrees crossovers) – Double check to make sure no other trades have been in after warning system works
checkpoint-status |  |  | checkpoint | Have all cables and conduits been installed in the correct position for devices
checkpoint-status |  |  | checkpoint | Have all devices been terminated for testing purposes
checkpoint-group |  |  | section | Cable Feeds
checkpoint-status |  |  | checkpoint | Have all cable supports been connected to the first device
checkpoint-status |  |  | checkpoint | Have all end of lines been fitted and measured
checkpoint-status |  |  | checkpoint | Have cables feeds been connected at the panel
checkpoint-group |  |  | section | Visual Check
checkpoint-status |  |  | checkpoint | Check that no other services are run with or attached to occupant/emergency warning cables or devices
checkpoint-status |  |  | checkpoint | Check that no cables or devices have been damaged
checkpoint-status |  |  | checkpoint | Check that all final device locations are correct and match up with the “For Construction Drawings” and “Reflected Ceiling Plans”
checkpoint-status |  |  | checkpoint | Have devices and readings been noted on “As Constructed Drawings” for handover
checkpoint-status |  |  | checkpoint | Have all stickers been installed to fire rated walls and smoke walls for penetrations
checkpoint-status |  |  | checkpoint | Has photographic evidence been taken and recorded for all penetrations
checkpoint-group |  |  | section | Completion
checkpoint-status |  |  | checkpoint | Sign Off below - pass once complete
holdpoint |  |  | signoff | Sign-Off - click to Add signature(s)
checklist-sectioned |  |  | checklist | LM-FOR-50-ITR-303.1 Fire Panel Installation |  |  |  |  | Yes | LM-FOR-50-ITR-303.1 Fire Panel Installation | 2c4a3cfd-24be-4f7e-b2a0-130c6d5d032f
checkpoint-group |  |  | section | Fire Indicator Panel
checkpoint-status |  |  | checkpoint | Are visual indicators and controls not less than 750 mm from the floor
checkpoint-status |  |  | checkpoint | Are visual indicators and controls not more than 1850 mm from the floor
checkpoint-status |  |  | checkpoint | Connected to Brigade - Is the fire indicator panel clearly visible and readily accessible within the designated building entry point or the fire control room
checkpoint-status |  |  | checkpoint | Not Connected to Brigade - Is the fire indicator panel in a secure location and clearly visible and readily accessible to authorized personnel
checkpoint-group |  |  | section | Accessibility
checkpoint-status |  |  | checkpoint | Is the fire indicator panel obscured by a door (if No, continue to CLEARANCE)
checkpoint-status |  |  | checkpoint | Is the door marked in a contrasting colour to the general colour scheme with the words “FIRE PANEL” in letters not less than 50mm high
checkpoint-status |  |  | checkpoint | Is the door absent of locks
checkpoint-status |  |  | checkpoint | Where the door reduces the CIE sounder sound level below the CIE requirement, means are provided to give the required sound level outside the covering door
checkpoint-status |  |  | checkpoint | A minimum clearance is maintained from the enclosure as shown
checkpoint-group |  |  | section | Power sources
checkpoint-status |  |  | checkpoint | Is the battery enclosure located such that the batteries are readily accessible for inspection
checkpoint-status |  |  | checkpoint | Are the connecting leads to the battery clearly labelled to reduce the possibility of reverse connections to the battery
checkpoint-status |  |  | checkpoint | The battery is not be tapped for intermediate voltages
checkpoint-status |  |  | checkpoint | All connections are made using suitable connectors
checkpoint-group |  |  | section | Sub-Indicator Panels
checkpoint-status |  |  | checkpoint | The SIP shall only serve areas on one level of a building unless - Pass once below considered
button | 3ec02f27-e02d-5942-8070-d7afa333c27e |  | button | (a) The SIP serves the entire building | Yes,No
button | ba5e7a2b-8568-5f72-8833-4ae1a57695a1 |  | button | (b) All zones connected to the SIP are readily accessible without leaving the area served by the SIP; or | Yes,No
button | 67380757-2078-539d-b5e5-2ccb0f28fcdf |  | button | (c) The location of each zone in alarm at the SIP can be identified at the designated building entry point | Yes,No
button | 0323f668-0b1e-5ccc-bf2d-6ed3af5d6607 |  | button | Where the SIP serves the entire building, it shall be installed in accordance with the requirements for an FIP | Yes,No
button | 03abd06e-5016-5d56-9f86-a44768ffd838 |  | button | If the SIP serves a specific area, is it located at the main point of entry into that area | Yes,No
checkpoint-group |  |  | section | Wiring
checkpoint-status |  |  | checkpoint | The extra low voltage wiring of the fire detection and alarm system is be kept separate and distinct from all other systems
checkpoint-status |  |  | checkpoint | The extra low voltage wiring of the fire detection and alarm system is installed in accordance with the requirements of AS/ACIF S009
checkpoint-status |  |  | checkpoint | Other wiring is installed in accordance with the electrical safety requirements of AS/NZS
checkpoint-status |  |  | checkpoint | Externally energized circuits at voltages in excess of extra low voltage, except the power source for CIE, do not enter any CIE enclosure
checkpoint-group |  |  | section | Completion
checkpoint-status |  |  | checkpoint | Sign Off below - pass once complete
holdpoint |  |  | signoff | Sign-Off - click to Add signature(s)
checklist-sectioned |  |  | checklist | LM-FOR-50-ITR-303.4 Fire Detection Installation |  |  |  |  | Yes | LM-FOR-50-ITR-303.4 Fire Detection Installation | 43376474-0b7e-4779-9142-6f098af4d51e
checkpoint-group |  |  | section | Cabling
checkpoint-status |  |  | checkpoint | Have all cable supports been installed in the correct position with no obstructions
checkpoint-status |  |  | checkpoint | Have all cables been cable tied to soffit / catenary wire with no sagging or obstructions
checkpoint-status |  |  | checkpoint | Have all cables been installed for detectors
checkpoint-status |  |  | checkpoint | Have all cables been installed for sprinkler valve sets
checkpoint-status |  |  | checkpoint | Have all cables been installed for magnetic door holders
checkpoint-status |  |  | checkpoint | Have all cables been installed for security fire trips
checkpoint-status |  |  | checkpoint | Have all cables been installed for mechanical fire trips
checkpoint-status |  |  | checkpoint | Have all cables been installed for AS 1668 Fan Controls
checkpoint-status |  |  | checkpoint | Have the ELV and LV segregation rules been applied as per AS/CAS 009 (including 90 degrees crossovers)
checkpoint-status |  |  | checkpoint | Have all cables been installed in the correct position for devices
checkpoint-status |  |  | checkpoint | Have all cables been joined through for testing purposes
checkpoint-group |  |  | section | Cable Feeds
checkpoint-status |  |  | checkpoint | Have all cable supports been installed in the correct position with no obstructions
checkpoint-status |  |  | checkpoint | Have all cable feeds been installed in the correct position
checkpoint-status |  |  | checkpoint | Have all cables been tied to cable tray with steel ties with no sagging or obstructions
checkpoint-status |  |  | checkpoint | Have all cable trays been installed correctly and secured including joiners and bends
checkpoint-status |  |  | checkpoint | Have the modified cable trays been re-galvanized
checkpoint-group |  |  | section | Visual Check
checkpoint-status |  |  | checkpoint | Check that no other services are run with or attached to fire detection cables
checkpoint-status |  |  | checkpoint | Check that no cables have been damaged
checkpoint-status |  |  | checkpoint | Check that all final cable locations are correct and match up with the “For Construction Drawings” and “Reflected Ceiling Plans”
checkpoint-status |  |  | checkpoint | Have all cable runs, cable trays and penetrations been mark on “As Constructed Drawings” for handover
checkpoint-status |  |  | checkpoint | Have all stickers been installed to fire rated walls and smoke walls for penetrations
checkpoint-status |  |  | checkpoint | Has photographic evidence been taken and recorded for all penetrations?
checkpoint-group |  |  | section | Completion
checkpoint-status |  |  | checkpoint | Sign Off below - pass once complete
holdpoint |  |  | signoff | Sign-Off - click to Add signature(s)
checklist-flat |  |  | checklist | Site Diary |  |  |  |  | Yes | Add Site Diary Checklist | 5194f6c2-9695-4b35-a8f6-579d757a342e
checkpoint-status |  |  | checkpoint | Areas of work accessible for the day
select | e048d81c-b120-5201-90b9-737dc818e2c4 |  | dropdown | Day | Friday, Saturday, Sunday, Thursday, Tuesday, Wednesday,Monday
text | 8b06ec40-8a3c-5890-8eef-2138d0007662 |  | textbox | Date
text | 220bbcf8-26f5-50d0-8333-a92a92c45817 |  | textbox | Year
text | 2ee2d4ff-2e7a-5a32-abbd-16864834758c |  | textbox | Number of workers on site
text | f718a78d-8c75-581f-8ecc-f206357c4ca1 |  | textbox | HSR on site today enter name
text | 67e1eae6-6cc5-54f1-9e71-af2e0d4466a4 |  | textbox | First Aider on site today enter name
text | 300a822f-3c8d-5eb4-ace2-997e233cf07a |  | textbox | Injury on site today enter name
checkpoint-status |  |  | checkpoint | Work area 1 details entered
text | 47c51389-20da-5ede-8014-b3d862ef3eaa |  | textbox | Area
select | be2d3209-4753-5610-ab16-ae8739025b3a |  | dropdown | Task | Cores, Deck, Footings G/Slab, Framing, Other, Setdown, Stripping, Upstand, Walls,Columns
text | 8e3893b8-ed2f-5026-a09c-93c5cb077f2f |  | textbox | Comments
checkpoint-no-status |  |  | checkpoint | Work area 2 details entered
text | c3bf60c1-b562-5b80-a516-8f9ebd4704ed |  | textbox | Area
select | 4be3a27e-4b3d-586a-b513-ceb15fc40bfe |  | dropdown | Task | Cores, Deck, Footings G/Slab, Framing, Other, Setdown, Stripping, Upstand, Walls,Columns
text | c2b720eb-8138-59ab-8725-672f980b9236 |  | textbox | Comments
checkpoint-no-status |  |  | checkpoint | Work area 3 details entered
text | 67ba33fd-a2e8-519a-9718-9602c1c22c34 |  | textbox | Area
select | d67e8a5c-0701-5122-8469-a3f875979c90 |  | dropdown | Task | Cores, Deck, Footings G/Slab, Framing, Other, Setdown, Stripping, Upstand, Walls,Columns
text | e0c6f448-ea66-5571-ab37-d4e5b00d7eba |  | textbox | Comments
checkpoint-no-status |  |  | checkpoint | Work area 4 details entered
text | a65ca3a0-57ef-5fca-9a21-6c58979e77b1 |  | textbox | Area
select | 228c593c-8c7b-556a-a358-a302692731ee |  | dropdown | Task | Cores, Deck, Footings G/Slab, Framing, Other, Setdown, Stripping, Upstand, Walls,Columns
text | be73872c-40d0-5fe1-95e7-28fc71abd66b |  | textbox | Comments
checkpoint-no-status |  |  | checkpoint | Work area 5 details entered
text | 5c62749c-d156-5f1a-a0db-c1bfbf345bbe |  | textbox | Area
select | fb2b9525-bedc-5e79-8595-7d9e44168dbe |  | dropdown | Task | Cores, Deck, Footings G/Slab, Framing, Other, Setdown, Stripping, Upstand, Walls,Columns
text | 0f36562c-85d2-5c15-b10e-0e0351ca42a0 |  | textbox | Comments
checkpoint-no-status |  |  | checkpoint | Work area 6 details entered
text | df45fc36-050d-52a7-b4de-4c3dfd8b7dc1 |  | textbox | Area
select | ce639f3d-bbb2-5e33-bfa7-831d0f7f3ce4 |  | dropdown | Task | Cores, Deck, Footings G/Slab, Framing, Other, Setdown, Stripping, Upstand, Walls,Columns
text | 7a39984c-f43a-5db8-bbb8-67cb3b46d3ad |  | textbox | Comments
checkpoint-no-status |  |  | checkpoint | Work area 7 details entered
text | f56b01be-ce67-517e-9201-21fbb9da80c2 |  | textbox | Area
select | cd1edc93-5190-52b7-8b91-cd4940a807f6 |  | dropdown | Task | Cores, Deck, Footings G/Slab, Framing, Other, Setdown, Stripping, Upstand, Walls,Columns
text | 0ce609f8-0e23-570c-84bf-8d4ab1c5a902 |  | textbox | Other
checkpoint-no-status |  |  | checkpoint | Work area 8 details entered
text | 87fec433-1b39-5b0c-85ab-47b3724894e7 |  | textbox | Area
select | 497f30d6-7d3e-567a-9fde-26ab4d0ca912 |  | dropdown | Task | Cores, Deck, Footings G/Slab, Framing, Other, Setdown, Stripping, Upstand, Walls,Columns
text | 64afa6dd-5e29-541b-8f7a-b3eefebb69ef |  | textbox | Comments
checkpoint-no-status |  |  | checkpoint | Weather conditions entered
select | e4a9dd83-8a46-5d40-9016-ecdf1143b19f |  | dropdown | Conditions: | Hot, Overcast, Rain, Showers, Windy,Fine
text | c4eca12e-6581-575e-a282-008a28f85230 |  | textbox | Min temp predicted
text | 9f6d3c08-4655-5cb2-a2ec-d500dc6aaf2c |  | textbox | Max temp predicted
checkpoint-no-status |  |  | checkpoint | Delays from inclemency
text | f4baf749-c7b9-5264-82f9-225bad01bac5 |  | textbox | Total Hours of delay
select | c7cb66ed-53d5-5a5a-8876-a70cef304006 |  | dropdown | Conditions: | , Heat, Other trades, Windy,Rain
checkpoint-no-status |  |  | checkpoint | Delays from Builders or Others
text | afcd53cc-c4ba-599f-8ce0-c3160cb74e57 |  | textbox | Total Hours of delay
select | c19fccf4-46f7-5cda-af3d-ffd8ba800343 |  | dropdown | Conditions: | Concreter, Crane, Earthworks, Other, PT, Safety, Scaffold, Steel fixer, Union,Builder
checkpoint-status |  |  | checkpoint | Attach Specific site photos for respective day
checklist-sectioned |  |  | checklist | LM-FOR-30-ITR-301.1 Sprinkler Control Valve |  |  |  |  | Yes | LM-FOR-30-ITR-301.1 Sprinkler Control Valve | 77272084-d45b-43ee-8951-bbba941ab6d1
checkpoint-group |  |  | section | Installation
checkpoint-status |  |  | checkpoint | Supply and Installation pipe works are installed in the correct position and alignment in accordance with the approved drawing/plan
checkpoint-status |  |  | checkpoint | All supports are completely installed, spaced and bolted down box / assembly secured
checkpoint-status |  |  | checkpoint | All roll grooved couplings / flanges are properly tightened
checkpoint-status |  |  | checkpoint | Valve station drain is properly connected to risers drain and building hydraulic drainage
checkpoint-status |  |  | checkpoint | Approved type of Monitored Main Stop Valve is fitted and operational
checkpoint-status |  |  | checkpoint | All specific signage is installed lock shut / lock open including FSV number of M/V’s
checkpoint-status |  |  | checkpoint | Correct size and range of supply and installation pressure gauges with shut-off cocks are fitted
checkpoint-status |  |  | checkpoint | Correct type solenoid, flow switch, couplings etc installed
checkpoint-status |  |  | checkpoint | Correct size and range of supply and installation pressure gauges with shut-off cocks are fitted
checkpoint-status |  |  | checkpoint | Confirm GFA on solenoid activation/ flow switch/ MV activation
checkpoint-status |  |  | checkpoint | Control Valve is positioned between 1150mm to 1800mm
checkpoint-group |  |  | section | Completion
checkpoint-status |  |  | checkpoint | Sign Off below - pass once complete
holdpoint |  |  | signoff | Sign-Off - click to Add signature(s)
checklist-sectioned |  |  | checklist | LM-FOR-40-ITR-302.2 Hydrant Installation |  |  |  |  | Yes | LM-FOR-40-ITR-302.2 Hydrant Installation | 7a9e4256-0b00-4d7b-9597-7743be5d70f7
checkpoint-group |  |  | section | Installation
checkpoint-status |  |  | checkpoint | Hydrant supply pipe works completely installed of correct size, position, elevation, alignment and adequately supported in accordance with approved drawing/plan
text | 1322c22e-dbda-5264-9cbe-dd35cf31e109 |  | textbox | Hydrant No.
checkpoint-status |  |  | checkpoint | Hydrostatic pressure testing of installed supply pipe works completed and accepted
checkpoint-status |  |  | checkpoint | Hydrant valves and associated pipes and fittings used are in accordance with the approved specifications and applicable codes/standards
checkpoint-status |  |  | checkpoint | Fire Hydrant and associated fire water main isolation valves locations are in accordance with the approved drawing/plan
checkpoint-status |  |  | checkpoint | Hydrants stand pipe is adequately supported and bolted down. Concrete surround block provided for external hydrant
checkpoint-status |  |  | checkpoint | Hydrant valve is between 750 to 1200 mm from finish floor/grade level
checkpoint-status |  |  | checkpoint | Valve outlet is facing away from the wall and not more than 35O below its horizontal axis. Minimum 300 mm clearance around the valve outlet
checkpoint-status |  |  | checkpoint | Minimum 1000 mm clear space in front of valve outlet is provided
checkpoint-status |  |  | checkpoint | Valve handwheel clearance is minimum 100 mm clear of any obstruction at fully open
checkpoint-group |  |  | section | Completion
checkpoint-status |  |  | checkpoint | Sign Off below - pass once complete
holdpoint |  |  | signoff | Sign-Off - click to Add signature(s)
checklist-flat |  |  | checklist | Document Attachment ITP (V.220421) |  |  |  |  | Yes | Document Attachment ITP (V.220421) | 815f0fca-b8ec-40c0-a042-52cbe11255fb
checkpoint-status |  |  | checkpoint | Documents/Drawings attached for reference - Pass once attached
checklist-flat |  |  | checklist | Additional Tasks Checklist |  |  |  |  | Yes | Additional Tasks Checklist | 82c9a56f-b6cf-480a-8a54-ef8a5ee12e27
checkpoint-status |  |  | checkpoint | Details of additional tasks - comment below
checklist-sectioned |  |  | checklist | LM-FOR-30-ITR-301 Sprinkler Installation/Fitoff |  |  |  |  | Yes | LM-FOR-30-ITR-301 Sprinkler Installation/Fitoff | 8cb92c61-3ece-4859-97cb-c61978110c5f
checkpoint-group |  |  | section | Sprinkler Rough-In
checkpoint-status |  |  | checkpoint | Supports spacing & fixing as per AS2118
checkpoint-status |  |  | checkpoint | Pipework installed as per drawings
checkpoint-status |  |  | checkpoint | Concealed space sprinklers installed
checkpoint-status |  |  | checkpoint | All ends blanked off/plugged for testing
checkpoint-status |  |  | checkpoint | Pipes left out
label | 695bdd5c-ae3c-5040-9fc6-e47510cdf100 |  | note | Fail=Missing, Pass=Complete
button | 5f07c099-7c3b-5a11-993c-557bf6319ce6 |  | button | Pipes left out - installed | Yes,No
checkpoint-group |  |  | section | Sprinkler Fit-Off
checkpoint-status |  |  | checkpoint | Ceiling grid levelled
checkpoint-status |  |  | checkpoint | Sprinklers installed as per drawings
checkpoint-status |  |  | checkpoint | Sprinkler Type & temperature as per drawings
checkpoint-status |  |  | checkpoint | All escutcheon plates installed
checkpoint-status |  |  | checkpoint | Areas not fitted-off
label | 4ca7fdbd-99b8-5ec4-8e67-779a859b64e2 |  | note | Fail=Missing, Pass=Complete
button | 48aa11be-f4fe-5946-8113-ec6365663187 |  | button | Areas not fitted-off - completed | Yes,No
checkpoint-status |  |  | checkpoint | Client Sign Off Sheets Complete
checkpoint-status |  |  | checkpoint | Painting carried out
checkpoint-status |  |  | checkpoint | Pressure Tested (refer ITR 401) - Completed
checkpoint-group |  |  | section | Completion
checkpoint-status |  |  | checkpoint | Sign Off below - pass once complete
holdpoint |  |  | signoff | Sign-Off - click to Add signature(s)
checklist-sectioned |  |  | checklist | LM-FOR-40-ITR-302.3 Hose Reel Installation |  |  |  |  | Yes | LM-FOR-40-ITR-302.3 Hose Reel Installation | 9f416460-bcd5-42bd-9ee3-78dd0ffb15fd
checkpoint-group |  |  | section | Installation
checkpoint-status |  |  | checkpoint | Hose Reel supply pipe works completely installed of correct size, position, elevation, alignment and adequately supported in accordance with approved drawing/plans
text | 089c20e9-258e-5eae-accd-41e403fbecd9 |  | textbox | Hose Reel No.
checkpoint-status |  |  | checkpoint | Hydrostatic pressure testing of installed pipe works completed and accepted
checkpoint-status |  |  | checkpoint | Hose Reel and associated valves, pipes and fitting used are in accordance with the approved specifications and applicable codes/standards
checkpoint-status |  |  | checkpoint | Hose Reel located along normal path of travel to nearest exit and readily accessible
checkpoint-status |  |  | checkpoint | Verify and confirm hose length to be 36-metres or 40-meters
checkpoint-status |  |  | checkpoint | Hose reel spindle is 1400 mm minimum to 2400 mm maximum above floor level. Stop valve is 1000 + 100 mm above floor level
checkpoint-status |  |  | checkpoint | Minimum radial clearance of 100 mm between the reel rim and cabinet/cavity to the sides, above and below
checkpoint-status |  |  | checkpoint | Minimum 100 mm clearance around the stop valve handwheel/handle
checkpoint-status |  |  | checkpoint | Any defects found on the hose reel assembly have been corrected
checkpoint-group |  |  | section | Completion
checkpoint-status |  |  | checkpoint | Sign Off below - pass once complete
holdpoint |  |  | signoff | Sign-Off - click to Add signature(s)
checklist-flat |  |  | checklist | Variation |  |  |  |  | Yes | Variation | a659d88b-5c37-4e63-9e98-cff636986adb
checkpoint-status |  |  | checkpoint | Variation Details Complete (Pass once inputted)
text | 0cf51977-6d75-5af4-a97d-fbb55832298b |  | textbox | Variation Name
text | 456c7393-3d47-5f94-96fe-dde149bcdf48 |  | textbox | Variation Description
text | 83b89ec8-1776-5044-a934-f4d09f4b1d81 |  | textbox | Materials & labour breakdown (Names, Hours & Material(s)/Quantities)
text | ec2054e7-1c8c-5337-b42c-32593298a0a6 |  | textbox | Acknowledgement
text | f1d0cdfe-486c-57f8-ab76-60e4a40d8048 |  | textbox | Signature/Reference Mail
checkpoint-status |  |  | checkpoint | Photo(s)
checkpoint-status |  |  | checkpoint | Supporting Documentation (Attached or Referenced)
checkpoint-status |  |  | checkpoint | Variation Sign-Off - Click to Add signatures below
button | 64723357-e840-5990-b650-f9868a197067 |  | button | Leemark Representative Signature Added below | Yes, No
button | 678e2a6c-2c78-56d9-a89f-7bfd9a7761c0 |  | button | Builder Representative Signature Added below | Yes, No
holdpoint |  |  | signoff | Click to Add Signatures
checklist-sectioned |  |  | checklist | LM-FOR-30-ITR-301.2 Alarm Control Valve |  |  |  |  | Yes | LM-FOR-30-ITR-301.2 Alarm Control Valve | d254aeca-edf8-4226-b6ea-d44f06f51fc5
checkpoint-group |  |  | section | Installation
checkpoint-status |  |  | checkpoint | Supply and Installation pipe works are installed in the correct position and alignment in accordance with the approved drawing/plan
checkpoint-status |  |  | checkpoint | All supports are completely installed, spaced and bolted down
checkpoint-status |  |  | checkpoint | All roll grooved couplings / flanges are properly tightened
checkpoint-status |  |  | checkpoint | Correct size and specification of Alarm Valve is installed in accordance with the approved drawing/plan
checkpoint-status |  |  | checkpoint | Approved type of Monitored Main Stop Valve is fitted and operational
checkpoint-status |  |  | checkpoint | Correct size of alarm line is installed, adequately supported and alarm gong is properly piped to drain
checkpoint-status |  |  | checkpoint | Correct size of orifice is fitted and piped to drain when system is with retard chamber
checkpoint-status |  |  | checkpoint | Main waste & test valve is fitted and piped to drain
checkpoint-status |  |  | checkpoint | Correct type and model of Direct Brigade Alarm device is fitted
checkpoint-status |  |  | checkpoint | Correct model and range of Pressure Switch is fitted
checkpoint-status |  |  | checkpoint | Correct size and range of supply and installation pressure gauges with shut-off cocks are fitted
checkpoint-status |  |  | checkpoint | All signalling devices (Monitored Stop Valve, DBA, Low Pressure Switch), are wired back to FIP
checkpoint-status |  |  | checkpoint | Control Valve associated pipe works paint touch-up repair is completed
checkpoint-group |  |  | section | Completion
checkpoint-status |  |  | checkpoint | Sign Off below - pass once complete
holdpoint |  |  | signoff | Sign-Off - click to Add signature(s)
checklist-sectioned |  |  | checklist | LM-FOR-33-ITR-401 Sprinkler & Hydrant hydrostatic test |  |  |  |  | Yes | LM-FOR-33-ITR-401 Sprinkler & Hydrant hydrostatic test | d88b88a0-d3c9-46f8-8dca-0801115113f3
checkpoint-group |  |  | section | Guidelines
checkpoint-status |  |  | checkpoint | Guidelines understood - Pass once read
label | 38061bc4-7161-5727-9ca2-f81cbbbecd3c |  | note | Guidelines: Fire Sprinkler Systems – 1600 kPa or 400 kPa above the maximum static pressure for a duration of 2 hours (Check notes on Construction Drawing for nominated test pressure)
label | 8b58d25e-2536-595f-b186-492314e05d90 |  | note | Fire Hydrant Systems (Low Rise) – 1700 kPa or 1.5 times the design pressure for a duration of 2 hours (Check notes on Construction Drawing for nominated test pressure)
label | 94d66f46-cedd-56da-ba60-547939955f67 |  | note | Playhouse Theatre – 1200 kPa or 1.5 times the design pressure for a duration of 2 hours. (Check notes on Construction Drawing for nominated test pressure)
checkpoint-group |  |  | section | Rough In Only OR Rough In & Fit Off Together
checkpoint-status |  |  | checkpoint | First Sighting - Pass once entered - attach photo of pressure gauge and builder sign off if required
checkpoint-status |  |  | checkpoint | Second Sighting - Pass once entered - attach photo of pressure gauge and builder sign off if required
checkpoint-group |  |  | section | Fit Off (if required ie if not covered by the above section)
checkpoint-status |  |  | checkpoint | Subsequent Sighting - Pass once entered - attach photo of pressure gauge and builder sign off if required
checklist-flat |  |  | checklist | Additional Tasks - add as required |  |  |  |  | Yes | Additional Tasks - add as required | dcdf0275-dc3f-4263-878a-aa81f9eb97a3
checkpoint-status |  |  | checkpoint | Details of additional tasks - comment below
checklist-sectioned |  |  | checklist | LM-FOR-40-ITR-302.4 Tank Installation |  |  |  |  | Yes | LM-FOR-40-ITR-302.4 Tank Installation | f13d8ebc-dd9c-48b2-858a-31df0312b8a2
checkpoint-group |  |  | section | Installation
checkpoint-status |  |  | checkpoint | Tank installation/construction is completed including associated pipe works in accordance with the approved drawing/plan
checkpoint-status |  |  | checkpoint | Tank is free from dents, buckling, cracks, and internal is clean and free of any debris and construction materials
checkpoint-status |  |  | checkpoint | Tank internal liner (if provided) is complete and properly bonded to tank wall/shell
checkpoint-status |  |  | checkpoint | Tank quick infill line including associated infill valve and isolation valve installed and adequately supported
checkpoint-status |  |  | checkpoint | Tank suction isolation valve is fitted in the correct position and operational in accordance with the approved drawing/plan
checkpoint-status |  |  | checkpoint | Tank suction vortex inhibitor is fitted in the correct position and elevation in accordance with the approved drawing/plan
checkpoint-status |  |  | checkpoint | Tank overflow is fitted in the correct position, elevation and properly piped to drain Adequate drain available
checkpoint-status |  |  | checkpoint | Tank drain/sludge isolation valve is fitted and blank off
checkpoint-status |  |  | checkpoint | Tank external water level indicator is fitted and operational
checkpoint-status |  |  | checkpoint | Tank internal and external access ladders are fitted & secured
checkpoint-status |  |  | checkpoint | Tank access hatch is fitted and provided with lockable cover
checkpoint-status |  |  | checkpoint | Ball float for infill pilot line is fixed tightly, close to the manhole and away from the discharge path of tank infill
checkpoint-status |  |  | checkpoint | Tank is located with minimum of 600 mm clearance around tank perimeter and roof line
checkpoint-group |  |  | section | Completion
checkpoint-status |  |  | checkpoint | Sign Off below - pass once complete
holdpoint |  |  | signoff | Sign-Off - click to Add signature(s)