## Resources
Rich Type | Id | Warnings | type | name | values | prefix | postfix | Usage Count | User Addable | Template Name | Template Id
checklist-flat |  |  | checklist | Additional Tasks - add as required |  |  |  |  | Yes | Additional Tasks - add as required | 3698277c-cacf-47cd-820d-858ab2a21f58
checkpoint-status |  |  | checkpoint | Details of additional tasks - comment below
checklist-flat |  |  | checklist | wet fire ITP |  |  |  |  | Yes | wet fire ITP | 645d3c3e-3289-444a-94f7-518453d22efd
checkpoint-status |  |  | checkpoint | Are all sprinklers installed clear of obstructions as per AS2118.4(2012) Clause 4.4.3.2?
checkpoint-status |  |  | checkpoint | Have sprinkler spares been left in cabinet including a sprinkler key, if new install? INSERT PHOTO
checkpoint-status |  |  | checkpoint | Have the valves been labelled inside the SCV? INSERT PHOTO
checkpoint-status |  |  | checkpoint | Has the Sprinkler Block Plan been laminated and stuck on to the inside of the SCV cabinet? INSERT PHOTO
checkpoint-status |  |  | checkpoint | Has the Water Tapping been connected to the SCV? INSERT PHOTO OF PRESSURE GAUGE
checkpoint-status |  |  | checkpoint | Has the Water Tapping Cage been installed? INSERT PHOTO
checkpoint-status |  |  | checkpoint | Has a Flow Test been conducted and recorded?
checkpoint-status |  |  | checkpoint | Has the remote test valve been installed as per our shop drawing and labelled? INSERT PHOTO
checkpoint-status |  |  | checkpoint | Have sprinklers been installed with guards if exposed? INSERT PHOTO
checkpoint-status |  |  | checkpoint | Has a Hydrostatic test record been completed and recorded? 1600kPA min 2 Hours INSERT PHOTO OF PRESSURE GAUGE
checkpoint-status |  |  | checkpoint | Do the As-Installed conditions on site reflect the Shop Drawings
checklist-flat |  |  | checklist | dry fire ITP |  |  |  |  | Yes | dry fire ITP | 9da79649-e18e-4c34-89cf-7e86b3c76e19
checkpoint-status |  |  | checkpoint | Does the Emergency Lighting system operate manually and automatically via the RFP? RECORD VIDEO OF OPERATION
checkpoint-status |  |  | checkpoint | Have all cables been cable tied to roof trusses / catenary wire with no sagging or obstructions? INSERT PHOTO
checkpoint-status |  |  | checkpoint | Have all Smoke Alarms been installed in bedrooms within 3m of bedhead? INSERT PHOTO
checkpoint-status |  |  | checkpoint | Have all cables been installed for sprinkler valve sets and mechanically fixed inside cabinet? INSERT PHOTO
checkpoint-status |  |  | checkpoint | Have all cables been installed for Door Strikes and tested to ensure correct operation on Smoke Detector & Sprinkler Alarm?
checkpoint-status |  |  | checkpoint | Does the main entry strobe operate on Smoke Detector & Sprinkler Alarms? RECORD VIDEO OF OPERATION
checkpoint-status |  |  | checkpoint | Do the audible alarms ring independently when the relative SCV is operated for that property? RECORD VIDEO OF OPERATION
checkpoint-status |  |  | checkpoint | If ASE is installed, does the ASE only trigger upon receival of all Sprinkler Alarms and not on Smoke Detection?
checkpoint-status |  |  | checkpoint | Does the Heating System shut down on activation of smoke detector or sprinkler and operate manually via RFP? RECORD VIDEO OF OPERATION
checkpoint-status |  |  | checkpoint | Have the Block Plans been installed next to the RFP and match the current zones and detectors installed on site accurately? INSERT PHOTO
checkpoint-status |  |  | checkpoint | Has all patching and painting been completed or booked in to be completed? INSERT PHOTO
checkpoint-status |  |  | checkpoint | Have the As-Installed’s been left inside the RFP? INSERT PHOTO
checkpoint-status |  |  | checkpoint | Is there a completed copy of the discharge test in the Emergency Lighting Logbook on top of the RFP, if applicable to project?
checkpoint-status |  |  | checkpoint | Have the newly installed Emergency Lights been labelled, if applicable to project? INSERT PHOTO
checkpoint-status |  |  | checkpoint | Is there a FIRE label installed above the strobes? INSERT PHOTO
checkpoint-status |  |  | checkpoint | Have the Installers Statements been filled out in the back of the Manual in the RFP? ATTACH PHOTO OF ALL PAGES