## res
type | name | values | prefix | postfix | usage count | user addable | template name
checklist | ITP - Streetlighting - 903 - Rev B | itp |  |  |  |  | ITP - Streetlighting - 903 - Rev B
section | Safety in Design Analysis
checkpoint | 3.1.01 - Safety in Design Analysis
label | Acceptance / Conformance Criteria - Conduct a detailed safety in design analysis. Ensure the installation is compliant with the Site’s safety in design proposal including all regulatory requirements.
label | Standard / Specification - PS 22.1.15& 22.3.2
label | Verifying Document - Design Analysis report
label | Frequency - Prior to Construction
label | Verification Activity: Activity - H
label | Verification Activity: By - PE
section | Streetlighting Quality Assurance plan
checkpoint | 3.2.01 - Streetlighting Quality Assurance plan
label | Acceptance / Conformance Criteria - Sub-Contractor to provide a Quality Assurance plan to propose, establish, maintain, monitor and document a quality assurance system covering all aspects of the procurement, fabrication, installation and completion of the works.
label | Standard / Specification - PS 22.4.6
label | Verifying Document - Streetlighting QA Plan
label | Frequency - Prior to Construction
label | Verification Activity: Activity - HP
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
section | Montrose Box (MSB-NMB) (1)
checkpoint | 3.3.01 - (MSB-NMB)
label | Acceptance / Conformance Criteria - Provide MSB-NMB shop drawings complete with wiring schematics for review and approval by the Engineer prior to construction.
label | Standard / Specification - PS 22.1.7
label | Verifying Document - Shop Drawings
label | Frequency - Prior to Installation
label | Verification Activity: Activity - HP
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 3.3.02 - Hasp and Staple
label | Acceptance / Conformance Criteria - MSB-NMB shall be fitted with a Stainless-Steel hasp and staple to allow for Waka Kotahi to fit their own padlock onto it. MSB-NMB shall be sourced directly from Montrose Foundry, Mt. Wellington, Auckland.
label | Standard / Specification - PS 22.1.7
label | Verifying Document - Datasheet and dockets
label | Frequency - Prior to Installation
label | Verification Activity: Activity - I
label | Verification Activity: By - PE
checkpoint | 3.3.03 - Metering
label | Acceptance / Conformance Criteria - Liaise with the client’s electricity retailer for the installation of their three-phase meter within the metering compartment of the new Montrose Box.
label | Standard / Specification - PS 22.1.9
label | Verifying Document - Comms
label | Frequency - Prior to Installation
label | Verification Activity: Activity - I
label | Verification Activity: By - PE
checkpoint | 3.3.04 - CCTV Compartment
label | Acceptance / Conformance Criteria - Allow for a CCTV Compartment withing the Montrose Box. Provide a 10A double power outlet within this compartment for future use of CCTV equipment. CCTV Compartment to meet NZTA requirements.
label | Standard / Specification - PS 22.1.10
label | Verifying Document - Datasheet
label | Frequency - Prior to Installation
label | Verification Activity: Activity - I
label | Verification Activity: By - PE
checkpoint | 3.3.05 - Earthing, Bonding & Surge Protection
label | Acceptance / Conformance Criteria - Install an earth electrode in accordance with the in AS/NZS 3000. Install new Earth Bar and Neutral Bar c/w MEN link.
label | Standard / Specification - PS 22.1.11 & 22.6.10
label | Verifying Document - Site Record
label | Frequency - Prior to Installation
label | Verification Activity: Activity - I
label | Verification Activity: By - PE
section | Lighting Equipment
checkpoint | 3.4.01 - Design Drawings
label | Acceptance / Conformance Criteria - Provide drawings of luminaire design and pole locations for review and approval by the Engineer prior to construction.
label | Standard / Specification - PS 22.1.14
label | Verifying Document - Drawings
label | Frequency - Prior to Construction
label | Verification Activity: Activity - HP
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
section | Welding
checkpoint | 3.5.01 - Welding
label | Acceptance / Conformance Criteria - All welding shall be performed by qualified and experienced tradesmen in accordance with relevant New Zealand or Australian Standards, with the engineer having the right to request certification and welding experience, and, if concerns arise about welding quality, to request at no additional cost X-ray and/or ultrasonic testing of up to 10% of all welds selected by the engineer, with any failures potentially requiring additional testing.
label | ○ All welding is to be completed before any corrosion protection treatment is applied.
label | Standard / Specification - PS 22.6.6 & 22.7.1
label | Verifying Document - Welding Certificates
label | Frequency - Prior to Construction
label | Verification Activity: Activity - R
label | Verification Activity: By - PE
section | Corrosion Protection
checkpoint | 3.6.01 - General
label | Acceptance / Conformance Criteria - Notwithstanding anything to the contrary in this specification, where possible all items of plant, equipment and materials shall be manufactured or supplied in materials that will not suffer corrosion. Appropriate materials include galvanised steel, aluminium, fibreglass, stainless steel, etc. All support steelwork, fixings and other galvanised steel shall be hot dip galvanised. The use of electro plated fastenings for external works is not acceptable. All welding is to be completed before any corrosion protection treatment is applied.
label | Standard / Specification - PS 22.7.1
label | Verifying Document - Datasheet
label | Frequency - Prior to Construction
label | Verification Activity: Activity - I
label | Verification Activity: By - PE
section | Painting, Protection and Identification
checkpoint | 3.7.01 - Environmental
label | Acceptance / Conformance Criteria - Select painting and finishes in accordance with the area environmental conditions.
label | Standard / Specification - PS 22.8.1
label | Verifying Document - Datasheet
label | Frequency - Prior to Painting
label | Verification Activity: Activity - I
label | Verification Activity: By - PE
checkpoint | 3.7.02 - Compliance Review
label | Acceptance / Conformance Criteria - Review the risk assessment and statutory and authority requirements completed as part of the system testing, commissioning and handover requirements and provide labelling and signage as determined.
label | Standard / Specification - PS 22.8.1
label | Verifying Document - Datasheet
label | Frequency - Prior to Painting
label | Verification Activity: Activity - R
label | Verification Activity: By - PE
checkpoint | 3.7.03 - Colours
label | Acceptance / Conformance Criteria - Paint colours nominated are to be in accordance with NZS 5807
label | Standard / Specification - PS 22.8.6 NZS 5807
label | Verifying Document - Datasheet
label | Frequency - Prior to Painting
label | Verification Activity: Activity - I
label | Verification Activity: By - PE
section | Underground Services (1)
checkpoint | 3.8.01 - Ducting
label | Acceptance / Conformance Criteria - Unless shown otherwise all buried ducts shall be the sizes and quantities as indicated on the layout plan. (DIA. 50mm) (DIA. 100mm)
label | a) Use heavy duty HD PVC conduit for underground services. Use best practice PVC where possible.
label | b) Colour: Orange for all conduits containing consumer mains, sub-mains or final sub-circuits cabling.
label | Standard / Specification - Road Lighting Ducting Layout, PS 22.12.8
label | Verifying Document - Datasheet
label | Frequency - Prior to Installation
label | Verification Activity: Activity - I
label | Verification Activity: By - PE
checkpoint | 3.8.02 - Warning Tape
label | Acceptance / Conformance Criteria - Provide orange marker tape complying with AS/NZS 2648.1
label | Standard / Specification - PS 22.12.9, AS/NZS 2648.1
label | Verifying Document - Datasheet
label | Frequency - Prior to Installation
label | Verification Activity: Activity - I
label | Verification Activity: By - PE
section | Existing Underground Services
checkpoint | 4.1.01 - Existing Underground Services
label | Acceptance / Conformance Criteria - The contractor shall undertake a comprehensive services identification program prior to beginning site works. This would include as a minimum, review of all service providers maps and drawings, a site scan, and if necessary, a scan using GPR (ground penetrating radar).
label | Standard / Specification - PS 22.6.4
label | Verifying Document - Site Record/Survey Record
label | Frequency - Prior to Construction
label | Verification Activity: Activity - R
label | Verification Activity: By - PE
section | Survey (1)
checkpoint | 4.2.01 - Set-out
label | Acceptance / Conformance Criteria - Light columns set out as per design locations.
label | Standard / Specification - IBEX Lighting Plan
label | Verifying Document - Survey Record
label | Frequency - Prior to Construction
label | Verification Activity: Activity - R
label | Verification Activity: By - SV
section | Underground Services (2)
checkpoint | 4.3.01 - Trench Excavation
label | Acceptance / Conformance Criteria - Excavate trench and lay 50mm sand bedding and free from obstraction
label | Standard / Specification - PS 22.12.8
label | Verifying Document - Site Record
label | Frequency - Where Required
label | Verification Activity: Activity - I
label | Verification Activity: By - SE
checkpoint | 4.3.02 - Ducting/Conduit
label | Acceptance / Conformance Criteria - (a)Separation from LV conduits: Minimum separation between conduits shall be no less than 50mm from other conduits and no less than 100mm from boundary of the trench. Sandy loam is required for building and separation.
label | b) Depth: Conduits shall be buried in trench at a depth no less than that nominated in AS 3000 for the method of installation, with all bends being slow radius bends.
label | c) Separation from other services: Maintain separation from other services running in parallel and crossing electrical installation as nominated by relevant standard (e.g. AS/NZS 3500 for water services, AS/ACIF S009 for telecommunications, AS 5061 for gas services, etc.).
label | Standard / Specification - Road Lighting Ducting Layout, PS 22.12.8
label | Verifying Document - Site Record
label | Frequency - Where Required
label | Verification Activity: Activity - I
label | Verification Activity: By - SE
checkpoint | 4.3.03 - Survey As-Built
label | Acceptance / Conformance Criteria - Accurately record the routes of underground cables before backfilling
label | Standard / Specification - PS 22.12.9
label | Verifying Document - Survey Record
label | Frequency - After ducts are Installed
label | Verification Activity: Activity - H
label | Verification Activity: By - PE
checkpoint | 4.3.04 - Backfill
label | Acceptance / Conformance Criteria - Backfill trenches with sand as soon as possible after approval of laid and bedded service to a height of 300mm. Place the sand in layers < 150mm thick and compact to the density which applies to the location of the trenches to minimize settlement,
label | Standard / Specification - PS 22.12.8
label | Verifying Document - Site Record
label | Frequency - Where Required
label | Verification Activity: Activity - I
label | Verification Activity: By - SE
checkpoint | 4.3.05 - Warning Tape
label | Acceptance / Conformance Criteria - Install orange marker tape complying to AS/NZS 2648.1. Install marker tape at 150mm or 50% of the depth of burial, whichever is greater, below finished ground level.
label | Standard / Specification - PS 22.12.9
label | Verifying Document - Site Record
label | Frequency - Where Required
label | Verification Activity: Activity - I
label | Verification Activity: By - SE
section | Lighting
checkpoint | 4.4.01 - Shear Base
label | Acceptance / Conformance Criteria - Ensure the shear base is installed as per the NZTA M26 specification and in the correct location as per the latest IFC drawing.
label | Standard / Specification - NZTA M26, IBEX Lighting Plan
label | Verifying Document - Site Record
label | Frequency - Where Required
label | Verification Activity: Activity - I
label | Verification Activity: By - SE
checkpoint | 4.4.02 - Column Installation
label | Acceptance / Conformance Criteria - Columns shall be positioned 1.0m behind the kerb unless stated otherwise or advised.
label | Allowable tolerances of the column location are:
label | A) 0.5m Parrallel to the carriageway
label | B) 0.2m Perpendicular to the carriageway
label | C) 0.2m Vertically
label | ○ Ensure columns are oriented correctly and have the correct outreach arm lengths.
label | Standard / Specification - IBEX Lighting Plan
label | Verifying Document - Site Record
label | Frequency - Each Column
label | Verification Activity: Activity - I
label | Verification Activity: By - SE
checkpoint | 4.4.03 - Luminaire
label | Acceptance / Conformance Criteria - Ensure the correct luminaire type and tilt angle is installed as per the latest IFC drawings
label | Standard / Specification - IBEX Lighting Plan
label | Verifying Document - Site Record
label | Frequency - Each Luminaire
label | Verification Activity: Activity - I
label | Verification Activity: By - SE
section | Montrose Box (MSB-NMB) (2)
checkpoint | 4.5.01 - Montrose Box (MSB-NMB)
label | Acceptance / Conformance Criteria - Install MSB-NMB as per project specification, Installation and commisioning ITP and the Electrical Services drawings.
label | Standard / Specification - PS 22.1.7
label | Verifying Document - Site Record
label | Frequency - Once
label | Verification Activity: Activity - I
label | Verification Activity: By - SE
section | Painting and Protection
checkpoint | 4.6.01 - Preparation of Surfaces
label | Acceptance / Conformance Criteria - Preparation: all surfaces shall be prepared by thorough cleaning of all dirt, grease, scale, welding flux and corrosion in accordance with AS/NZS 2312.1. For galvanised surfaces that have been subsequently cut or welded, prime the affected area with organic zinc rich coating for protection of steel to AS/NZS2312.1, two pack or accepted alternative
label | ○ Prime/undercoat all surfaces. Galvanised and non-ferrous surfaces must be etch primed.
label | Standard / Specification - PS 22.8.3
label | Verifying Document - Datasheet
label | Frequency - Prior to Painting
label | Verification Activity: Activity - I
label | Verification Activity: By - PE
checkpoint | 4.6.02 - Application
label | Acceptance / Conformance Criteria - Apply the first coat immediately after substrate preparation and before contamination, and follow all paint system applications strictly according to the manufacturer's recommendations.
label | Standard / Specification - PS 22.8.4
label | Verifying Document - Site Record
label | Frequency - After surface preparation
label | Verification Activity: Activity - I
label | Verification Activity: By - SE
checkpoint | 4.6.03 - Finishing
label | Acceptance / Conformance Criteria - Concrete Bases: 2 coats synthetic emulsion paint
label | ○ Equipment Panels/Switchboards: 2 final coats full gloss enamel (c) Equipment: Factory spray application
label | ○ Other surfaces: 2 final coats full gloss enamel.
label | Standard / Specification - PS 22.8.5
label | Verifying Document - Streetlighting QA Plan
label | Frequency - Prior to Construction
label | Verification Activity: Activity - I
label | Verification Activity: By - PE
section | Survey (2)
checkpoint | 5.1.01 - As-Built Drawings
label | Acceptance / Conformance Criteria - As-builts reviewed and submitted showing final location of all poles.
label | Standard / Specification - PS 22.9.4
label | Verifying Document - Survey Record
label | Frequency - Post Works Completion
label | Verification Activity: Activity - R
label | Verification Activity: By - SV
section | Testing
checkpoint | 5.2.01 - Electrical Certificate of Compliance (CoC)
label | Acceptance / Conformance Criteria - The contractor shall provide a CoC for the electrical installation. The certificate shall record all test results including insulation resistances, earth continuity and earth resistance. Detail to be included on the CoC is the measured prospective short circuit current for each outlet, switchboards and termination point,
label | Standard / Specification - PS 22.6.11
label | Verifying Document - CoC
label | Frequency - Post Works Completion
label | Verification Activity: Activity - R
label | Verification Activity: By - PE
checkpoint | 5.2.02 - Twelve-month warranty period
label | Acceptance / Conformance Criteria - Provide twelve (12) months statutory testing, servicing, maintenance, remediation of defects and warranty of all services systems and equipment installed under this contract from the date of Practical Completion
label | Standard / Specification - PS 22.1.15
label | Verifying Document - Warranty
label | Frequency - Datasheets
label | Verification Activity: Activity - R
label | Verification Activity: By - PE
section | Certification
checkpoint | 5.3.01 - Final Certification
label | Acceptance / Conformance Criteria - Obtain final certification of the installed systems by an independent electrical inspector approved by the Electricity Workers Registration Board.
label | Standard / Specification - PS 22.1.15
label | Verifying Document - Final Certificate
label | Frequency - Post Works Completion
label | Verification Activity: Activity - R
label | Verification Activity: By - PE
section | Guarantee
checkpoint | 5.4.01 - Guarantee
label | Acceptance / Conformance Criteria - Provide guarantees for all equipment including 10-year minimum guarantees for external luminaires and poles.
label | Standard / Specification - PS 22.1.15, IBEX Lighting Plan
label | Verifying Document - Guarantee
label | Frequency - Post Works Completion
label | Verification Activity: Activity - R
label | Verification Activity: By - PE
section | Spare Parts Schedule
checkpoint | 5.5.01 - Spare Parts Schedule
label | Acceptance / Conformance Criteria - Provide a comprehensive schedule of maintenance spare parts, detailing recommended quantities, manufacturer prices including packaging and delivery to site, marking and numbering procedures, referencing equipment schedules, and preventive measures such as painting and greasing to avoid deterioration during storage.
label | Standard / Specification - PS 22.9.7
label | Verifying Document - Spare Parts Schedule
label | Frequency - At least 8 weeks prior to Practical Completion
label | Verification Activity: Activity - R
label | Verification Activity: By - PE
section | Required Operating Instructions
checkpoint | 5.6.01 - Required Operating Instructions
label | Acceptance / Conformance Criteria - Provide operating instructions and schematic diagrams mounted alongside equipment to meet statutory requirements, e.g., Fire Brigade. Diagrams to be colour-coded, colour-fast, laminated and mounted.
label | Standard / Specification - PS 22.9.7
label | Verifying Document - Site Records
label | Frequency - Post Works Completion
label | Verification Activity: Activity - R
label | Verification Activity: By - PE
section | Operating and Maintenance Manuals
checkpoint | 5.7.01 - Operating and Maintenance Manuals
label | Acceptance / Conformance Criteria - Provide a comprehensive Operating and Maintenance documentation to cover all installations to provide a detailed understanding of the plant and its operation, an aid for training of operators, a reference for fault diagnosis and a framework for preventative and breakdown maintenance.
label | ○ Submit manuals in two stages. Stage 1 include all the sections (generally sections 1-5) of manuals excluding final testing and commissioning records and As Built drawings. This manual shall be submitted well in advance of the Practical Completion and should be signed off by the Engineer at least 4-6 weeks before programme Practical Completion Date.
label | ○ A first draft manual should be submitted 8-10 weeks before the practical completion date for review. Subsequently, submit a completed second draft incorporating comments for further review. Finally, include all remaining sections, incorporate all changes and resubmit until all comments are addressed to the satisfaction of the Engineer
label | Standard / Specification - PS 22.9.6
label | Verifying Document - O&MM
label | Frequency - 4-6 weeks before programme Practical Completion Date
label | Verification Activity: Activity - HP
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 5.7.02 - Inspection and Test Plan
label | Acceptance / Conformance Criteria - Installation and commisioning Inspection and Testing Plans to be provided to the satisfaction of the Engineer
label | Standard / Specification - PS 22.9.6, PS 22.9.4
label | Verifying Document - ITP
label | Frequency - Prior to Installation
label | Verification Activity: Activity - HP
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 5.7.03 - Final Copies Stage 1 & 2
label | Acceptance / Conformance Criteria - Submit 3 sets of final volumes within 2 weeks after practical completion. Incorporate feedback from review and from training of Principal’s staff, including preparation and insertion of additional data. Include a section containing commissioning test reports.
label | Standard / Specification - PS 22.9.6
label | Verifying Document - O&MM
label | Frequency - Within 2 weeks after practical completion
label | Verification Activity: Activity - R
label | Verification Activity: By - PE
section | Final Contract and Hand-Over Documentation
checkpoint | 5.8.01 - Final Hand-Over
label | Acceptance / Conformance Criteria - Documentation is required in electronic and hard copy format. Electronic documentation shall be supplied on the latest Microsoft and Autodesk Software versions at the time of Practical Completion.
label | Operating and Maintenance Manuals (including Final Commissioning Data):
label | ○ Electronic format installed on BMS File Server: 1 set
label | ○ PDF format on USB storage device: 3 sets
label | ○ Hardcopy: 3 sets
label | As-Built Drawings:
label | ○ AutoCAD format on USB storage device: 3 sets
label | ○ Hardcopy full-size with hanging strips: 1 set
label | ○ A3 size (included in O&M Manual): 2 sets
label | Revit Model:
label | ○ Refer to the requirements set out in the project BEP (BIM Execution Plan)
label | Control Software:
label | ○ USB storage device: 1 set
label | OH&S Safety Signage:
label | ○ Permanent: 1 set
label | Standard / Specification - PS 22.9.7
label | Verifying Document - Site Records
label | Frequency - Post Works Completion
label | Verification Activity: Activity - R
label | Verification Activity: By - PE