## zres_siteapp_NEW
Id | Type | Name | Values | Prompting Name | Postfix | Resource Id
| checklist | INF-HSEQ CC0398-ITP-031 Blinding, Pile Caps and Slab Footings Rev D | itp | INF-HSEQ CC0398-ITP-031 Blinding, Pile Caps and Slab Footings Rev D |  | fb9861af-a689-4541-93a0-241e1cc8be4a
| section | 1.0 General
| checkpoint | 1.1 - Material Submission / Approval
38dc39c1-97aa-5987-bc61-8cc1a17d59b7 | note | Ref docs - AS 3600 235929-000- CV-SP-00007
66bc53e2-f270-563e-a4b5-d9d15ed3de85 | note | Acceptance criteria - Has the mix design to be approved prior to placement. Material properties meet project specification, AS 3600, AS 1379?
2051261c-d26c-51f1-a53b-15cc5181a8cd | note | ○ Do Structural Elements meet: Minimum Concrete strength 40 MPa or as specified in Drawings?
5f725601-87d4-5f25-98f8-ff0c4a102d4e | note | ○ Do Non-Structural Elements meet: Minimum Concrete strength 15 MPa or as specified in Drawings?
0b478f3b-221b-593b-bd2a-27904927049d | note | ○ Has Steel Reinforcement schedule provided to MDR for review and approved?
fd49ac14-fc4c-577d-b810-d73735edd6c8 | note | ○ Do admixtures shall conform with AS 1478.1 and are permitted if used in accordance with manufacturers instructions?
bfd4a202-eac0-583a-8d60-53ff6f4a61f1 | note | ○ Mixtures containing calcium chloride shall not be used.
1e83a2a2-1a47-58b0-9171-77d1d5b38a78 | button | Acceptance | Yes,No,N/A
de1c3c54-5e6f-59fd-9d9f-cc7d4a4f11f6 | note | Key - H
dc65c313-7a5a-5d5d-a677-e787b15d0c60 | note | MDR/VIVA Key - H
556114eb-a1b4-5385-b989-cb03ac46bf52 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - Mix Design Number, Bar Bending Schedules, Material compliance certificates
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 1.2 - Determine lot size
5ae5a78b-cf2a-597c-bce9-680c9cdad51c | note | Acceptance criteria -
9cc93c84-89f3-523e-af5a-3b1a4e2623ca | textbox | Lot Size = Each pour section per day (location or m2) or each structural (Pilecap)
dfe7de41-a4ef-5ac9-b818-c1a6c13751da | note | Key - S
c76448c8-724e-5395-b5f5-34fc6089ff77 | note | MDR/VIVA Key - S
| checkpoint | 1.3 - Permits
9bff6d0e-771e-52a8-946a-8d127d399758 | note | Acceptance criteria - The following are relevant, in place and signed onto:
5af0f85a-9817-5358-b330-02e31e30ebc7 | note | – Penetration permit
da668d64-52b7-55d5-b6ed-31b53edc1a2d | note | – Hot works permit
f304070e-4b95-5b82-a3d3-695a812a5b09 | note | – Temporary work permit
79378160-af0d-5fa8-97d6-79591e53e5bc | note | – Working at heights permit
1b6ccd4a-1282-5b7c-b04d-9e07d17fb828 | button | Acceptance | Yes,No,N/A
138c99c4-157f-5bbc-9974-29302a05cf6b | note | Key - H
51da0678-2edf-5890-9cd5-b33a628dca49 | note | MDR/VIVA Key - S
| section | 2.0 Blinding/Lean Concrete
| checkpoint | 2.1 - Set out
86fe4bc4-62ff-5c40-9bb9-3a7cd82075f1 | note | Ref docs - IFC drawings
089626ac-9bbd-548e-bd18-dacf51ff92f9 | note | Acceptance criteria - Extents, grades and levels correct to relevant drawings. All services have been marked out.
33a08e2f-ba2f-5484-a2b9-57125200af6a | button | Acceptance | Yes,No,N/A
f591230a-d954-5fcf-a8ca-acc37573e700 | note | Key - W
a4ef8778-38d4-53a9-b6bb-1d5f4a174358 | note | MDR/VIVA Key - W
| checkpoint | 2.2 - Pre-Pour Inspection
ec7ee693-13c8-5626-ab42-5d7cca6da121 | note | Ref docs - IFC drawings, Pre Blinding inspection
508b44c2-a4d5-5b6a-8064-f431605ab32e | note | Acceptance criteria - Has a pre-pour inspection been completed with the client, and they have verified in writing that the pour is able to commence?
01eabe0a-10f8-5400-9041-d074788419d5 | note | ○ The foundation base excavation shall be tested, surface compacted and approved prior to placement of the blinding.
ae86cf42-f983-5714-ab6c-42571514a449 | note | ○ The foundation location, depth and dimensions shall also be checked and confirmed prior. to placing the blinding.
4de94789-0a5f-514d-b31d-d228bee0d2aa | note | ○ Approval shall be provided, in writing, by McDermott to the foundation. subcontractor before commencing with concrete placement.
766f8803-c430-5e51-9098-f4c55463bf94 | note | ○ Has this been completed?
be854e56-748b-562b-b097-10edb85de43e | button | Acceptance | Yes,No,N/A
85c6c7fb-2f8a-53f4-b9f3-8d5eac4d1f55 | note | Key - H
e6e9c8c3-c1d8-54f1-88e0-e11486688fa5 | note | MDR/VIVA Key - H
ca558a49-2270-58c0-a08d-98204cced2cc | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - Pre-Pour Checklist
| note | ○ 235929-000-CV-SP-00007 Appendix 7.1 Pre-Concrete Placement Checklist
| note | ○ Bearing Capacity report (if not on piles)
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 2.3 - Lean Mix Concrete
c0181690-db59-5f12-936c-d0cb9382f4ec | note | Ref docs - Section 5.1.2 of document 235929-000- CV-SP-00007
b999404c-0268-5609-b37f-fe95f278faf5 | note | Acceptance criteria - Approved Concrete Mix Design.
d4c31910-d804-590a-8b32-76c475a8e69a | button | Acceptance | Yes,No,N/A
6983f950-b771-5c06-850e-ab5b59e303b2 | note | Key - W
0c5e9dcb-64e5-5698-8cf9-c92c8380d069 | note | MDR/VIVA Key - W
15a44087-ddb2-5c30-a1fc-a12f8ba0a5ef | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - Dockets
| checkpoint | 2.4 - Placement of Lean Mix
49209e33-c527-599b-bd12-ae606910c89e | note | Ref docs - 235929-000-CV-SP-00007
a84414c6-b35c-56cf-b14c-8fc6cd13cf02 | note | Acceptance criteria - Has the blinding been poured to the correct level? The following are acceptable:
5a62b3de-cf3f-5125-bd5e-4329bb47d03b | note | – Minimum Thickness = 50mm
6e9a8561-a3de-5bbf-a3cd-386009a4c82c | button | Acceptance | Yes,No,N/A
0a030111-d672-5aef-a44c-b2489fda43a8 | note | Key - W
7387a6ed-a301-5b0b-b17e-e8e79b0d6977 | note | MDR/VIVA Key - W
d5da4906-4e10-5691-b7c4-785fe3ed91e4 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - As-built Survey
| section | 3.0 Formwork
| checkpoint | 3.1 - Temporary works requirements
c7819eff-ac8d-5ff9-b597-0f2b6f3a4a78 | note | Ref docs - SYM-INF-Temporary Work Procedure IFU 05122
fb975dca-1c9e-50e7-9e2d-f87b208c3eeb | note | Acceptance criteria - Formwork above 1.0m to be designed by temporary works engineer.
2ab242e7-9df3-5ef7-8398-aa12988d9771 | note | ○ Has design to be undertaken by external consultant complying with AS1170 and AS3610 plus any project specification requirements?
4478758b-9afd-5146-93d3-af9f63a08daf | button | Acceptance | Yes,No,N/A
f8449bb5-6135-5252-a322-90a42793f594 | note | Key - H
1f9c2ac4-53bd-5031-986d-94e9fcfd3364 | note | MDR/VIVA Key - S
| checkpoint | 3.2 - Pile Penetration
ca94c097-afa7-5f79-a50e-916650438797 | note | Ref docs - Civil Drawings IFC
20309ffe-f6ee-590f-9186-18ba5bd6f161 | note | Acceptance criteria - Pile C.O.L to penetrate 50mm above blinding of pile cap (+/- 25mm).
7b063ac0-ac9b-5948-9e3a-1146ce759369 | note | ○ Has the pile been determined to be free of cracking and concrete damage following cropping?
9f1bb396-e983-53ed-ba99-e6d9d34cd1a8 | button | Acceptance | Yes,No,N/A
344e6758-6c88-5409-8f2f-0a58e050cf22 | note | Key - H
9de46810-e107-5e8a-96c8-6c10f3f048d1 | note | MDR/VIVA Key - H
854479c7-f6e2-581e-8033-e770c58f9fef | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - Survey Report
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 3.3 - Formwork Setout and positioning correct
5535dc21-45a0-5166-aeaa-70a54f48f3ca | note | Ref docs - Civil drawings 235929-000- CV-SP-00008; Section 6
e7480757-5b6f-5994-b7b2-b90610675b29 | note | Acceptance criteria - Is formwork checked for potential loose sections, ensuring no movement upon placement of concrete?
5b47baf0-737f-596f-9bbf-ebb400095fe0 | note | ○ Is formwork in line with survey markings?
7f7dd498-3c4f-5eff-9bc5-ce271fcbfc67 | note | ○ Have chamfers (if required) been attached to formwork in level manner?
7d1dcfdb-096d-5461-ab3a-78ebee5e310f | button | Acceptance | Yes,No,N/A
7ad068b9-91fc-590d-b608-0150ab8ff736 | note | Key - W
1b82924b-a9bb-5542-aacf-0703c64a07b0 | note | MDR/VIVA Key - W
| checkpoint | 3.4 - Concrete jointing
4f59ced6-d6b0-5831-837d-bf1581fcd594 | note | Ref docs - Civil drawings
91eede06-c374-5b5f-92ff-d89a7db6e3f2 | note | Acceptance criteria - Have construction joints to be installed as detailed on Drawings and notes using correct materials?
5721c9c0-a3fc-546a-97d9-092302ebc07b | button | Acceptance | Yes,No,N/A
0228c326-27c4-510e-b07a-cb7faf01793e | note | Key - W
4c1d22f1-532a-514d-9c9b-f26cbffbb870 | note | MDR/VIVA Key - S
| section | 4.0 Reinforcement
| checkpoint | 4.1 - Steel reinforcement supply
f42931b2-66a1-51f1-be50-2c7e599cc49e | note | Acceptance criteria - Have steel tags checked against supply schedule prior to installation?
61b24da6-4ac4-5952-8d6b-4337b1843aec | note | ○ Does the manufacturer hold a valid ACRS certificate?
fd813473-0387-5126-a63b-b569baf3b18c | note | ○ Is reinforcement is free from rust and other contaminates that may affect bonding?
e59386e9-e209-5aaa-82f8-cdd0697773db | button | Acceptance | Yes,No,N/A
890a24d8-f366-56c7-b083-3bffc08bdef2 | note | Key - S
8221f792-3caa-5c2e-ba97-26cff7f5ab2f | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - Delivery Dockets / certificates / product tags, Incoming material checklist Photo’s
| checkpoint | 4.2 - Steel reinforcement installation
d22409ec-ccf9-5370-b6eb-4dbbf8715b67 | note | Ref docs - 235929-000- CV-SP-00009, AS3600 17.5.3, 235929-000- CV-01-92002- 010002
6810c17f-d835-59a0-ac94-7a3df2f24a31 | note | Acceptance criteria - Is steel installed as per the latest IFC drawings?
70f1ae2d-0b63-5ef3-8fa0-1d2c9a22913e | note | ○ Does steel reinforcement conform with Steel Reinforcement Specification?
866f16bd-0658-51b0-95d6-2bc197050c44 | note | – – – – – – – – – – – – – –
4fdf6b1d-4ff2-5ef9-9362-2baa7e9ab501 | note | 17.5.3 Tolerance on position of reinforcement and tendons
216d941c-878a-5ede-ab23-3d86b51297ec | note | The deviation from the specified position of reinforcement and tendons shall not exceed the following:
bf01ae81-1011-5a6a-81c4-8f7e5eb74919 | note | (a) For positions controlled by cover –
e7b5e44b-7575-5e12-a0c2-ecaff87cd733 | note | (i) in beams, slabs, columns and walls: -5, +10 mm;
f8f39c39-2cfc-51fd-ba00-ce6cfa6e2b3f | note | (ii) in slabs-on-ground: -10, +20 mm; and
ea7f388f-2b47-5ff4-8246-2e841888ff04 | note | (iii) in footings cast in the ground: -10, +40 mm,
a4f8bc42-4867-53e0-b2a1-65ce6b07823a | note | where a positive value indicates the amount the cover increases and a negative value indicates the amount the cover decreases.
823636fa-9bb5-59e4-b47f-57b5832f0b1c | note | (b) For positions not controlled by cover, namely –
b9133cb8-cb80-5600-aaaf-d6ee1eb8d8d1 | note | (i) the location of tendons on a profile: 5 mm;
99065f29-b07c-594f-841c-6df3a506c4d7 | note | (ii) the position of the ends of reinforcement: 50 mm; and
af268ade-110f-5716-a4cf-67cdaebfb06a | note | (iii) the spacing of bars in walls and slabs and of fitments in beams and columns: 10% of the specified spacing or 15 mm, whichever is greater.
ee259f74-8863-5c36-899c-9be71202c541 | note | – – – – – – – – – – – – – –
16a1861c-5b6b-5fc6-846f-36200d7dcc3b | note | ○ Has minimum cover to inside face of wall must be maintained? All reinforcement shall be in accordance with AS 3600 & Civil drawings.
d2fe726d-b515-5987-9f1d-bbd12508d9b8 | note | – – – – – – – – – – – – – –
d63c2bfc-fe63-5578-a6d5-82ffca82744a | note | 8.1 CONCRETE COVER SHALL BE IN ACCORDANCE WITH AUSTRALIAN STANDARD AS 3600 OR THE VALUES STATED BELOW, WHICHEVER IS GREATER.
0f40a8cf-669f-53ed-9c92-6f5ebb5f02ac | note | ○ PAVING (TOP) = 30 mm
6d8f4b08-39eb-5b25-8d96-a62bdab591f1 | note | ○ PAVING (BOTTOM - AGAINST GROUND) = 50 mm
16e94149-4024-5b9f-9d6f-42ae460a5559 | note | ○ FOUNDATIONS CAST AGAINST FORMWORK (INCL. EXPOSED WEATHER FACE) = 45 mm
021a922d-e5d0-513f-890d-c06debe22372 | note | ○ FOUNDATIONS CAST AGAINST GROUND = 65 mm
0973c0aa-da2f-5900-88f6-b3260841c5fc | note | ○ EXPOSED TO WASH DOWN WATER AND/OR PROCESS SPILLAGE = 50 mm
81964aa0-8a8f-543e-8519-793fafead59f | note | ○ CAST ON LEAN CONCRETE = 45 mm
c7557033-23b8-54df-98eb-9909d90dc9ca | note | ○ CFA PILES = 70 mm
9926baa2-c277-5d16-8aa2-294dd6120c87 | note | – – – – – – – – – – – – – –
7e9e464f-63c6-50ef-a40b-8ee9989570f8 | button | Acceptance | Yes,No,N/A
9f00da5c-02b5-57c6-9ee4-45d014933309 | note | Key - H
5d6b38f5-845a-5e80-993e-560195f284be | note | MDR/VIVA Key - S
05102a51-0c35-550a-ad38-1a1984d66084 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - IFC Drawing Number and Revision
| section | 5.0 Structural Concrete Pour
| checkpoint | 5.1 - Pre-pour Inspection
239ffe9e-5ec3-5fd1-b0c4-f20c7e67ae4b | note | Ref docs - 235929-000-CV-SP-00007 Appendix 7.1 Pre-Concrete Placement Checklist
4db2740b-4bb6-5ccc-b27e-5b092ab54960 | note | Acceptance criteria - Has a pre-pour inspection checklist completed prior to placement?
0b4afb99-2b27-5759-b940-2528358e76b5 | button | Acceptance | Yes,No,N/A
9236e013-4ce8-5ec0-bf67-f3a5d594cb12 | note | Key - H
b137a84d-23cd-5150-ada7-fac772779c01 | note | MDR/VIVA Key - H
52f81244-cb49-539d-80e2-05c4178e5004 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - 235929-000-CVSP-00007 Appendix 7.1 Pre-Concrete Placement Checklist
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 5.2 - Placement
cf45ad69-6304-520e-ac92-0418c788afea | note | Ref docs - 235929-000- CV-SP-00007 Appendix 7.3 Concrete Truck Record
b20d327c-4997-5b05-b905-9173ff44a912 | note | Acceptance criteria - Concrete shall not be placed when temperature is less the 5°C or greater than 36°C. Between 32°C and 36°C admixtures and placing requirements must be met.
3b518dbe-f4ef-51f9-a0de-f4b0f17e3944 | note | ○ Concrete shall be transported, handled and placed to prevent segregation, loss or leakage of materials.
90b508b7-9702-5ee3-921a-475378d98e79 | note | ○ Concrete shall not be dropped from a height greater than 2m.
5f46a6c2-e296-59d7-83f1-6aece02703d6 | note | ○ Concrete shall be discharge within 90 minutes of dispatch from plant.
2deae49a-8fe0-535d-9ff4-94c49e292fcc | note | ○ For continuous pours, the maximum time lag between truck loads shall not exceed 25 minutes.
a8eeefbb-ca7c-5b1d-9a41-e4a56283a0b2 | note | ○ Concrete shall be thoroughly vibrated to ensure no honey combing, voids or surface defects occurs and compaction is achieve throughout structure.
77a59b85-24df-5680-8886-66f8739d49d4 | note | ○ Water shall not be added to achieve slump greater than that specified. Slump test to be completed after water is added.
895d47a5-a1aa-549c-a38c-11b1e0dd2ae1 | button | Acceptance | Yes,No,N/A
2f23a380-2723-599a-8be2-b9d622724aab | note | Key - H
74c06dfc-9064-5b62-9ade-07340b55e3cf | note | MDR/VIVA Key - W
0d5bea98-5a15-51b4-a762-f1c9019ae34c | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - 235929-000-CVSP-00007 Appendix 7.3 Concrete Truck Pour Record/Dockets
| checkpoint | 5.3 - Slump Test
df23455f-3b5a-5d55-8fac-fa1d22e46fe8 | note | Ref docs - Section 5.1.1 235929-000- CV-SP-00007
32e1fcef-a061-5f7c-ba59-e3482e2575f3 | note | Acceptance criteria - Slump must be within tolerance of designed slump.
c2171f33-7ce8-5763-adaf-bb6787dbadbf | note | ○ Testing shall be +- 15% of stated.
86df0126-48a2-5e18-bd77-5ff70ac53d96 | note | ○ Approved mix design slump
d1ef89bb-380e-5796-91f7-2829c0908bde | button | Acceptance | Yes,No,N/A
ecd5aa8f-f4ed-54d6-a786-af29109ff584 | note | Key - S
16baa9ec-1bc4-597c-b27e-8406c7aa512f | note | MDR/VIVA Key - S
f6a24409-a0b3-536c-afca-48d362553b0f | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - Test docket
| checkpoint | 5.4 - Strength Testing
6a712eec-24b0-515d-b216-0914620452ee | note | Ref docs - 235929-000- CV-SP-00007 Section 6.8
436c519e-acfa-54a4-9e8c-583a2586890a | note | Acceptance criteria - Samples to be taken from chute. 5 cylinders collected per sample – 1x 7day, 3x 28day, 1x reserve.
36fa5d97-aa53-5a90-b994-98f5f4f0ebc9 | note | ○ 1 test for the first 20m3
5d6827c1-535d-50ae-b753-418f1a284471 | note | ○ 1 test per 40n3 thereafter
35fcfc0c-c309-5d8d-9de0-4c58c778f5bf | note | ○ Frequency reduce to 1 test per 80m3 for pours over 400m3
322fdf96-ea09-5a44-ad31-dbc9ae3f6d98 | note | Acceptance
a0426478-4d97-538c-b10c-52d69069e918 | note | – – – – – – – – – – – – – –
1d705805-ea00-5501-94af-40d2904998cb | note | No. of samples ¦¦ Volume of concrete (m3)
eeedf888-d6b9-54ea-a141-1f1d40027f74 | note | – – – – – – – – – – – – – –
bbc71923-925e-575e-98d7-466e7be68a57 | note | 1 ¦¦ <20
5a9c0c7a-b950-5538-a8d8-739efd701cfe | note | 2 ¦¦ 20-60
e971d102-313c-5225-a980-fd95f29b565d | note | 3 ¦¦ 60-100
80c633b5-0611-5e1b-861a-88805ff61a31 | note | 4 ¦¦ 100-140
e2ab1c0c-441c-5b5d-9c66-11b4d40eb400 | note | – – – – – – – – – – – – – –
9983feff-0c46-5f99-948b-86aed595806f | note | Key - H
45500009-804d-54b6-8fed-29d19bac0829 | note | MDR/VIVA Key - S
180eefb4-5dcc-5324-a1ed-2aaee9d8ddcc | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - Test report
| checkpoint | 5.6 - Curing of Concrete
f7c0712b-8955-55e8-ab27-f69d4626a3a7 | note | Ref docs - 235929-000-CV-SP-00007 Section 6.5
c1edee11-ee08-5473-b83b-4a2a6ed25110 | note | Acceptance criteria - As per the approved Curing Methodology.
adf2a0c3-8e3f-5603-81f6-b2380f89ae5a | note | – Applied once bleed water has gone
65f5950e-d5e8-54bd-8253-75674123c1e6 | note | – Continuous uniform film achieved
cb076cc0-2c21-551d-bb2e-620e61c15228 | note | – Rate of 5m2/L
b5547988-aa51-55c8-a251-12d415d7da7d | note | ○ Has curing been conducted as per approved curing methodology?
817fae1c-00a7-52d5-a06c-fbc361bf5901 | button | Acceptance | Yes,No,N/A
17874744-6164-5a97-933e-416f164d96fc | note | Key - H
1e74c937-5f23-5ec4-bba8-f6195146f428 | note | MDR/VIVA Key - W
92fa07e0-a3fe-5057-a34f-dd18e3de53c6 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - Approved Curing Technical Data Sheet
| checkpoint | 5.7 - Concrete Finishing
ca172474-abe9-5707-9354-92222823cb7e | note | Ref docs - 235929-000-CV-SP-00007 Section 6.4
0e6e3ad2-49b5-5869-92fb-3e51d525d504 | note | Acceptance criteria - Finish concrete per schedule below:
a0814925-0f71-561b-b587-d7a05fccbb1e | note | ○ Interior walls or columns exposed: smooth form/rubbed finish.
c5f50b3a-6d8c-5caf-9989-bb2fea7549bf | note | ○ Exterior walls or columns exposed: smooth form/rubbed finish.
5ecdd4ef-02b2-56c3-bb96-20a75b791a03 | note | ○ Walls below grade: rough form finish.
d6ea72f1-fd74-5653-ad3c-401c3053c4f9 | note | ○ Exterior slabs for spill containment: float finish.
a6b1b127-b96e-5e22-9317-4a01d53b7d2c | note | ○ Other exterior slabs (i.e. foot traffic): broom finish.
bc06f7d0-e86b-5d4f-a708-03e036c88fd7 | note | ○ Interior slabs: steel trowel.
a11f21c5-2d68-555f-8348-706701894c3a | note | ○ Interior slabs to accept additional finish: steel trowel.
9dea0913-2eda-5e7d-b7bc-d4c125d26d0b | note | ○ Surfaces to be grouted: rough [6 mm amplitude] but even finish with laitance removed to provide good bond between grout and concrete.
a30e398c-0496-5a92-b198-9caff7926968 | button | Acceptance | Yes,No,N/A
860f64e1-1579-5c3c-ad59-70ce5fcc6bdd | note | Key - S
1c75f4e8-aabf-5861-9841-72c7b9f3affc | note | MDR/VIVA Key - S
315fb1fd-846f-5914-a953-3709828694a0 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - 235929-000-CVSP-00007 Appendix 7.3 Concrete Truck Pour
| checkpoint | 5.8 - Formwork Stripping
fa3a5756-6946-57eb-acac-9d5d87d55622 | note | Ref docs - 235929-000-CV-SP-00007, AS1510, AS1509, Section 6.6 of 235929-000-CV SP-00008 CONC FORMWORK
8b21296e-c06f-5993-954b-ae76c7df9417 | note | Acceptance criteria - Has Remove formwork progressively so no unbalanced loads are applied to the structure, or concrete is damaged?
0c2c6fda-7612-55fb-aefd-5e0c545ef761 | note | ○ Has the formwork been removed in the same sequence as concrete placement to achieve similar concrete surface coloration?
50ba77fb-2509-5919-89c0-9c478a004902 | note | ○ In accordance with AS3600 Table 4.4 and Section 17.1.5, removal of forms before 7 days would require a curing membrane conforming to AS3799 to be applied immediately or any other approved acceptable method of water retention in the concrete.
621e2dc8-4940-5541-bdf8-c42a4b914fca | note | ○ Has this been completed?
501e0beb-5a27-5550-b675-c737dea147cd | button | Acceptance | Yes,No,N/A
396cd9db-d4ed-5070-8c8c-3651e219380c | note | Key - S
a95a6b67-8daf-5635-8665-fea3aa2b89dd | note | MDR/VIVA Key - S
| checkpoint | 5.9 - Post Pour inspection
83b22758-b60c-5795-93f8-c10d1940174c | note | Acceptance criteria - All abovementioned works have been completed in-line with the drawings and specification and backfilling around structure can be completed (if applicable)
481205fd-06dc-5e83-86f2-969975dc853b | button | Acceptance | Yes,No,N/A
1700a992-191f-5f1d-82cb-31f02e3c63b6 | note | Key - H
ec247bc9-a2be-5b86-9e16-1a94cc9299f9 | note | MDR/VIVA Key - H
| signoff | AUTHORITY HOLDPOINT
| section | 6.0 Completion
| checkpoint | 6.1 - As Built
a4a248be-348c-596f-bb94-db2e17b0b3ee | note | Acceptance criteria - As built to be submitted after pour, showing set out, RLs, grades, extents, bolts, grout tubes, starter bars, etc.
dd426662-ba58-5d08-a428-ffd5f9a65067 | button | Acceptance | Yes,No,N/A
31c043f2-f95a-5193-af01-8d294bcbac7a | note | Key - S
2eae9447-6a3d-5a16-9da6-e962fa10673d | note | MDR/VIVA Key - H
f461e7b7-35df-5ee5-b3f2-3cd1c91fea8e | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - Survey Conformance report
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 6.2 - Concrete Test Results
b0567501-b655-5047-805f-92a97030f726 | note | Ref docs - 235929-000-CV-SP-00007 AS3600, AS1379, AS3610 IFC drawings
4c830c25-5a30-5cde-8b1c-c4ad69c131fd | note | Acceptance criteria - Submission of 28 days results. Results meet requirements of 40MPa.
882fd5d6-c066-5d45-ac9e-f6265108dcbe | button | Acceptance | Yes,No,N/A
9378086f-efbb-56df-a8d4-c7f36335e80d | note | Key - H
62736c2b-c383-51eb-814a-f744b74d40ff | note | MDR/VIVA Key - S
da0c4da8-e8c2-5f85-8aaa-0ab3912af901 | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - NATA endorsed test report
| checkpoint | 6.3 - Concrete cracking approval
ee34ac15-e616-59bb-8540-c270d0479483 | note | Acceptance criteria - Contractor is to submit a concrete crack repair methodology to MDR prior to commencing any crack repair. Has this been approved?
ef164b3f-5bce-5145-a896-fd14f3aa7aa9 | note | – – – – – – – – – – – – – –
c19c26dc-0b16-532a-bdcc-050cae2b75d3 | note | Maximum Allowable Crack Widths in New Concrete
843c554a-8132-52c5-9c68-020dd3a3602f | note | – – – – – – – – – – – – – –
34360a93-ec16-558c-8d16-8eaae13492ef | note | Service Exposure Condition ¦¦ Crack Width, μm
a11b7ea0-7c7b-5a1f-afef-85f410f63e8c | note | – – – – – – – – – – – – – –
7c9647fa-d9e2-5392-b4b3-156699739c90 | note | Interior ¦¦ 300
3105f302-a6da-57b6-aee1-73160c8d4993 | note | Exterior air (or soil) ¦¦ 200
320853ad-9ad1-5686-87f5-fd0b0b860ad3 | note | Water-retaining structures ¦¦ 100
f5b4a7d2-f20c-59ea-b522-91085f645b10 | note | – – – – – – – – – – – – – –
75e83a5f-9507-5d54-aefc-f438730e4bd0 | button | Acceptance | Yes,No,N/A
318f2ad8-d665-5344-8acb-3bf3225ac2b9 | note | Key - H
b16419de-1901-5fd9-bfea-cc56b3ed6245 | note | MDR/VIVA Key - H
6d3a76c9-6037-5d0a-be16-9752f81fb2ae | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - Concrete Repair Method Document Approval
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 6.4 - Concrete cracking repair
4690863e-91d7-573c-928b-0dc622373387 | note | Acceptance criteria - Has concrete crack repair been undertaken as per the approved method?
d5217aab-b234-5307-ba82-f79ac01566e9 | button | Acceptance | Yes,No,N/A
0a981ae8-f477-5408-a8fb-c610b4e47dfc | note | Key - H
b6f635be-858e-52e8-b614-4c5c61f0214a | note | MDR/VIVA Key - H
cb75cf7c-87e6-551c-a1d3-29fc188af5aa | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - Photo’s
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 6.5 - Leak Testing
f0bc5ff6-a703-5ea3-94ad-c84071958231 | note | Ref docs - 235929-DM-AT-000002
ad1590fb-52e5-5324-9352-8b43e5d1fbb2 | note | Acceptance criteria - Has the nominated structure had leak testing completed and passed as per the approved testing procedure.
bc84f206-8228-5747-819f-45f42a58d86f | button | Acceptance | Yes,No,N/A
235c43bb-6a7e-51e4-bd2a-d180ad9dea00 | note | Key - H
e4da6402-2ff7-5c05-9008-d7774e20e814 | note | MDR/VIVA Key - H
a9b4c81b-fe00-5038-b395-33a02fd6f0bc | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - Water Test Check-list
| signoff | AUTHORITY HOLDPOINT