## res
type | name | values | prefix | postfix | usage count | user addable | template name | Resource Id
checklist | Install Fire Service (In-ground)
section | Details
checkpoint | Installation complies with latest revision of AS/NZS-1221
checkpoint | Installation complies with current drawings & specifications
checkpoint | All pipes, fittings, materials & associated systems were used are in accordance to manufacturer instructions
checkpoint | Check all, pipework, fittings, connections, etc for damage or leaks
checkpoint | Check materials & joining/ installation methods are in accordance to manufacturer instructions
checkpoint | Check thrust blocks
checkpoint | Check pipework is clear of debris
checkpoint | Check pipe trench marking tape
checkpoint | Check trench backfill & compaction
checkpoint | Ensure that system is pressure tested
checkpoint | Area to be cleaned before worker departs
checkpoint | Ensure that installation photographs have been taken
checklist | Install Gas Services (In-ground)
section | Details
checkpoint | Installation complies with latest revision of AS/NZS 5601.1 (2022)
checkpoint | Installation complies with current drawings & specifications
checkpoint | All pipes, fittings, materials & associated systems were used are in accordance to manufacturer instructions
checkpoint | Check all, pipework, fittings, connections, etc for damage or leaks
checkpoint | Check materials & joining methods are in accordance to manufacturer instructions
checkpoint | Check pipework is clear of debris
checkpoint | Check pipe trench marking tape
checkpoint | Check trench backfill & compaction
checkpoint | Ensure that system is pressure tested
checkpoint | Area to be cleaned before worker departs
checkpoint | Ensure that installation photographs have been taken
checklist | Install Water Services (In-ground)
section | Details
checkpoint | Installation complies with latest revision of AS/NZS-3500 (2021) Parts 1 - 4
checkpoint | Installation complies with current drawings & specifications
checkpoint | All pipes, fittings, materials & associated systems were used are in accordance to manufacturer instructions
checkpoint | Check all, pipework, fittings, connections, etc for damage or leaks
checkpoint | Check materials & joining methods are in accordance to manufacturer instructions
checkpoint | Check alignments & levels
checkpoint | Check thrust blocks
checkpoint | Check pipework is clear of debris
checkpoint | Check trench backfill & compaction
checkpoint | Ensure that system is pressure tested
checkpoint | Area to be cleaned before worker departs
checkpoint | Ensure that installation photographs have been taken
checklist | Install Recycled Water Services (In-ground)
section | Details
checkpoint | Installation complies with latest revision of AS/NZS-3500 (2021) Parts 1 - 4
checkpoint | Installation complies with current drawings & specifications
checkpoint | All pipes, fittings, materials & associated systems were used are in accordance to manufacturer instructions
checkpoint | Check all, pipework, fittings, connections, etc for damage or leaks
checkpoint | Check materials & joining methods are in accordance to manufacturer instructions
checkpoint | Check thrust blocks
checkpoint | Check pipework is clear of debris
checkpoint | Check pipe trench marking tape
checkpoint | Check trench backfill & compaction
checkpoint | Ensure that system is pressure tested
checkpoint | Area to be cleaned before worker departs
checkpoint | Ensure that installation photographs have been taken
checklist | Install Sewer Drainage (In-ground)
section | Details
checkpoint | Installation complies with latest revision of AS/NZS-3500 (2021) Parts 1 - 4
checkpoint | Installation complies with current drawings & specifications
checkpoint | All pipes, fittings, materials & associated systems were used are in accordance to manufacturer instructions
checkpoint | Check all, pipework, fittings, connections, etc for damage or leaks
checkpoint | Check materials & joining/ installation methods are in accordance to manufacturer instructions
checkpoint | Check alignments, levels, grades, etc
checkpoint | Check pipework & traps are clear of debris
checkpoint | Check trench backfill & compaction
checkpoint | Check pre-slab CCTV recording
checkpoint | Ensure that system is pressure tested
checkpoint | Area to be cleaned before worker departs
checkpoint | Ensure that installation photographs have been taken
checklist | Install Storm Water Drainage (In-ground)
section | Details
checkpoint | Installation complies with latest revision of AS/NZS-3500 (2021) Parts 1 - 4
checkpoint | Installation complies with current drawings & specifications
checkpoint | All pipes, fittings, materials & associated systems were used are in accordance to manufacturer instructions
checkpoint | Check all, pipework, fittings, connections, etc for damage or leaks
checkpoint | Check materials & joining methods are in accordance to manufacturer instructions
checkpoint | Check alignments, levels, grades, etc
checkpoint | Check pipework & traps are clear of debris
checkpoint | Check trench backfill & compaction
checkpoint | Check pre-slab CCTV recording
checkpoint | Ensure that system is pressure tested
checkpoint | Area to be cleaned before worker departs
checkpoint | Ensure that installation photographs have been taken
checklist | Install Trade Waste Drainage (In-ground)
section | Details
checkpoint | Installation complies with latest revision of AS/NZS-3500 (2021) Parts 1 - 4
checkpoint | Installation complies with current drawings & specifications
checkpoint | All pipes, fittings, materials & associated systems were used are in accordance to manufacturer instructions
checkpoint | Check all, pipework, fittings, connections, etc for damage or leaks
checkpoint | Check materials & joining methods are in accordance to manufacturer instructions
checkpoint | Check alignments, levels, grades, etc
checkpoint | Check pipework & traps are clear of debris
checkpoint | Check trench backfill & compaction
checkpoint | Check pre-slab CCTV recording
checkpoint | Ensure that system is pressure tested
checkpoint | Area to be cleaned before worker departs
checkpoint | Ensure that installation photographs have been taken and the system pressure tested
checklist | Rough In - Above Ground High Level Mains & Riser Installations (Hot Water, Cold Water, Recycled Water, Gas, Pump Services, Fire Services)
section | Details
checkpoint | Installation complies with latest revision of Australian Standards
checkpoint | Installation complies with current drawings & specifications
checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
checkpoint | Setout & alignment as per drawing
checkpoint | Welding / pressfit / push fit / witness marks (as per AS 3500.1)
checkpoint | Support & fixings checked (acoustic / seismic / water hammer/ silicone)
checkpoint | Pipework installation checked against standards (as per AS 3500.1)
checkpoint | Check no cross connection
checkpoint | Pipe risers water sealed per floor & capped off to prevent damage
checkpoint | Pressure test water lines to (1500kpa)
checkpoint | Identification of services
checkpoint | Check floor/wall penetration fire proofing
checkpoint | Ensure that installation photographs have been taken
checkpoint | Final sign off - Pass when happy to proceed (Any issues please comment & Add photos below)
checkpoint | Area to be cleaned before worker departs
checkpoint | Ensure that installation photographs have been taken
checklist | Rough In - Above Ground High Level (Sewer, Storm Water, Vents, Stacks)
section | Details
checkpoint | Installation complies with latest revision of Australian Standards
checkpoint | Installation complies with current drawings & specifications
checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
checkpoint | Setout & alignment as per drawing
checkpoint | Support & fixings checked (acoustic / seismic / water hammer/ silicone)
checkpoint | Pipework installation checked against standards (as per AS 3500.1)
checkpoint | Pipe risers water sealed per floor & capped off to prevent damage
checkpoint | Check all, pipework, fittings, connections, etc for damage or leaks
checkpoint | Check materials & joining methods
checkpoint | Check alignments, levels, grades, etc
checkpoint | Check pipe clips, hangers, brackets & fixings for correct size, spacing & pipe separation
checkpoint | Check expansion joints and anchor points
checkpoint | Check inspection openings
checkpoint | Check pipework is clear of debris
checkpoint | Check open ends are sealed
checkpoint | Check acoustic insulation
checkpoint | Check pipe labelling
checkpoint | Check floor/wall penetration fire proofing
checkpoint | Check vents are run to atmosphere and are complete
checkpoint | Ensure that installation photographs have been taken
checkpoint | Pressure test
checkpoint | Identification of services
checkpoint | Check floor/wall penetration fire proofing
checkpoint | Ensure that installation photographs have been taken
checkpoint | Final sign off - Pass when happy to proceed (Any issues please comment & Add photos below)
checkpoint | Area to be cleaned before worker departs
checkpoint | Ensure that installation photographs have been taken
checklist | In Wall Rough-ins (Cold Water, Hot Water, Recycled Water, Gas, Waste, Vents, Fire Services)
section | Details
checkpoint | Installation complies with latest revision of AS/NZS-3500 (2021) Parts 1 - 4
checkpoint | Installation complies with current drawings & specifications
checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
checkpoint | Check all, pipework, fittings, connections, etc for damage or leaks
checkpoint | Check crimp fittings & joints
checkpoint | Check for cross connections
checkpoint | Check alignment & levels
checkpoint | Check materials & joining methods
checkpoint | Check pipe clips, hangers, brackets & fixings for correct size, spacing & pipe separation
checkpoint | Check in-wall mixer bodies & lugged elbows
checkpoint | Check in-wall fixture mounting brackets & concealed cisterns
checkpoint | Check fixture fit-off noggins
checkpoint | Check sharp edge pipe protection
checkpoint | Ensure Recycled Water Inspections has been booked
checkpoint | Ensure that system is pressure tested
checkpoint | Area to be cleaned before worker departs
checkpoint | Ensure that installation photographs have been taken
checklist | Fit Off & Commissioning
section | Details
checkpoint | Installation complies with latest revision of AS/NZS-3500 (2021) Parts 1 - 4 &/or AS/NZS 5601.1 (2022)
checkpoint | Installation complies with current drawings & specifications
checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
checkpoint | Thoroughly check all pipework, fittings, connections, etc for damage or water leaks
checkpoint | Check for any damage or missing components
checkpoint | Check level & alignment of all fixtures & tapware
checkpoint | Check all fixtures, tapware & components are securely fixed
checkpoint | Check all mini-stops and valves are fully open
checkpoint | Check all pressure reduction & non-return valves
checkpoint | Check all flexible connections are not twisted or kinked
checkpoint | Check for water for cross connections
checkpoint | Check fixture wastes & connections
checkpoint | Check dishwasher drain hose is looped hard-up under bench-top
checkpoint | Check pipework & all traps are clear of debris
checkpoint | Check AAV is installed hard-up under bench-top
checkpoint | Check future connection water valves are securely capped (fridge/washing machine stops)
checkpoint | Check hot water delivery temperature
checkpoint | Check TV do not exceed 50°C
checkpoint | Check TMV do not exceed 45°C
checkpoint | Check dishwasher function through short cycle
checkpoint | Check gas valves & regulators
checkpoint | Check gas flame stop device
checkpoint | Check all gas burner functions
checkpoint | Check emergency gas shut-off valve is fitted
checkpoint | Check balcony hose tap is securely fixed
checkpoint | Check balcony floor grate is clear
checkpoint | Check all downpipes & overflows are fitted correctly
checkpoint | Check all vents are finished & weather proofed
checkpoint | Check all fixtures & tapware function correctly
checkpoint | Check receipt of all Authority sign-off & acceptance documentation
checkpoint | Check receipt of all manufacturers warranty documentation & owners manuals
checkpoint | Confirm area has been left clean
checkpoint | Ensure that commissioning photographs have been taken
checklist | Install Backflow Prevention Device
section | Details
checkpoint | Installation complies with latest revision of AS/NZS-3500 (2021) Parts 1 - 4
checkpoint | Installation complies with current drawings & specifications
checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
checkpoint | Check all, pipework, fittings, connections, etc for damage or leaks
checkpoint | Check materials & joining methods
checkpoint | Check alignments & levels
checkpoint | Check pipe clips, hangers, brackets & fixings for correct size, spacing & pipe separation
checkpoint | Check isolation valves, filters, connections, etc
checkpoint | Check pressure relief discharges to drainage
checkpoint | Confirm area has been left clean
checkpoint | Ensure that installation photographs have been taken
checklist | Commission Backflow Prevention Device
section | Details
checkpoint | Commission Backflow Prevention Device checked off as below:
dropdown | Valve Type: | Reduced Pressure Zone Device,Double Check Valve,Single Check Valve
dropdown | Hazard Type: | High Hazard,Medium Hazard,Low Hazard
textbox | Serial Number:
textbox | Location:
dropdown | Size: | 15mm,20mm,25mm,32mm,40mm,50mm,65mm,80mm,100mm,150mm,225mm
checkpoint | Installation complies with latest revision of AS/NZS-3500 (2021) Parts 1 - 4
checkpoint | Installation complies with current drawings & specifications
checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
checkpoint | Check all, pipework, fittings, connections, etc for damage or leaks
checkpoint | Check valves are fully open
checkpoint | Check inlet water pressure does not exceed manufacturer specification
checkpoint | Check outlet water pressure is as per manufacturer specification
checkpoint | Check pressure relief discharges to drainage
checkpoint | Provide the commissioning report & all plant documentation to this checkpoint
checkpoint | Confirm area has been left clean
checkpoint | Ensure that commissioning photographs have been taken
checklist | Install Cast-in Pipework
section | Details
checkpoint | Installation complies with latest revision of AS/NZS-3500 (2021) Parts 1 - 4
checkpoint | Installation complies with current drawings & specifications
checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
checkpoint | Check all, pipework, fittings, connections, etc for damage or leaks
checkpoint | Check materials & joining methods
checkpoint | Check alignments, levels, grades, etc
checkpoint | Check pipe clips, hangers, brackets & fixings for correct size, spacing & pipe separation
checkpoint | Check surface & floor grated outlets
checkpoint | Check pipework & traps are clear of debris
checkpoint | Check pipe expansion lagging
checkpoint | Check open ends are sealed
checkpoint | Check pre-slab CCTV recording
checkpoint | Confirm area has been left clean
checkpoint | Ensure that installation photographs have been taken
checklist | Installation & Commissioning of Pump Stations (Sewer Pump Stations, Storm Water Pump Stations, Trade Wate Pump Stations)
section | Details
checkpoint | Commission Drainage Pump Station (In-Ground) checked off as below:
dropdown | Type: | Sewer Drainage,Stormwater Drainage,Trade Waste Drainage
textbox | Location:
checkpoint | Installation complies with latest revision of AS/NZS-3500 (2021) Parts 1 - 4
checkpoint | Installation complies with current drawings & specifications
checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
checkpoint | Check all, pipework, fittings, connections, etc for damage or leaks
checkpoint | Check access covers & hatches
checkpoint | Check access ladders & statutory signage
checkpoint | Check pipe connections & venting
checkpoint | Check all pipework, fittings, valves & connections
checkpoint | Check lifting rails & chains
checkpoint | Check float tree or water level sensor is not impeded by water inflow
checkpoint | Check water level set points
checkpoint | Check pump motor rotation
checkpoint | Check dry pump fault
checkpoint | Check low water level fault
checkpoint | Check high water level fault
checkpoint | Check auto pump roll-over
checkpoint | Check delivery flow rates
checkpoint | Check control panel display
checkpoint | Check programmed set points
checkpoint | Check fault warning alarms
checkpoint | Check BMS connection
checkpoint | Check statutory warning signage
checkpoint | Check suppliers commissioning report & all plant documentation
checkpoint | Confirm area has been left clean
checkpoint | Ensure that commissioning photographs have been taken
checklist | Install & Commissioning of Rain Water Storage Tank & Pump
section | Details
checkpoint | Commission Rain Water Storage Tank & Pump checked off as below:
textbox | Tank Capacity:
textbox | Location/Lot Number:
checkpoint | Installation complies with latest revision of AS/NZS-3500 (2021) Parts 1 - 4
checkpoint | Installation complies with current drawings & specifications
checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
checkpoint | Check all, pipework, fittings, connections, etc for damage or leaks
checkpoint | Check all fixing/hold down points
checkpoint | Check isolation valves are fully open & non-return valves flow direction
checkpoint | Check pressure pump & filters for correct operation
checkpoint | Check downpipe connections & tank venting
checkpoint | Check mains water back-up supply
checkpoint | Check tank over-flows to drain
checkpoint | Confirm area has been left clean
checkpoint | Ensure that commissioning photographs have been taken
checklist | Commission Water Tank
section | Details
checkpoint | Commission Water Tank checked off as below:
dropdown | Service Type: | Potable Water,Rain Water,Fire Service Water
dropdown | Position: | Below Ground,Above Ground
textbox | Location:
textbox | Capacity:
checkpoint | Installation complies with latest revision of AS/NZS-3500 (2021) Parts 1 - 4
checkpoint | Installation complies with current drawings & specifications
checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
checkpoint | Check all, pipework, fittings, connections, etc for damage or leaks
checkpoint | Check all fixing/hold down points
checkpoint | Check isolation valves are fully open & non-return valves flow direction
checkpoint | Check access covers & hatches
checkpoint | Check access ladders & statutory signage
checkpoint | Check pipe connections & venting
checkpoint | Check over-flow & connection to drain
checkpoint | Check float tree or water level sensor is not impeded by water inflow
checkpoint | Check water fill physical air break
checkpoint | Check water level set points
checkpoint | Check back-up mains water supply
checkpoint | Check 'Bermad' tank fill valve
checkpoint | Check low level fault
checkpoint | Check high level fault
checkpoint | Check passive over-flow
checkpoint | Check control panel display
checkpoint | Check programmed set points
checkpoint | Check BMS connection
checkpoint | Check statutory warning signage
checkpoint | Provide the suppliers commissioning report & all plant documentation to this checkpoint
checkpoint | Confirm area has been left clean
checkpoint | Ensure that installation photographs have been taken
checklist | Commission Thermostatic Mixing Valves
section | Details
checkpoint | Commission Thermostatic Mixing Valves checked off as below:
textbox | Location:
checkpoint | Installation complies with latest revision of AS/NZS-3500 (2021) Parts 1 - 4
checkpoint | Installation complies with current drawings & specifications
checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
checkpoint | Check all, pipework, fittings, connections, etc for damage or leaks
checkpoint | Check TMV has been installed in a lockable wall box
checkpoint | Check TMV has been installed in the room it services and can be readily accessed from floor level
checkpoint | Check water temperature does not exceed 45°C for disabled persons
checkpoint | Confirm area has been left clean
checkpoint | Ensure photograph has been taken of thermometer in water flow at maximum temperature
checklist | Install Fire Booster Assembly
section | Details
checkpoint | Installation complies with latest revision of AS/NZS-3500 (2021) Parts 1 - 4
checkpoint | Installation complies with current drawings & specifications
checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
checkpoint | Check all, pipework, fittings, connections, etc for damage or leaks
checkpoint | Check materials & joining methods
checkpoint | Check alignments & levels
checkpoint | Check pipe brackets & supports are correctly positioned & bedded
checkpoint | Check thrust blocks
checkpoint | Check trench depth, bedding, service clearances, minimum cover, etc
checkpoint | Check suction valve assembly
checkpoint | Check booster valve assembly
checkpoint | Check hydrant hose assemblies
checkpoint | Check monitored valves & connections
checkpoint | Check isolation valves, connections, etc
checkpoint | Check gauge lines
checkpoint | Check pipework is clear of debris
checkpoint | Check pipe trench marking tape
checkpoint | Check trench backfill & compaction
checkpoint | Check pipe labelling
checkpoint | Confirm area has been left clean
checkpoint | Ensure that installation photographs have been taken
checklist | Install Fire Service (Hose Reels)
section | Details
checkpoint | Installation complies with latest revision of AS/NZS-1221
checkpoint | Installation complies with current drawings & specifications
checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
checkpoint | Check all, pipework, fittings, connections, etc for damage or leaks
checkpoint | Check hose reel is mounted securely
checkpoint | Check hose reel spindle heights are 1500mm above FSL
checkpoint | Check hose reel cabinets conform (if specified)
checkpoint | Check roll-groove couplings
checkpoint | Check crimp fittings & joints
checkpoint | Check materials & joining methods
checkpoint | Check pipe specification markings are visible
checkpoint | Check alignments & levels
checkpoint | Check pipe clips, hangers, brackets & fixings for correct size, spacing & pipe separation
checkpoint | Check isolation valves, connections,etc
checkpoint | Check pipe labelling
checkpoint | Confirm area has been left clean
checkpoint | Ensure that installation photographs have been taken
checklist | Install Fire Service (Hydrants)
section | Details
checkpoint | Installation complies with latest revision of AS/NZS-1221
checkpoint | Installation complies with current drawings & specifications
checkpoint | All pipes, fittings, materials & associated systems were used in accordance to manufacturer instructions
checkpoint | Check all, pipework, fittings, connections, etc for damage or leaks
checkpoint | Check hydrant is mounted securely.
checkpoint | Check above ground hydrants height are between 750mm to 1200mm above FSL
checkpoint | Check hydrant cabinets conform (if specified)
checkpoint | Check in-ground hydrant heads & covers conform
checkpoint | Check roll-groove couplings
checkpoint | Check materials & joining methods
checkpoint | Check pipe specification markings are visible
checkpoint | Check alignments & levels
checkpoint | Check pipe clips, hangers, brackets & fixings for correct size, spacing & pipe separation
checkpoint | Check isolation valves, connections, valve covers, etc
checkpoint | Check monitored valves & connections
checkpoint | Check pipe labelling
checkpoint | Confirm area has been left clean
checkpoint | Ensure that installation photographs have been taken