## Master List Templates
Id | Type | Name | Values | Prompting Name | Prefix
0588dd2a-d440-5502-9cc1-2a984d2e6c8d | checklist | Add Project Photos |  | Project Photos
b3a47312-e99b-57a3-b655-b50313c2200a | checkpoint | Attach Photos and Comments
6f002ec6-dce0-558c-8fdb-30e47eb710bb | checklist | Day Labour Docket |  | Day Labour Docket
bebe4fd5-1509-5079-aaeb-c20fb5659019 | checkpoint | Day Docket Details
5c7662b9-6d67-5076-b081-34174d83b306 | textbox | Project Name
b7294f2b-5cf0-527e-907f-9d7ee8f6d1ea | textbox | Job Number
87975a9c-dc3f-53d8-b468-d8bf91570174 | textbox | Site Instruction
fd3b561b-2193-5a5b-b7e3-1de40a68ce7b | textbox | Geschke Reference / Subject
43851586-96a4-59f4-8761-4f20e0c93511 | textbox | Requested by name
bf76ba28-5cd9-5a95-8e48-c79ba2487249 | textbox | Requested by company
2340b828-e42a-5a5c-9fb2-c2644dc2d5db | textbox | Brief description - scope, location, other contractor involvement
79e98b40-db35-5c2a-8348-61e9ec1a4f7a | note | Attached - requester signature
5993b08a-e5d6-5cb6-b10b-38646360139f | note | Attached - photos before
cf644e64-73f9-5910-a520-92d88986c35a | note | Attached - photos after
8b7b2956-7179-5850-a84f-80a41f74e47d | checklist | QA 7_Commissioning Test Report |  | Commissioning Test Report
e4899f25-d436-5b4a-b4c3-dd5cb6b2362a | checkpoint | Commissioning Test Report:
d327703b-f3ba-539b-b251-1bdae31b11c9 | textbox | Zone/Grid:
8ae0555c-198f-58d7-96f1-34792d52d64d | textbox | Drawing No.:
036bd35e-308e-50b4-83a8-10b735e5014c | textbox | Rev.:
020f181c-f792-55c0-b912-56202f3cdf0a | checkpoint | Item: FIXTURE OPERATION - Pans, Basins, Sinks, Other
20eb13e0-a11b-584b-9ebd-a15417a134c9 | note | Test:
3db11513-05c7-532b-bf55-bbe4827a2d9d | note | Performance Test CL 2.20
0d887cae-55e9-588e-b235-627fdc5d12a2 | note | Fill fixture with water remove plug
53e6629a-e167-5ba9-abb0-d6d8c9c0032f | note | Test for:
648a4c5e-2393-5020-8f35-eddfe179e4a9 | note | Leaks
013055b0-bd75-5aa6-92df-0cac740afe59 | note | Loss of water
d293626f-d41b-5f0d-a1e7-4d20db791d6a | note | Seal in Trap
133d001f-2654-5fff-bbc6-13c0a0704435 | note | Induce siphonage in trap of adjacent fixture
20c8db35-41ba-50cb-b99e-5f79d25f9629 | note | Complete draining of fixture
31b8d3d0-2c0d-527d-a988-2732a1665c5f | textbox | OK:
7316e753-a568-52c8-ad94-1fe21ca06772 | textbox | Not OK:
431ab26f-1b7b-55ad-a431-4e10dad53284 | checkpoint | Item: Water Supply
67c87bc5-d6b0-5c1d-9155-8433a522d136 | note | Test:
2d614b85-72c4-5b5c-adfc-d0c3c663cca9 | note | Performance Test CL 2.20
b250e969-b551-5d80-be4b-dffa7693ca9a | note | Check for adequate water volume.
73abf86f-25d8-595d-b0a6-75317c670dd1 | note | Flush out pipework
452b504a-081d-59c2-ad5c-10618af31089 | note | Clean aerator
ae730b29-0279-579f-8f30-919295fd7d51 | note | Water hammer
30e248a3-9146-5ac6-ab8b-e9ce68ed56dc | textbox | OK:
ecd810a2-8f89-5453-95ae-8d9c6982aae1 | textbox | Not OK:
5fb85726-ea98-588d-b15a-923847490066 | checkpoint | Item: Flush Performance
c9949532-2826-5289-8b56-aab0ff1a7b0c | note | Test:
b843bc61-cc18-5cbf-9683-a9b62bfc4e59 | note | Performance Test
0f892e15-28b1-5230-9deb-3ac3e1966196 | note | Check for:
38ece3ca-011e-5795-9208-065bd616d4c6 | note | Water Volume
dc85abcd-fc9b-50da-a62b-2e6fe40476c8 | note | Duration of flush
0aee1722-0560-553f-bb4c-bf1ee62c2a5e | note | Flush out pipework
9ae2a9d6-01d8-5d88-8008-cdbb6dee0b7d | note | Water hammer
3c4f2bd7-2a10-5147-bbe5-c1f81fb7673f | textbox | OK:
db3a6357-1846-5330-9f4f-e5142d47ff66 | textbox | Not OK:
12c36d30-1d36-54aa-9a51-c192e19f7df5 | checkpoint | Other
00d279f7-4c10-5994-9fa6-fb85ee3b1c7c | checklist | QA 9_Non-Conformance and Rectification Report |  | Non-Conformance and Rectification Report
3dbb6f2e-c870-5aa5-87b6-39ec9cfa4da3 | checkpoint | Non-Conformance and Rectification Report Details:
497480bc-16f9-57d1-a38d-b53f285ead12 | textbox | Drawing No./Rev:
6c7020c8-cb4b-5056-aedc-1eda68789ef9 | textbox | Zone or Grid:
c1b1944f-9e73-5dfc-85e7-ed80a4769931 | textbox | Issued To:
ec26a073-1fc2-5a02-a43e-1a4975f7246c | textbox | Item Not Conforming
0344f07b-d886-595d-ac05-a2e52a3647ab | textbox | Reason For Non-Conformance
6a8fe17b-aeec-5947-a7ad-703f786a7e75 | textbox | Consequences: Impact On Time, Cost Co-Ordination Etc
162acb0a-6221-5ed8-b32e-8bf9074941a4 | textbox | Action Required:
49bb3ead-9d10-58ba-b134-b5dc0c361c05 | textbox | Date:
41c65d3b-845e-51e2-b40e-83856850ea32 | textbox | Rectification:
b80c061a-a1e2-5ec9-a894-87917f2ade88 | textbox | Date:
2942d0e2-7101-5037-8548-4a3587576906 | note | Note: Non-conformance register to be updated
af4c34c3-620e-5cf6-89ef-3fb11c6178c2 | checklist | QA 11_Equipment Calibration Register |  | Equipment Calibration Register
a0b01591-964f-5515-85c6-7f96b57877d7 | checkpoint | 1
b4d2c565-6cee-5beb-9f2a-9a346000f629 | textbox | Equipment Type:
be6ab2aa-d446-582d-a849-bfe836eb24eb | textbox | Manufacturer:
47593f44-3f6c-5547-84c2-26e0bbe47831 | textbox | Model and Type:
5941931a-1aa8-58e8-be93-967243c88d47 | textbox | Serial No.:
c86e3e82-4a80-595b-9779-716c2b19f620 | textbox | Next Service Due:
80eb3b16-184b-5f92-932d-71403b994572 | checkpoint | 2
0306dcf0-68f3-549c-9016-f7af3b1c6ec3 | textbox | Equipment Type:
33c0b8b5-8807-5a36-8e57-78e3b2cffd0b | textbox | Manufacturer:
9bc41edb-c3df-5933-9cb9-88e19a0a352f | textbox | Model and Type:
95d17765-6174-52b6-af43-d2574c3cf7c2 | textbox | Serial No.:
974f94f4-32e3-5b07-b53e-96a207c4e5a9 | textbox | Next Service Due:
7a173f6c-500c-553d-b74a-85afb565eb50 | checkpoint | 3
76a02e6d-6074-56d0-87c9-bedee5e2fd92 | textbox | Equipment Type:
191cf691-0333-562f-84d4-a19180c8c35e | textbox | Manufacturer:
f4614282-7975-5463-b1d2-174c3a96397e | textbox | Model and Type:
c30ae13d-364b-5dbc-b392-cb79271ea4f3 | textbox | Serial No.:
52bb628b-cc74-5d15-9174-7a2093a79f63 | textbox | Next Service Due:
b911b1b9-6725-5360-8e28-f6a01e7ce249 | checkpoint | 4
3707671d-ca0d-57a3-adeb-787ad49847d6 | textbox | Equipment Type:
6b916005-e6be-5e93-abc6-40dfef2a82c7 | textbox | Manufacturer:
2ae7293d-67a1-55c5-8559-1f1c7f0191b0 | textbox | Model and Type:
2b5afd9c-bed7-563d-9fba-8740e3731118 | textbox | Serial No.:
b1afa72f-9aca-5386-9ef9-0af842e99e74 | textbox | Next Service Due:
24dce8d0-3e3b-5c3c-b560-2a93082053b4 | checkpoint | 5
069ace06-2f9e-5ec9-b970-a842724880ea | textbox | Equipment Type:
29c5bf83-58d0-556f-92ca-4404d9c3b2bf | textbox | Manufacturer:
3f11dbde-edf2-5bbd-8c1a-ca5495acda6f | textbox | Model and Type:
502d77c5-8f9b-582c-8fe8-11abd0c65c6f | textbox | Serial No.:
bd6fb2a4-219a-5322-ba03-0382fa934a03 | textbox | Next Service Due:
e4ee39db-2ed2-56d4-9d1e-70d41b06e452 | checkpoint | 6
e8563fe9-3fbd-5210-841b-411bcfb2df35 | textbox | Equipment Type:
a2683913-abd9-5c90-9c8b-40899f0ea4c3 | textbox | Manufacturer:
8b366f34-db94-5c4d-a37b-98b8864a9024 | textbox | Model and Type:
556b2989-7730-5701-9d81-b0d8702a4a5b | textbox | Serial No.:
3bdbd6e4-a10e-5320-a32f-41e2025dab39 | textbox | Next Service Due:
928a8d37-d6be-57e8-9819-49b7c2a1d92d | checkpoint | 7
d9b32f47-74f7-5c54-86e7-29b5eb68f311 | textbox | Equipment Type:
c25f1b07-ccd9-545d-bcf1-70f7de3772ae | textbox | Manufacturer:
557ae0af-ae79-52fe-ac32-5ae783bfbd24 | textbox | Model and Type:
da86f339-f33c-5594-ad94-a07efba683a0 | textbox | Serial No.:
34b3d541-2c85-5e93-8711-8208ef1ae94c | textbox | Next Service Due:
b556b88f-cfc7-5c58-a0d3-21aa1fcf562f | checkpoint | 8
45af7411-27d7-5290-a4f3-e3c060b1732d | textbox | Equipment Type:
439911d9-6d5a-58b9-9d9a-e5fbb711d9e6 | textbox | Manufacturer:
fbc2bbb8-1c08-5ed5-b94a-64d9a782f33c | textbox | Model and Type:
ac8e6743-b058-5e6f-bfa5-336be58119a7 | textbox | Serial No.:
50731a42-0a37-550f-aacf-70906c6fcaa9 | textbox | Next Service Due:
f81a9cad-2202-53fc-aea8-cbaacb40a1ec | checkpoint | 9
1663dd13-3559-5831-919c-49102d9fec96 | textbox | Equipment Type:
c8f55def-8873-5711-ad58-9ea5462b3445 | textbox | Manufacturer:
fac8902a-ff44-5501-b258-36913a18b048 | textbox | Model and Type:
9e3de27c-9b55-5e59-bc48-2a233c014957 | textbox | Serial No.:
38356761-d8a1-5f92-89db-89d0b9e489a8 | textbox | Next Service Due:
e48a2151-c0b0-593e-afe7-b90d947c1f50 | checkpoint | 10
f44f60a4-ad2e-59a7-83c3-f267d022f77d | textbox | Equipment Type:
f1ff474c-26e8-5ddf-909d-0cdb53b8d9dd | textbox | Manufacturer:
a001f1d9-90a7-5634-9641-fc9b22fc172d | textbox | Model and Type:
ca7d7f0c-915c-5e5b-9c73-6e0c60b161d6 | textbox | Serial No.:
caafb20b-52c7-5415-9dbe-4f70c7fc52a1 | textbox | Next Service Due:
0031234f-9912-46c3-a078-f477e6517a29 | checklist | QA 13_Backflow Prevention Device (RPZD) Test Report |  | QA 13_Backflow Prevention Device (RPZD) Test Report
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
b8ce494d-efac-43d4-9d80-b639b58e2925 | checkpoint | RPZD Test Report
5663cc76-db9b-5f5d-a20d-bdbb9c98bcb8 | textbox | Owner/Occupier:
09a521b5-ae50-5630-b1bb-fa2fd826257f | textbox | Address:
7ac76895-8073-5f8b-9184-f046b607fec4 | button | Type of Test: | Installation Test,Annual Test
ebb17e6d-febc-5d3e-b342-32ee83e9ff17 | textbox | Location of Device:
6582af23-52bb-561a-8e55-1026c4fa32a3 | textbox | Authorised Tester Name:
35ce7278-11b7-5893-b9a7-3733b83b11aa | textbox | Test Kit Serial No.:
ee5d85e9-8ba8-526d-ba29-761100c44c99 | textbox | Tester Licence No.:
f51c15d9-98c3-5c06-82c5-44a044053943 | textbox | Test Kit Calibration Date:
f7055ebe-9218-5e53-8dad-b0f6c61bdf86 | textbox | Date of Test:
831c4371-9c72-48d4-9d9b-c7274e4d1ae3 | checkpoint | Device Details
04b4b94b-69b2-59b7-ae3e-e681ed56aa64 | button | Permission to Isolate Water Supply: | Yes,No
ebf53778-8429-51f3-bc00-a38176ecdda0 | textbox | Make:
844cefa4-b2e4-513f-b71c-724fe949c74f | textbox | Size (mm):
6914e388-90b9-5e57-aee6-7a21bbd2ec4c | textbox | Model No.:
0e53e44a-fe1d-5205-96c9-68c52a2e4844 | textbox | Serial No:
804baea5-c619-53a1-b55b-ad8fcee304b5 | button | Is the device installed high enough to prevent ingress of any possible contaminated water? | Yes,No
84fb6cb6-d3ae-5ee3-bfd1-aa2ea89cadef | button | Protection: | Containment Protection,Individual Protection,Zone Protection
72d77dfa-afa2-5e9a-a923-62dd52895274 | button | Strainer Installed: | Yes,No
7a2e853a-f751-5f00-ac41-3a70d1c2516a | button | Strainer Cleaned: | Yes,No
fedd1479-1815-54f7-9b74-819c273ffaba | button | Device Type: | RPZD (Reduced Pressure Zone Device),Double Check Valve
d080bd4b-6553-4727-85a6-ff685b5d0a81 | checkpoint | Testing Results
3740b007-e9ad-5279-b6f6-172f9ab6c28d | note | Check Valve 1
a8b0c594-7454-584c-9f68-2d145b8a2506 | textbox | Close tight at ___ kpa (min 35kpa) OR Leaked
b8029d08-a8c0-53f1-86ea-7714b78a8794 | note | Check Valve 2
23b81140-fc6b-5a86-8d2b-c377788a19e9 | textbox | Close tight at ___ kpa (min 7kpa) OR Leaked
a1330509-36ad-5e37-92ea-716ee34ec002 | note | Relief Valve
71e07d93-8bb8-53e7-9ae0-2665ffb50bb2 | textbox | Opened at ___ kpa (min 14kpa) OR Leaked
b32da936-ea01-52a8-ae2b-3712dcbe4726 | button | Reason for the device failure | Incorrect position,Foreign material in the device,Incorrect installation,Spring wear damage,Seal or Rubber Damage,Other
8fff143e-c9ec-4f36-92b8-57d1ba24df09 | checkpoint | Test After Maintenance
a2123714-4af2-542a-b5ae-dad97b56e44d | note | Check Valve 1
07f5d6ff-a1d4-5e11-8cb5-81d26e7f1f91 | textbox | Close tight at ___ kpa (min 35kpa) OR Leaked
f8cd9cd2-fae3-59d8-b14a-7efd3ec85fa0 | note | Check Valve 2
06afcb01-b5d6-52e3-a9fc-23b56c98bce4 | textbox | Close tight at ___ kpa (min 7kpa) OR Leaked
bb1f99f4-93e6-5af3-8c27-513e225bb0f3 | note | Relief Valve
cdf982d2-dfec-51c3-9b47-e646ef4823e3 | textbox | Opened at ___ kpa (min 14kpa) OR Leaked
7fcc5821-83b2-5605-8c78-3e7a7686effb | button | Water turned back on | Yes,No
0a66f083-63a8-5ea7-bf3f-4e8e1de2bf50 | textbox | Describe the maintenance:
943abf6a-31dd-5342-a500-69d1a2674cbf | textbox | Parts used in repair:
3e7b70c9-946e-468b-acb1-41ad5f166ca1 | checkpoint | Results
2f05aa93-9e2c-505e-b0d4-4f9a21a81e85 | button | Is the device installed correctly | Yes,No
01afc502-46d5-50b5-a6ce-a02984e4b9a7 | button | Test Result | Pass,Fail
b0a3e5e9-e77b-4b69-b104-8f369fd5ba2f | checkpoint | Sign Off
3d4c6bb1-563a-57a1-b66f-6ec85a824f20 | textbox | Tester Name:
9c45721c-b2a1-56d6-b786-a00b10308eb9 | textbox | Signature:
bfa43644-b1fc-51ba-914b-2932b5d6c4ad | date | Date:
c6bf1c14-4c30-5052-9dc4-982eb73acfc1 | checklist | QA 16_PE Electrofusion Welding - Field Operational Sheet |  | PE Electrofusion Welding - Field Operational Sheet
286304e4-d491-530e-a879-79048a305a1e | checkpoint | Operator Details
d09890f7-646a-5143-b4f3-8969ff90db97 | textbox | Name
57467f91-fde3-52e0-b267-7ab820283d74 | textbox | ID No.
ceea6ef6-6308-537d-9437-f8e63b6f21ac | textbox | Company
8daea862-b26a-564a-a7a8-38196260bc8f | textbox | Address
66b87a78-074a-570c-b59f-8aeb22d53d0b | checkpoint | Welding Machine Details
6d41d224-e2e5-546b-8b09-be07b8add981 | textbox | Manufacturer
c6e1c48b-a115-580a-8f7c-18a9fbd4a3b4 | textbox | Type/Model
a6161095-5a26-5337-9adb-93ec7a6c00bf | textbox | Serial Number
f7e39ce5-586e-5ced-9b42-366b61773496 | textbox | Year Built
07064409-656f-5d8e-ba2c-57154117505c | checkpoint | Actual Pipe Size
f984d670-cda8-5f18-bf60-2e0f2a47d258 | textbox | Type
494cb07f-d5a8-5039-a6fd-ded454b33aaf | textbox | Brand
c426b190-d5fb-50b3-8329-bcc5dc0c6c93 | textbox | En
a28c3702-0c63-5953-ba84-af92909d5e43 | textbox | OD
6aeaed54-c92c-599c-9731-2f4ac78f2885 | textbox | Ovality %
e9e19a09-af9a-5dd9-add0-04e44c20d339 | checkpoint | Fitting Data
31760176-42f8-5b20-b8d5-f13e4fe89024 | textbox | Brand
183249e9-b8ac-5e48-b375-03c842a1ffce | textbox | Type (Coupling, Tee, Reducer etc.)
a1ea026f-d998-57bc-8662-5ada0860350c | checkpoint | Unit Setting
333602de-d20b-5569-8fe7-680b88bca173 | textbox | Manual
8a211235-6a36-557d-ba86-0d8a0adc44bd | textbox | Automatic
ee9dc83b-144a-596a-9418-efc47324c835 | checkpoint | Preparation
8d969b29-d822-5ebc-947a-f3de632ff619 | textbox | Cleaned and Peeled
482fee68-93a2-5ef0-8a4c-9456b9d680a3 | textbox | Pipe/Fitting Clamped
d851523d-87b5-5bee-ad87-5b7e17d639fd | checkpoint | Welding Times
0577cc8d-f3e3-52e5-ac80-91e18b37b737 | textbox | Joining Seconds
826b512c-5d90-56c1-a74b-8e4e5876e703 | textbox | Cooling Minutes
b99ca8e0-f16a-50d3-8db6-7aba95e6486a | checkpoint | Conditions
32a3c930-dbd3-59a5-a937-863e388c83d9 | textbox | Ambient Temp
0bcf9c4f-5183-5a0a-a5b5-f3a6c2ace2ef | textbox | Weather
81ba753f-caa6-55ba-ab86-854ee1f6d67d | textbox | Preventive Measures
a4055e15-3d26-5e25-84be-c62c1b1d24b9 | checkpoint | Power
af7e98e3-5e08-5b7c-a821-fcde34042cd0 | textbox | Mains
7dda302b-01bc-53f8-a5ab-dbc76f069c6f | textbox | Gen Set
f39d7021-bda5-5819-9f3a-a3f34b9c769a | checkpoint | Operator Sign Off
7f452676-6d64-5449-800f-e282a376cb40 | checklist | QA 17_Water Meter Accuracy Test |  | Water Meter Accuracy Test
47148228-30da-5bbc-8da8-3cc2b8857bca | checkpoint | Water Meter Accuracy Test Details:
3314fb28-6004-50b1-9780-eefb1b71510e | textbox | Date:
430b7245-e716-513b-9047-9c4e4fc6ca44 | textbox | Project:
208dde16-7f35-52ce-b4aa-bf9e249d1072 | textbox | Location of Water Meter:
72a0013a-b8c3-5856-a4c3-a54ed8e566ff | textbox | ID Number of Water Meter:
06f570b6-b549-598c-991a-21c07d01fa4b | textbox | Model & Manufacturer:
fdbfa2df-492b-534b-b8f1-f7cc5a3e7405 | textbox | Current Counter Reading:
e89edae7-6e74-57cf-b7c7-7e878428911c | textbox | Zone/Appliances to be Metered:
3e193013-f935-59a7-852f-40ae23dec67e | textbox | Pulse Rate:
857503a4-a5b8-5ea0-b22e-6414f76d17d2 | checkpoint | Measurement Apparatus
1e41da32-9761-534a-960e-e0f9e7e6b264 | tickbox | Bucket
360faded-a3ea-5cfa-a0fb-f1b75e6c2aa8 | textbox | Bucket Size
ea7ae63a-b9ad-5afa-9fe1-43aed4f6003e | tickbox | Water Meter
0e4bdf03-1f7b-5f0b-aab1-898e3d630651 | textbox | Calibrated Date:
649b76ce-264e-5376-aecb-d46f59de9eda | textbox | Other
0faa6954-3d69-5f2e-8d5b-27a52358f137 | checkpoint | Measurement Method
3622e18a-b1b3-56de-bf4f-0028521a67c5 | note | Isolate all fixings
03c1d46e-10a6-5a14-9b1c-a3947a0e30c9 | note | Place bucket at outlet of fixture and fill
ccb3121d-2dfa-5a79-a724-46ce9a34d3c4 | note | Fill in completed counter reading and minus "current reading" to measure accuracy
32d2480b-6c21-5252-87db-7f5c7291ba03 | textbox | Completed Counter Reading:
d7938c77-17a2-5fd2-95b5-d442fcd94056 | note | Accuracy
a90c66bb-a98c-5fb1-9288-5e92871b9098 | textbox | OK
39d33286-e360-576e-ba75-e0e81e5c5b15 | textbox | FAILED
aec8060c-cb17-5fa6-98d5-69f07b2c8640 | note | Replace Counter and Re-Test
c14044e9-0ffe-5ba8-910d-9271ac1424a1 | textbox | OK
b6b31f97-d145-51b1-9ab0-d60631df6e69 | textbox | FAILED
10225846-1170-53ff-a50b-c95c6d7745f7 | checkpoint | Pulse Check
c96818d2-e638-55e9-a052-1c9937861a16 | note | Method:
6e3c2261-ce63-506b-9a84-1f03bdcf0a8d | note | Connect multimeter to the 2x wire connection points on pulse kit and set multimeter OHMS
c0ffe883-62e1-5c4c-bcae-49e31526dd70 | note | Turn a fixture on and wait for pulse reading on multimeter, then stop flow immediately
f4399fce-a9c1-5503-935a-aa5d1cbb5d4b | note | Measure bucket contents:
502a4ba5-22e3-53f4-8c1d-97cebc66e345 | textbox | Pulse Registered:
9f07c428-edf3-5779-8f6e-58de75fc7371 | note | No Pulse - Install new pulse kit and repeat process
5b8950c5-0956-5cc9-a698-3fa49180f8ad | note | If Pulse registered OK
6c34fdbd-6bdd-5043-82cf-369de26354df | textbox | Pulse Accuracy:
2dc63887-83ae-51bf-84c1-da817edca9d2 | note | (Bucket contents match spec at top of page)
46079bb5-7f41-53aa-930b-73bf874e3ebd | note | Failed - Install new pulse kit and repeat process
3ceadcd6-d779-5c97-8426-53dd865a89c4 | checkpoint | Sign Off
ad50d9d8-26e8-56f3-bdd2-19531046f2ec | textbox | Name - Geschke Representative
485867d5-005d-5646-ab1b-3a930afb474a | signoff | Signature - Geschke Representative
8fd88cab-c71f-5671-a6fa-93ccde270927 | checklist | QA 18_Gasket Installation |  | Gasket Installation
f0716ed7-860c-5feb-8dcd-a0c4acf3dfb3 | checkpoint | Gasket Installtion:
7be172d1-9829-5a2c-b7f8-00457cfb7cc9 | textbox | Location/Identification:
f876129f-5eb4-51c8-bb9e-756b83edf312 | textbox | Nominal Bolt Size:
9907296c-8706-5b66-9807-55d455c2d7c7 | textbox | Gasket Contact Surface Finish on Flange:
ea836f76-c300-5007-be0a-6a052b6b7f4f | textbox | Lubricant used:
8b341548-e87e-54cd-8475-7e96e7853e4f | note | 1. Galvanised nuts and bolts must use good quality lubricating oil on threads
c956b192-1fea-588d-bb53-83472d861f51 | note | 2. Below Ground Galvanised nuts and bolts must denzo and plastic wrap full flange and cover bolts
d5e0165e-cff4-5c8d-bfea-b4a82bd73d4b | note | 3. Stainless steel nuts and bolts must use anti seize / molybond on threads must return 24 hrs later to tighten in sequence and required torque
d192a8f9-d6f4-58b4-ab1b-8a843ec0f0a5 | note | 4. Galvanised nuts and bolts on stainless steel flanges / backing rings - Thinsulators (insulating top hats) or insulating washer with thin PE sleeve must be used, and complete flange must be denzo wrapped with plastic protection
23edc375-619c-5ac0-9792-9449541ee315 | note | 5. Stainless Steel nuts and bolts on galvanised steel flanges / backing rings - Thinsulators (insulating top hats) or insulating washer with thin PE sleeve must be used, and complete flange must be denzo wrapped with plastic protection
00b820d6-cc4c-53b3-8f3c-6c72d3b45a68 | note | 6. Zinc bolts, nuts and washers rust when used externally use galvanised
e379697a-b2c5-5a64-9c25-eafc72ed07b3 | checkpoint | Visually examine and clean flanges, bolts, nuts and washers. Replace components if necessary. Alignment of flange faces is very important and maintain support of the flange, pipework and valve at all times
250b076c-dfae-5db8-a35b-7bba0249a23b | checkpoint | Lubricate bolts, nuts AND flange surface AROUND BOLT HOLES, not on flange/gasket surface, or use hardened steel washers. Use anti-seize on stainless steel threads and nuts or on galvanised bolts and nuts lightly oil with good quality lubricating oil. Insert bolts in locations 1 to 4 as indicated in the below diagrams.
c2d2b3b6-4fa3-506d-83ec-9ec2ec54dbfb | checkpoint | Install new gasket. DO NOT REUSE OLD GASKET, OR USE MULTIPLE GASKETS. Gaskets for water applications must be EPDM potable water gasket PN16 type. Gaskets for gas need to be AGA and GPL approved
2bee71dd-e32e-59b1-9420-46b083121224 | checkpoint | Number bolts in cross-pattern sequence according to the appropriate sketch below with a marker pen, black or white
d4bf153a-9d1d-5fd0-8512-ebf65e461e96 | checkpoint | IMPORTANT! HAND TIGHTEN; then PRE-TIGHTEN BOLTS to 7Nm torque, but DO NOT EXCEED 20% of Target Torque. Target torque is required to be supplied by Gasket manufacturer / supplier seek from GPL foreman
70414949-d3d3-5c11-a9c3-86105b9cd86d | checkpoint | Check gap for uniformity.
c40c9bc9-4ac3-5841-ade3-ca4e8b683c56 | checkpoint | Use the appropriate cross-pattern tightening sequence in the sketch below for Rounds 1,2 and 3 and/or Round 4 (each sequence constitutes a Round)
30d03fea-c825-59b3-9194-9eead2853f3c | checkpoint | Final Torque
8c38a178-2bad-569d-8c91-4bb0a1397452 | textbox | Final torque*: |  |  | (Nm)
74fb850e-4f2b-5f8a-8595-cf364cd6d87e | note | * Refer to gasket manufacturer spec with torque chart on next page and GPL advice
85b780c7-a5d6-502f-aa26-1029459226ac | note | Lubricate, Hand Tighten, Pre-Tighten bolts (5% of final torque) (as mentioned in item 5 above)
9899d5d1-ecd4-5263-ab82-abcf9d1a1481 | textbox | Round 1 Tighten to: |  |  | (Nm)
b02ee652-b36d-5629-a550-0cfbcf597499 | textbox | Round 2 Tighten to: |  |  | (Nm)
2e643e63-79ef-53a3-a263-9351b8b02708 | textbox | Round 3 Tighten to: |  |  | (Nm)
6b8d6f2f-5526-5691-95cd-134f8af00f7d | note | Check gap around the circumference between each of these rounds, measured at every other bolt. If the gap is not reasonably uniform around the circumference, make the appropriate adjustments be selective bolt tightening before proceeding.
0bf7c0ca-43f7-56c8-ba42-85e8487fcc21 | note | Final Rotational Round 100% of Final Torque (same as Round 3 or 4 above). Use ROTATIONAL, clockwise tightening sequence starting with Bolt No.1, for one complete round and continue by selective bolt tightening before proceeding.
6bf8c817-4eba-5a8c-9e3c-974f59942045 | note | Short-term bolt preload loss can occur between four to twenty-four hours after initial tightening due to bolt relaxation. Consider retightening to help recover this loss.
cd968700-19be-54d6-8335-26348bb19bf3 | dropdown | Tightening Method Used: | Hydraulic Torque Wrench, Impact Wrench, Manual Torque Wrench, Other,Hand Wrench
0590663a-5191-5add-8e4a-e6747fedf410 | textbox | Other:
e1bb53b7-18a6-56df-beee-b9bc27ecd4d0 | textbox | Where was torque information provided from:
a4b9afd0-2ce7-5108-b8eb-79ec7c44d92b | textbox | Joint Assembler Name:
45e3ad94-490c-51e3-9a05-c2d308653923 | signoff | Joint Assembler Signature
fc7dcc9b-15c4-5725-adb8-dc40bd143576 | checklist | QA 19_Service Cross Connection Check List Report |  | Service Cross Connection Check List Report
3d996e18-93fa-51d2-b7bc-3f8b0f3733fc | checkpoint | Service Cross Connection Check List Report Details:
384806cb-258e-5258-90d3-e1a938c4939b | textbox | Zone/Grid:
fbd6a78a-4611-54c3-bb01-878d324421e9 | textbox | Drawing No.:
f10de94c-e511-511d-b795-ae0056e636f8 | textbox | Rev:
d907f4be-f675-579a-b8e0-e3b1dd9dab2b | checkpoint | Service to be tested
b476d468-5583-54f0-a53c-9117067e9335 | note | Isolation of potable supply in general.
c9007909-0497-5e5b-ad9d-feb280c5bada | checkpoint | Potable Water Supply
0fac9376-7e12-5259-aa89-9e5856bb2448 | note | Confirmation of service isolation at all fixtures.
27e9f0f1-91a4-5a80-bc20-3b8b7a232445 | note | Keep potable water turned off.
281030ec-7b26-5b5a-924c-7bb2725f2c9f | checkpoint | Non Potable Supply
5bf38340-bd7e-5665-afc8-d3f0a7362a3b | note | Confirmation of water flow for non potable water supply at each non potable fixture while potable is still isolated.
c19ad19a-301c-5c27-b19f-d2ece5a07a0a | checkpoint | Turn potable back on
f0587b91-5d9a-5d4e-ab05-64d20e6df0d8 | note | Potable back on
bf7308ee-97d2-5181-8206-a81d9cf423d9 | checkpoint | Non potable supply
4d783ca5-0eed-5b3c-be44-c51958ad7ef5 | note | Isolate non potable water flow and prove that each non potable fixture has no water flow.
746aedca-403d-5ab9-b14b-281c871711e8 | checkpoint | Potable Supply
9d0666be-dbab-57ad-abaf-c142eaff17d6 | note | Check all fixtures that receive potable water are still getting potable water.
513dc09a-9e0d-5a59-bf6d-3513e98158c3 | checkpoint | Pipe Identification
034987f6-3f7f-597c-a330-66077eb2e9bf | note | Confirm recycled water piping is identified by colour and labelling.
12c36d30-1d36-54aa-9a51-c192e19f7df5 | checkpoint | Other
92a18618-2d1c-50c3-8cc6-d34b4708b9bc | checklist | QA 23_Boiling Water Service Maintenance Log |  | Boiling Water Service Maintenance Log
066a1a64-8669-5c77-b201-0f5a52cf233c | checkpoint | Boiling Water Unit Service Details
b3f30653-6178-506e-9db0-c86ab4fc3fdf | textbox | Purchased from:
ff0705b5-a1b1-510a-aa7a-e461a5a774d1 | textbox | Make:
a78e77ea-e373-5e4a-88a8-8b1fb7066083 | textbox | Model No.:
a1d24a33-e216-591c-895c-0b159085ad87 | textbox | Location:
e2697e52-d71d-5775-9301-bf7b11547968 | textbox | Room Designation:
28d78b65-0d62-57b6-85c2-041a9d570d33 | textbox | Installed by:
880f6bd0-870b-561a-90f2-36aa95480e0c | textbox | Installation Date:
22e49bd6-3bda-5925-8ddf-d5c03c2c930e | checkpoint | Does installation comply with manufacturers instructions
91cfe6cf-64a6-57a8-958d-53db8414eda8 | checkpoint | Does the installation appear in good working order.
e1127485-8530-5064-a3cf-362fd95de1e7 | checkpoint | Confirm all warning lights working correctly
b60eff23-0fa7-54bb-b27a-0810042ad144 | checkpoint | Confirm filter is clean
158f5d55-a21e-5343-b3f5-fdbbe93f63ec | checkpoint | Confirm Unit is Fully Operational
df7d45dc-5841-5b3a-8ace-d32f2292d029 | checkpoint | Commissioned By:
679e3648-4bab-5088-ba86-3d3b6327e1e1 | textbox | Name:
f59ebde1-31f2-5a17-8679-ed7817fee637 | textbox | Date:
a475ee04-c328-5bbb-86fe-2857c2ae1a5f | checklist | QA 25_Butt Welding Checklist |  | Butt Welding Checklist
ca4b4cd1-2358-5bf8-8194-06eb8adc280a | checkpoint | Operator Details:
46a54668-3daf-53a8-a151-e3d03f8911d6 | textbox | Name:
2b5d83a8-6916-5a15-864b-db62bbedc271 | textbox | Company:
1abfa6f6-57ff-5614-beb0-a6f453afd4c6 | textbox | Phone:
26da7c29-9908-5879-bd26-06afd54259f0 | textbox | Address:
c83758de-5f0c-547c-bfb1-8463595c99b7 | checkpoint | Welding Machine Details:
66ac11be-3c54-5c04-912d-d506cb74a987 | textbox | Manufacturer:
9585ac34-0396-5687-a910-6afd1430ff0e | textbox | Type/Model:
3717006a-52a1-5b9e-904b-55cf39bac98e | textbox | Serial Number:
d04d0eee-d87f-5773-9654-72e022766536 | textbox | Year Built:
a061f28f-55c2-5cab-b2ce-7ff80d0845d0 | checkpoint | Pipe / Material Details:
56aa49ac-cf77-536c-b917-c3273ed34133 | textbox | Dn (OD)
3473aa61-a0bd-5ae2-9abe-619e51c1b165 | textbox | SDR
fdf5fe47-d6a7-55fd-b61b-4b7d9f3f9015 | textbox | En
8fb7d4e4-466c-5ec5-a881-10d733926107 | textbox | Type
a36004fa-1394-5ba6-a3f0-d4855d41565b | textbox | Parameter
27378260-60c9-5c5b-b8a4-a6addaa79470 | textbox | SLP
9ab68ca3-d26d-5bde-9e60-93d9896bca6f | textbox | SHP
a0b01591-964f-5515-85c6-7f96b57877d7 | checkpoint | 1
0db8d60d-7522-5294-8183-cdfea08ef810 | textbox | Time
f5a8f40e-b467-5125-a090-edf393b5d733 | textbox | Ambient °C
1440467f-5fde-5121-9ea8-a6e5a2800a42 | textbox | Heater Plate °C
00dd074b-a686-53b6-8cec-6096504ae3e9 | textbox | Drag Pressure
2400e408-8c18-5c31-8fd7-e44f93c2ef81 | textbox | Bead Up: P1 (Kpa/Bar)
a9fd3c12-5904-59ac-9b3d-fc9f2c4df8c6 | textbox | Bead Up: t1 (Evidence)
4c773931-c621-5bb5-b506-872ee39facdd | textbox | Heat Soak: P2 (Kpa/Bar)
099e0b88-7dc5-5ccd-8022-ce71aa78bccb | textbox | Heat Soak: t2 (Seconds)
4365a50d-2804-556c-83a8-f4d469b5e628 | textbox | Change Over: t3 (Seconds)
f77ed4e8-f999-54f6-a7e0-cbe0c172e5a8 | textbox | Pressure Up: t4* (Seconds)
c4894126-b54c-5136-9637-7fd9b4b213c5 | note | *t4 not applicable for SHP situations
4a131c2e-c3d9-5b81-a50f-6a4af866e043 | textbox | Weld and Cool: P3 (Kpa/Bar)
46cddc23-a2e1-5dea-b4e9-ca6bb1e5d16d | textbox | Weld and Cool: t5 (h:m)
e6defa1e-93e0-59df-9fa3-e2a42ab8ed28 | textbox | Rough Handling: t6 (h:m)
c30bd40f-f2cb-59a8-9753-f37f19ab31e5 | textbox | Bead Size: Min
d78eb3b5-1cb3-57a1-a6ef-5964108cdcfa | textbox | Bead Size: Max
7e4c5935-5272-5a3e-85b5-3bf99c45bc10 | textbox | Comments
61a51d36-aa2c-5cde-817d-4ca50cdfc4ab | signoff | Add Operator Signature
80eb3b16-184b-5f92-932d-71403b994572 | checkpoint | 2
7858abc5-428a-54ed-8fef-c37697469294 | textbox | Time
1cfa4730-2456-52a4-9929-12d7417a31cb | textbox | Ambient °C
3c9c2a26-c894-52df-8a0a-f068a48df402 | textbox | Heater Plate °C
84339dc2-878f-5dfe-92de-21e71a1e4759 | textbox | Drag Pressure
7c2e3e5f-bfa4-5f80-b156-db516e6803f3 | textbox | Bead Up: P1 (Kpa/Bar)
56b89cfa-138d-53dd-b4d7-cf0582bd5081 | textbox | Bead Up: t1 (Evidence)
4cd79080-ad88-5291-a420-864d9ecf123f | textbox | Heat Soak: P2 (Kpa/Bar)
5e06c1f4-5fb1-5372-9436-1256a3452506 | textbox | Heat Soak: t2 (Seconds)
5bb56bcf-9bf0-5f44-bac0-543c14cb09e0 | textbox | Change Over: t3 (Seconds)
d365fd07-deac-5fa5-b778-cf586149acef | textbox | Pressure Up: t4* (Seconds)
6625be94-0187-52f7-9f4d-6b0881825de1 | note | *t4 not applicable for SHP situations
ef636e50-3085-5671-9d2c-995d1539c53e | textbox | Weld and Cool: P3 (Kpa/Bar)
9771b85a-af6c-5693-960b-d1662063818f | textbox | Weld and Cool: t5 (h:m)
97a80bdc-cf6c-5e66-b367-ccbad6ab6b3f | textbox | Rough Handling: t6 (h:m)
a0ca4822-cfa0-5a85-9305-d2323108f15a | textbox | Bead Size: Min
f2f58170-c484-57e4-a1bd-b6606185c49e | textbox | Bead Size: Max
8c762868-6b9b-500c-bd41-454e79b789c3 | textbox | Comments
6c544df2-1bf7-598f-b986-996e61a18da3 | signoff | Add Operator Signature
7a173f6c-500c-553d-b74a-85afb565eb50 | checkpoint | 3
37c593c4-fe01-5350-bb10-d64a0893c68f | textbox | Time
ef19d41f-da99-57bb-8f40-3c067a66de5a | textbox | Ambient °C
6276b928-ddcc-5bff-b3a5-13d24fac9aa9 | textbox | Heater Plate °C
20841de0-1811-54fb-af1f-fba13a0ac8d4 | textbox | Drag Pressure
c1be99a8-d192-5c6b-b7cf-40c7fb0688c3 | textbox | Bead Up: P1 (Kpa/Bar)
7b6c08a6-2e8e-5d9e-9546-94190f68b8aa | textbox | Bead Up: t1 (Evidence)
d17558db-4cc7-5545-bf8b-1aa2e2f54ddc | textbox | Heat Soak: P2 (Kpa/Bar)
f56b19b7-7670-59a6-a0f0-47ecadd9008d | textbox | Heat Soak: t2 (Seconds)
55574ce8-c096-5dfb-9bc6-055804e07282 | textbox | Change Over: t3 (Seconds)
f91cc93c-7588-5634-ad13-b2e294327807 | textbox | Pressure Up: t4* (Seconds)
d6c29471-709d-573e-9533-f3c4664ef232 | note | *t4 not applicable for SHP situations
e25a490d-2e19-5b38-bae2-bbac03dad96f | textbox | Weld and Cool: P3 (Kpa/Bar)
99635b19-e826-5e89-9411-e27801a4a38e | textbox | Weld and Cool: t5 (h:m)
4d8f28ab-e025-5d13-b1ca-e82586be5a2e | textbox | Rough Handling: t6 (h:m)
d7b56e20-1e16-5422-a8f2-cc915f232800 | textbox | Bead Size: Min
4dd96d85-f6cd-5391-8bfc-ab03c721e08a | textbox | Bead Size: Max
ce572f4b-3a9a-52f8-9204-0796e056b4c0 | textbox | Comments
47ba15b3-e1d2-5188-8d03-4a2b6e7a828f | signoff | Add Operator Signature
b911b1b9-6725-5360-8e28-f6a01e7ce249 | checkpoint | 4
51daddf4-f5ae-5f4e-9634-ee241615fd92 | textbox | Time
c4a74ddc-4dce-5ace-a620-e104b196d494 | textbox | Ambient °C
6c9b499b-cff3-5937-b360-ce6decc063ee | textbox | Heater Plate °C
49ba7e6f-08cf-57d9-ade3-168db33509ea | textbox | Drag Pressure
4f4f6de0-69db-5755-ae12-cea2cbd7df0d | textbox | Bead Up: P1 (Kpa/Bar)
a7532573-46f7-5e0f-8463-da4ff38946c9 | textbox | Bead Up: t1 (Evidence)
0123f480-9e99-5c8f-9531-bc8fbe1d24b0 | textbox | Heat Soak: P2 (Kpa/Bar)
3dd77afe-a845-5e29-b997-ab2eaddd96b1 | textbox | Heat Soak: t2 (Seconds)
2c300354-a2c4-558e-b6dc-de91a259d66f | textbox | Change Over: t3 (Seconds)
a1b5b247-199e-5cff-954b-e5d3f1fd4cb0 | textbox | Pressure Up: t4* (Seconds)
70286c1b-6c09-5500-9d52-93e488c4a136 | note | *t4 not applicable for SHP situations
3ac31eb6-dad3-5fe3-9c4c-1d08d2845f0f | textbox | Weld and Cool: P3 (Kpa/Bar)
8ba47d42-db0e-52c2-8127-a6589ae88a10 | textbox | Weld and Cool: t5 (h:m)
9b364ae5-7fda-5f80-b19a-d734900c5d90 | textbox | Rough Handling: t6 (h:m)
7404fa90-02c6-51b5-bb2e-7becf2a552b2 | textbox | Bead Size: Min
00609065-4f58-5d9f-856e-211c2e3e7597 | textbox | Bead Size: Max
540fb917-4ed2-58f1-801f-3483011fef4d | textbox | Comments
3edcb550-ab62-5c27-8568-2953aec00e0f | signoff | Add Operator Signature
24dce8d0-3e3b-5c3c-b560-2a93082053b4 | checkpoint | 5
13239f5f-1f8a-5019-b566-9e319c80acd9 | textbox | Time
5b118ae6-4ba9-5bad-8975-91ae7311b7b9 | textbox | Ambient °C
879505e6-6aa5-5bf0-8162-5ec7f85a085f | textbox | Heater Plate °C
1041f8c1-e35e-58bd-b9e1-fa037cd4b21c | textbox | Drag Pressure
b4570a54-9b5e-50d1-a7ac-dbfff9480f0f | textbox | Bead Up: P1 (Kpa/Bar)
a79dcfae-0969-5a9d-89c5-ad4ad3082e0f | textbox | Bead Up: t1 (Evidence)
6748028d-2b9b-5290-8c21-98e9f8dfac93 | textbox | Heat Soak: P2 (Kpa/Bar)
1a2bef15-4acc-53cf-bb48-95e2f565c83c | textbox | Heat Soak: t2 (Seconds)
d6ec3494-e711-5413-8f7f-2d91f7320dc9 | textbox | Change Over: t3 (Seconds)
2e717ebc-4a9b-595c-8816-1af63b4a9e58 | textbox | Pressure Up: t4* (Seconds)
57db01d7-e6c2-5e37-a3cd-74bf3c938b9e | note | *t4 not applicable for SHP situations
99c43286-1200-5dd7-bc4b-b0ec941959a9 | textbox | Weld and Cool: P3 (Kpa/Bar)
ba5d1f54-3d21-5656-85d5-60c8df82a31a | textbox | Weld and Cool: t5 (h:m)
a646bad0-5ab4-5664-a5c3-7e59553a3e80 | textbox | Rough Handling: t6 (h:m)
e7ac60f7-3ab0-5562-bd49-1ee193c5719b | textbox | Bead Size: Min
86f7e9b4-141c-54c9-a855-4aaa2c7b027f | textbox | Bead Size: Max
44306b91-0190-5627-8049-51e163f997dd | textbox | Comments
21c2e6a7-eaac-5418-9948-945da90380f2 | signoff | Add Operator Signature
e4ee39db-2ed2-56d4-9d1e-70d41b06e452 | checkpoint | 6
c9f3a0fe-2fab-5a91-89b1-9764a223b93f | textbox | Time
41c4a495-7520-57b9-bce3-7878bae669ef | textbox | Ambient °C
c808acf5-2f07-502e-9688-2f24492af699 | textbox | Heater Plate °C
30d8d23c-105a-52c2-a741-bd834b3f37dd | textbox | Drag Pressure
a8a93726-6d74-5c1d-8648-db8e18b1b003 | textbox | Bead Up: P1 (Kpa/Bar)
530a314d-5ab2-5605-80a7-aa264c1b45ef | textbox | Bead Up: t1 (Evidence)
941274f2-a3f7-5f34-99bc-5e04bab74876 | textbox | Heat Soak: P2 (Kpa/Bar)
82385811-9bab-5c69-b475-b583f7583ae0 | textbox | Heat Soak: t2 (Seconds)
dcb2556a-fa5a-51ba-b67a-19bcf4c3428b | textbox | Change Over: t3 (Seconds)
3f1a67ea-768c-5f79-9fdc-662c76dbf4b4 | textbox | Pressure Up: t4* (Seconds)
dc700e13-9645-50bf-a154-c34f8c0b288e | note | *t4 not applicable for SHP situations
096898ab-46e8-56b9-8bdc-e55533668d76 | textbox | Weld and Cool: P3 (Kpa/Bar)
b8bcef6c-5667-5690-b507-c03dee966d50 | textbox | Weld and Cool: t5 (h:m)
dcc821c0-9918-5f5a-867f-0aab3b249829 | textbox | Rough Handling: t6 (h:m)
73aacf78-7d9b-544a-b824-435aab9e1b64 | textbox | Bead Size: Min
1c2dd7d6-2b2a-5e42-9c37-6910e41eb33f | textbox | Bead Size: Max
d09127a9-51a0-556a-845e-512a56f4f8e7 | textbox | Comments
80690888-5962-5968-addb-c40a8fbb8f0a | signoff | Add Operator Signature
928a8d37-d6be-57e8-9819-49b7c2a1d92d | checkpoint | 7
0c10e1be-c838-5343-98b6-642a7e8903a0 | textbox | Time
e52142b7-2655-54c8-92ce-c5658f09a5e9 | textbox | Ambient °C
d2ecc2ee-cbbd-547b-bf15-7744dad17c30 | textbox | Heater Plate °C
2a6d8a9c-192a-5295-ba4f-3ee1805b3462 | textbox | Drag Pressure
cee2da90-ab6d-5722-a379-f620e6e3e210 | textbox | Bead Up: P1 (Kpa/Bar)
0ffa0f68-f28d-59d5-bd59-7c06d3a79aa5 | textbox | Bead Up: t1 (Evidence)
2ad53234-469f-5ab3-97c2-f642a7f37820 | textbox | Heat Soak: P2 (Kpa/Bar)
ccbecc9a-2c4b-5d30-8e26-31c041316285 | textbox | Heat Soak: t2 (Seconds)
58432c0d-3dba-520f-a019-38eb82315dbb | textbox | Change Over: t3 (Seconds)
466e8485-db20-5f7e-8532-bba280995899 | textbox | Pressure Up: t4* (Seconds)
b7fab505-9b68-5b63-a8e1-1795df504af5 | note | *t4 not applicable for SHP situations
9f0933c1-1a99-51bf-9aee-dc8a8f9c3429 | textbox | Weld and Cool: P3 (Kpa/Bar)
9b9dc124-4452-58cb-8e11-4e0d6d3ddb08 | textbox | Weld and Cool: t5 (h:m)
cae2a92e-d62c-597b-960d-bbdd9d2448c1 | textbox | Rough Handling: t6 (h:m)
df6274ad-0d65-5d2f-8ad0-5d8e51dfac89 | textbox | Bead Size: Min
a761fec6-c829-5103-ae44-caca2694b87c | textbox | Bead Size: Max
1b2a5930-c652-5fdb-8078-744c32476a49 | textbox | Comments
9c34bdb1-0b35-569d-a4b1-cf94c5ef5c49 | signoff | Add Operator Signature
b556b88f-cfc7-5c58-a0d3-21aa1fcf562f | checkpoint | 8
866722b3-aa94-5c05-b768-e3f3c2afd1a6 | textbox | Time
931196fb-778e-5314-8f70-97a6037357d8 | textbox | Ambient °C
121fa6b5-5566-5ba0-8f85-73da1c8dcae4 | textbox | Heater Plate °C
161b7d12-a950-5c51-8f61-471846a81f37 | textbox | Drag Pressure
f4c8a800-30d2-5ff2-b156-555ff94bbc5e | textbox | Bead Up: P1 (Kpa/Bar)
9c00aa83-30d1-52d3-bc6f-fc66f10bf475 | textbox | Bead Up: t1 (Evidence)
5b72a478-b2f7-5141-88ad-3a0cc23532ce | textbox | Heat Soak: P2 (Kpa/Bar)
1a347705-2201-5a16-b549-96f01a7eaacf | textbox | Heat Soak: t2 (Seconds)
b304443e-23e1-59f2-8802-67ae6436e952 | textbox | Change Over: t3 (Seconds)
dc495ef6-2fc6-55ee-a814-61946a50cfc7 | textbox | Pressure Up: t4* (Seconds)
349a7808-1e9f-5d18-8f70-156f8e9aa373 | note | *t4 not applicable for SHP situations
18e95f0c-08c5-50fb-8da6-de7c4ee7881e | textbox | Weld and Cool: P3 (Kpa/Bar)
c3196fd5-dfe6-50b1-aeb3-ae8a06b4b70b | textbox | Weld and Cool: t5 (h:m)
8aab0d41-c8af-5fe1-b35b-30b1be882210 | textbox | Rough Handling: t6 (h:m)
9bdee718-d0d9-57fe-9915-e734d0dccc1a | textbox | Bead Size: Min
bf57a7e7-88b4-5d3d-9492-6ef3920cfadd | textbox | Bead Size: Max
fc5a6f22-71b0-517f-9103-d45edbd1e8df | textbox | Comments
e893ee60-d3c8-5157-9bf6-e21703049a66 | signoff | Add Operator Signature
f81a9cad-2202-53fc-aea8-cbaacb40a1ec | checkpoint | 9
2c79cefc-aaf9-57b9-8781-5b26502d45a2 | textbox | Time
e46d12b4-751f-5f12-b435-5de42b6ea1f5 | textbox | Ambient °C
e1c59bcb-dd92-5fd0-ae3c-a276e79e5f90 | textbox | Heater Plate °C
8d92a942-eaf6-5c37-97c3-17334f3afb28 | textbox | Drag Pressure
79138fa8-783d-5ae3-bdf0-6db58ef9daf0 | textbox | Bead Up: P1 (Kpa/Bar)
35d1c479-4710-5411-b51f-520e9ee2bd7f | textbox | Bead Up: t1 (Evidence)
4c7bff51-fd41-580b-b366-2572f5019c6b | textbox | Heat Soak: P2 (Kpa/Bar)
0231f7b6-2bbc-52fd-9293-2720bf89c590 | textbox | Heat Soak: t2 (Seconds)
a6d2663d-f402-54c3-b90b-5647ad1943bd | textbox | Change Over: t3 (Seconds)
8dba2c13-16d5-50e0-99b1-7829ba447443 | textbox | Pressure Up: t4* (Seconds)
99e5e633-b91b-59f1-95f6-c883fd560261 | note | *t4 not applicable for SHP situations
14cd0078-2664-5624-88df-1a0a070f69d5 | textbox | Weld and Cool: P3 (Kpa/Bar)
689a73a5-db8e-50cc-8e15-e973bdc64f46 | textbox | Weld and Cool: t5 (h:m)
685abf86-ae3f-5485-bf90-dbae9f453d0f | textbox | Rough Handling: t6 (h:m)
320c993e-72ba-58c6-8b02-52f41709d669 | textbox | Bead Size: Min
ed77ab77-b645-5da0-97f0-e1fa2011bc28 | textbox | Bead Size: Max
60c75f13-475d-5a5e-bd2e-02d1de1be078 | textbox | Comments
20d0e98f-904e-5a83-816a-aea5353f2053 | signoff | Add Operator Signature
e48a2151-c0b0-593e-afe7-b90d947c1f50 | checkpoint | 10
13ebd8cd-7e46-5e58-ac80-3969e63659b6 | textbox | Time
3db617d6-c55e-5b1b-9bc0-2060de7cc58e | textbox | Ambient °C
e76f7ff5-3752-555e-b9b5-2b68da0eeb92 | textbox | Heater Plate °C
678b39f4-b138-592c-ad7a-ff86edcda462 | textbox | Drag Pressure
fe052fff-e524-510d-90ae-d0e0b378bf2b | textbox | Bead Up: P1 (Kpa/Bar)
95f3bc5d-4bab-5569-8b81-c518272cc777 | textbox | Bead Up: t1 (Evidence)
0db83871-a500-5c23-80b7-d414bac79e91 | textbox | Heat Soak: P2 (Kpa/Bar)
62de5984-72e4-58cb-abc0-3ed4ee1ed36c | textbox | Heat Soak: t2 (Seconds)
6510e35f-c6db-5791-97a1-c218145efeea | textbox | Change Over: t3 (Seconds)
38c66fc8-c2f7-5be1-849c-9b2712b2a659 | textbox | Pressure Up: t4* (Seconds)
d0a4931a-daf3-52be-8357-3e56e9a44643 | note | *t4 not applicable for SHP situations
4371880b-5991-54f0-97a7-ebac0dfd77c7 | textbox | Weld and Cool: P3 (Kpa/Bar)
9a0b6d19-2df5-5c23-ad28-4ac5854fd1dc | textbox | Weld and Cool: t5 (h:m)
5c343646-c8e7-5eea-a1e8-24990a277796 | textbox | Rough Handling: t6 (h:m)
ffcac9cd-f968-55b3-9b14-61a405f27661 | textbox | Bead Size: Min
6ce557ce-f756-53bd-a2e5-6fda7e99d876 | textbox | Bead Size: Max
91307927-b19d-5b0a-b370-aaada4f41cc6 | textbox | Comments
e99bd6f2-989e-5d94-bd70-78959c220c98 | signoff | Add Operator Signature
2b0bea58-0539-585d-af09-3bb070c1b6d5 | checkpoint | 11
53b2f860-eea7-5a3e-a64e-901575ae0fd9 | textbox | Time
543469d9-517d-54a9-ab4d-040df6becd9f | textbox | Ambient °C
4019160a-8475-5dd7-86cf-25bd345c2583 | textbox | Heater Plate °C
96f95b28-4bee-567a-958e-b24b477dffd6 | textbox | Drag Pressure
d548ba3a-c539-591f-9c6f-379b7e74daa7 | textbox | Bead Up: P1 (Kpa/Bar)
46c89aea-23a3-5471-9764-5d39ee0b24a0 | textbox | Bead Up: t1 (Evidence)
a486b75f-2f39-5fdc-af45-e5f97f1427d7 | textbox | Heat Soak: P2 (Kpa/Bar)
84c6f7a8-855e-55c4-8aad-fb74a5c66dbd | textbox | Heat Soak: t2 (Seconds)
f0175d97-9f0e-5c5d-8c01-4204b9b66b0b | textbox | Change Over: t3 (Seconds)
cfefa22e-cde7-51e3-8be6-c4c624a55533 | textbox | Pressure Up: t4* (Seconds)
64337296-f6c1-56d2-9d37-e5887baa0618 | note | *t4 not applicable for SHP situations
25b7cc88-e7da-5c46-9a9c-f013d1b7dcb4 | textbox | Weld and Cool: P3 (Kpa/Bar)
8280b597-2298-5ae2-81b5-e94025c75b82 | textbox | Weld and Cool: t5 (h:m)
a2e3befa-30db-5d9b-923e-a2e43e81c4a5 | textbox | Rough Handling: t6 (h:m)
90d16c4d-4a09-554e-a5b1-a3e414b0865d | textbox | Bead Size: Min
26115009-8dbf-566d-9438-ac58659694e7 | textbox | Bead Size: Max
93bc5a1c-5698-587c-acad-5fdd8fcd9b29 | textbox | Comments
46e0965a-29e5-5e68-a1a7-64201f269c65 | signoff | Add Operator Signature
0e643ae4-e6c2-54a9-8747-f8b26568f716 | checkpoint | 12
ff13f2af-268d-5c52-8f57-66ce637063dc | textbox | Time
9e9c46cc-0690-5a79-a35e-bf57c9a2025e | textbox | Ambient °C
0b15c02f-8ef8-5ede-a025-777ff9c0ce25 | textbox | Heater Plate °C
106acc3a-add6-5b20-a30c-23487e6d58ea | textbox | Drag Pressure
b70e0548-ae95-554f-b70e-b2c68afde17e | textbox | Bead Up: P1 (Kpa/Bar)
42779eba-89d8-5e6f-9204-d94c047daa35 | textbox | Bead Up: t1 (Evidence)
a40f693d-96ce-560c-8582-487d21756759 | textbox | Heat Soak: P2 (Kpa/Bar)
8975e037-bcc2-51fc-ac6f-0a4318bf354a | textbox | Heat Soak: t2 (Seconds)
3c75c233-e69d-5d5a-a6c9-43a26cbf3812 | textbox | Change Over: t3 (Seconds)
5c3388be-bb16-5984-84a4-72e50ead1129 | textbox | Pressure Up: t4* (Seconds)
a787c89d-9594-568d-bca6-b607465311a4 | note | *t4 not applicable for SHP situations
25fab38e-55a5-502b-b13c-57b6b808cbe1 | textbox | Weld and Cool: P3 (Kpa/Bar)
2d95d398-025d-59c6-9768-000abbc056aa | textbox | Weld and Cool: t5 (h:m)
2e6e8933-b8a0-5b82-939c-09796f5540d3 | textbox | Rough Handling: t6 (h:m)
ab34fddd-b094-5057-9a65-9b7d7a189285 | textbox | Bead Size: Min
9cb40fac-ad4a-5be9-8ad4-a7842288cce2 | textbox | Bead Size: Max
988e914e-850b-57fa-b02d-ee5b6c102b84 | textbox | Comments
1d6d316f-f043-5d0d-8221-86db1634ab9d | signoff | Add Operator Signature
30bc1dbb-5ad3-52f3-bcae-8c3add468ed4 | checkpoint | 13
748b51fe-3a53-5c2d-bcfd-3df1d00ca0d1 | textbox | Time
ac72861e-30c7-55cc-9466-968c3f6de48c | textbox | Ambient °C
db47b348-f555-57f4-b63e-7bfd6b784815 | textbox | Heater Plate °C
a92d4d48-a6c9-51c3-8e79-952642d69c06 | textbox | Drag Pressure
28bc6b16-0ae2-5641-ba6c-004068d1041e | textbox | Bead Up: P1 (Kpa/Bar)
2fed65ac-def0-5f82-b88c-b811da9965a1 | textbox | Bead Up: t1 (Evidence)
82259554-c0c2-56b9-b36f-3b55cffad1b6 | textbox | Heat Soak: P2 (Kpa/Bar)
d381bdbe-33a0-54b6-9629-ef55fd71e903 | textbox | Heat Soak: t2 (Seconds)
ed458da1-4766-50c4-b3a5-5188b32c8aec | textbox | Change Over: t3 (Seconds)
ba3c330d-f2a7-5fb1-9e56-e65bd6782a91 | textbox | Pressure Up: t4* (Seconds)
009742be-7b0d-50ac-98e8-5eb3923b5977 | note | *t4 not applicable for SHP situations
adfbec0d-e7f4-5f29-8019-de03bb33a055 | textbox | Weld and Cool: P3 (Kpa/Bar)
3e7bf794-a143-56e7-8068-d7d7a0ca5720 | textbox | Weld and Cool: t5 (h:m)
5da0e128-0c38-538a-8723-f23ad0ab15de | textbox | Rough Handling: t6 (h:m)
298241c2-04d5-53a4-9682-f47274449c44 | textbox | Bead Size: Min
facd45ab-fee1-5b38-8f4c-125657c1d7c6 | textbox | Bead Size: Max
6ada4d34-58fb-59e9-9956-968fcf92af91 | textbox | Comments
1858c9df-5b26-5c9d-a77e-f354de7235f2 | signoff | Add Operator Signature
45e03f67-4db9-5263-9332-bc9ca56b237b | checkpoint | 14
a7612892-71fd-5c4e-910d-64ae742ac696 | textbox | Time
e76a5509-9558-5be7-8d62-c8b58e36f04e | textbox | Ambient °C
04fd5155-5e47-5e7f-9612-e8e16cf52c40 | textbox | Heater Plate °C
862c1535-e1da-5054-86a6-cff4772c11b9 | textbox | Drag Pressure
8d9b7892-d0c9-54e1-8d53-df1aa92a7054 | textbox | Bead Up: P1 (Kpa/Bar)
f9c0ce2f-1d3e-52c4-b282-579531e7d6b4 | textbox | Bead Up: t1 (Evidence)
cf18d780-76cf-5c75-be93-07a817646e14 | textbox | Heat Soak: P2 (Kpa/Bar)
dc237503-ebfb-5a09-abdf-fc5c1eb24f0d | textbox | Heat Soak: t2 (Seconds)
71caa803-60a9-520d-bc3f-d697de1cd147 | textbox | Change Over: t3 (Seconds)
93054656-87b0-5c6c-bc5e-92d7612ef99f | textbox | Pressure Up: t4* (Seconds)
0f0dac9b-b2b8-5ced-a346-68bf1137b01c | note | *t4 not applicable for SHP situations
67bf54cb-515e-560b-b0af-a0c385b93180 | textbox | Weld and Cool: P3 (Kpa/Bar)
91a16908-7a75-56fa-8e74-548795f0a95f | textbox | Weld and Cool: t5 (h:m)
0b074d4a-a6cd-5238-9064-d11a75c4bd12 | textbox | Rough Handling: t6 (h:m)
2a10f2cf-e0be-5a79-84e5-33dbcd522e97 | textbox | Bead Size: Min
8d2e450b-487d-5837-b735-f94a0621e840 | textbox | Bead Size: Max
b1d20e13-32e8-514a-a611-a247bcc3e657 | textbox | Comments
a272b3bb-fb42-577d-b8b0-bbaf9df2e749 | signoff | Add Operator Signature
c4f85408-0c95-5c6e-926d-cd261cc5057f | checkpoint | 15
e4908b7e-ea08-566c-833f-65fc5ecfbdc3 | textbox | Time
5a214473-d982-5938-a146-47bc64d4efd4 | textbox | Ambient °C
a49ff0e6-04ac-539a-9bf0-32e64a73816f | textbox | Heater Plate °C
f318954f-5b32-5b37-978d-b9555a361be1 | textbox | Drag Pressure
7d42aa3f-83c3-5159-86b7-70aeb7e88d3d | textbox | Bead Up: P1 (Kpa/Bar)
eb18063d-dd2b-52d9-99ef-6e743cf85068 | textbox | Bead Up: t1 (Evidence)
ecce34d2-5aa5-5df7-9927-83ef5f51f867 | textbox | Heat Soak: P2 (Kpa/Bar)
e0494f53-b7af-5b2f-b862-da90602027d7 | textbox | Heat Soak: t2 (Seconds)
d828b996-b513-512f-8697-9fcdcd50f51a | textbox | Change Over: t3 (Seconds)
0c57053d-043e-5704-9e5c-a5dcf43126b6 | textbox | Pressure Up: t4* (Seconds)
41c80c9b-7961-5d92-ad7c-f25e0d5f71f6 | note | *t4 not applicable for SHP situations
246d0ed9-97fa-576b-b262-cca124664915 | textbox | Weld and Cool: P3 (Kpa/Bar)
49d17b6b-0d97-5422-b887-0e3a06a3e14d | textbox | Weld and Cool: t5 (h:m)
ef20136f-08df-5ac4-af0a-535f4f28192c | textbox | Rough Handling: t6 (h:m)
b6c69118-760d-5c00-bb10-5efafb78912b | textbox | Bead Size: Min
9215262f-c875-5d5b-8b74-92dd0c2831f6 | textbox | Bead Size: Max
9b817919-9485-5e3c-a7b9-25d8b93704eb | textbox | Comments
720bf538-b609-5363-809e-c29bb4056269 | signoff | Add Operator Signature
5ab7a9c9-d48c-5adb-8a4c-40224667d9ab | checkpoint | 16
83cd7473-1388-5a2a-8755-b5def54256b8 | textbox | Time
e8e4f420-3047-5608-8132-e29dc812ffa5 | textbox | Ambient °C
21051102-a589-51f4-aad9-3b8ad92af892 | textbox | Heater Plate °C
a2973ab5-51f3-520f-a3c8-75ce65ff5551 | textbox | Drag Pressure
3d051440-88a0-5abf-adef-2faf517a94e5 | textbox | Bead Up: P1 (Kpa/Bar)
b0095b18-9a25-56f5-b2bd-997dba748629 | textbox | Bead Up: t1 (Evidence)
3b071995-d27c-5a53-8e1a-778218da0782 | textbox | Heat Soak: P2 (Kpa/Bar)
efc9070f-0a39-50cb-802f-9db1127431da | textbox | Heat Soak: t2 (Seconds)
fcc4d142-cece-50e8-91fc-205fd24f6a5f | textbox | Change Over: t3 (Seconds)
7ecc3263-dcfc-53ab-a7e6-eddd9dbb7125 | textbox | Pressure Up: t4* (Seconds)
551ac8b9-5f7c-5249-9810-1ac1c85355dd | note | *t4 not applicable for SHP situations
bbfbb28d-f2f3-53e2-bfdd-7c0f3b219350 | textbox | Weld and Cool: P3 (Kpa/Bar)
25be3ce1-36a8-5ea1-8a27-d8fb5dbb946e | textbox | Weld and Cool: t5 (h:m)
4836e23b-4258-54fd-9cd4-d2c17018b188 | textbox | Rough Handling: t6 (h:m)
de193e04-fb91-522a-b753-b73aaba7c062 | textbox | Bead Size: Min
686dede9-217b-5301-a4c1-e1ecf0d79483 | textbox | Bead Size: Max
b276dde4-4711-5011-80a6-5bf9e134857d | textbox | Comments
39609a98-67de-52e9-9586-9605f5f5f44c | signoff | Add Operator Signature
50721303-a038-5977-9642-47de2d9caf8f | checklist | QA 30_Fixture/Hydraulic Installation |  | Fixture/Hydraulic Installation
a9e1ea2b-799a-5449-8020-407dbe196b58 | checkpoint | What is being installed?
a2d7abd6-97f6-5639-9052-0bec5a4ea929 | checkpoint | Where is this fixture being installed?
ea0cb74b-d31b-5934-b73a-8c9c3592824b | checkpoint | Have all parts been connected/completed and tested? If no, please detail why?
9466f9f1-c3f3-5da5-a1a6-b3cc08b62b8d | checkpoint | Has photos of installation been taken and uploaded?
cb1720a3-9665-555f-aaa7-61a44084e1a2 | checklist | TMV Commissioning Log Sheet V.040221 |  | TMV Commissioning Log Sheet
2eee693f-4717-525c-8936-347782dbe5d0 | checkpoint | TMV Commissioning Log Sheet:
26208a38-cac2-5918-9058-d6adb270105d | textbox | Building Name:
787ef829-aee9-54fc-a8fc-d4e33aabce85 | textbox | Contact Person:
9824ebd0-4dfb-5815-815b-add1ffc95121 | textbox | Address:
cd626b90-22ca-5992-bd5f-ab6086b4c2b3 | textbox | Lic:
82ed12b7-69b1-577b-bf22-722957661691 | textbox | Registration number:
07f933ec-5bcf-542f-9e95-50b4b99e4def | textbox | Phone number:
01186232-24be-5ea9-b7b4-5b0f1683cd16 | textbox | Make of valve:
de882b36-bfe4-5030-8645-4723ae74aacc | textbox | Model number:
8bdd78ff-e6a0-5a00-8c68-b3ec31b3c9f0 | textbox | Valve location:
a8dad8ea-077e-5472-9d1c-e77b6e4de212 | textbox | Room name:
ebd818f4-1e15-53d2-a9c8-f391da455ace | textbox | Valve purchased from:
eb6724cd-5f16-5c95-8c50-4a975f90a34c | textbox | Installation date:
75b6926b-f474-5f4e-a8e4-46e55d7e5b1c | textbox | Valve installed by:
b4b5c4ce-9f24-51ec-b78e-e8e6560aa58c | textbox | Number of outlets served - Baths:
66597c56-2cf7-5863-bfe5-78ad7d624a84 | textbox | Number of outlets served - Basins:
b62cedc0-a3a0-58d8-a8e5-e1782bf98dc3 | textbox | Number of outlets served - Showers:
eeafb204-d20a-5630-84dd-39203fef67e7 | textbox | Total number of mixing valves on site:
62c1e723-7b4d-55f6-a717-edcf40fa36c3 | button | Does the installation comply with the manufacturer's/supplier's published installation instructions? | No,Yes
91258da4-776c-536b-acc9-d1e75ae8315b | button | Does the installation comply with the current requirements of the local water supply authority? | No,Yes
85217217-7ea6-569a-b659-e3b40f2e6f2e | textbox | Temperature of hot water supply?
bdb81617-ceb6-5279-b3cb-aa4d42f75ac6 | textbox | Temperature of cold water supply?
30190140-47c3-5ce7-9389-198b882367aa | textbox | Temperature of warm water delivery at outlet fitting?
5ef75339-02af-5d05-8161-0937873b45c9 | textbox | Dynamic pressure of hot water:
db48ded7-f764-5dba-a1ae-dd93bc84c96d | textbox | Dynamic pressure of cold water:
4f07e862-63a4-5510-9bb5-28041ddf9970 | checkpoint | Check fail safe operation (hot water at least 20c above warm water)
4355dc79-ce72-53a2-bb34-68f3e45b61ea | checkpoint | Commissioned by
65f86cba-77a0-5c26-afdf-7b53eef90330 | textbox | Commissioned by:
a3daefa7-afd4-5c1d-aae3-7ac0018157bc | textbox | Company name:
f28c37c6-c2e4-5ccf-984f-1d374c916d01 | checklist | VHH - Water Protection ITP (V.090421) |  | VHH - Water Protection -
efd5b141-8b5f-5dbb-937c-282341f1e0b4 | section | Part 1 - VHH Periodic Flushing / Copper Protection Test Sheet
2ab05d22-5099-5fac-96d7-e5561c94d25a | checkpoint | ITP details
a47c0c3f-ba3d-5343-89b3-c9d48dcb12bf | note | Copper systems are failing in the construction industry due to issues relating to design, water quality, the management of water during construction, long term maintenance of buildings with issues arising from building management team not following protocols outlined at hand over. Stagnant water being left in both hot and cold copper pipelines have been deemed to have been a contributing factor to recent copper failures. Copper needs to form a protective layer of copper oxide on the internal surface which is formed by the contact with fresh aerated and oxygenated water
1d28916f-c0b9-5b56-a63b-6e8696d5f957 | note | Geschke Plumbing in consultation with John Holland & AECOM have put forward a proposal of periodic flushing of the systems during construction to mitigate the stagnant water issues that have arisen in the construction industry. The purpose of this ITP is to help create a strategy to ensure water is flowing through the piping system and flushed at nominated locations
31d10cf0-faa0-5586-ba19-071507a56087 | note | Plans to flush to be submitted to John Holland prior to any flushing occurring on site
a2245977-ec0f-5a38-b6dc-5d3c8369dcea | checkpoint | Flushing Details (Flushing to be Completed with Water ONLY)
7b1d1710-7b4b-51ae-8730-a9daf62f4d69 | textbox | Level being flushed
e02bf841-2c07-52d5-a32d-c28a41c6e070 | note | Stage of Flushing During the Project
ef70b62a-e9ad-52ba-b3e4-3b6708c8a509 | tickbox | 1. Initial flush after installation of pipework and prior to Quality Control Pressure Test Report (Geschke QA 6)
1ebbe732-5f30-5d2c-9c7f-c0f8237e83d3 | tickbox | 2. Final flush post disinfection
721a0b3e-8674-53a7-9f46-e70584e99fd9 | tickbox | 3. Periodic flushing during construction (to be completed every 4 weeks in line with AS 4809 clause 6.2.9)
359ae6ea-f072-5bfb-af85-9b37600846b7 | tickbox | 4. Periodic flushing from final flush until PC (to be completed every 4 weeks in line with AS 4809 clause 6.2.9)
03f646f8-850a-5a62-80a4-3ada34a268cb | checkpoint | Time & Type of Flushing (As per reference table below)
d17d12ef-8873-5504-880e-de81e25b2eb3 | tickbox | 5. Ring main Single point for flushing; the entire loop can be achieved in a maximum 10-minute flush
3e8df79c-f834-5272-806c-3deb90fe3fca | tickbox | 6. Non ring mains Any copper sub-branch from the main feed requires individual flush time of 5 minutes (an example of this would be a corridor feed)
5158ed6e-0535-59fc-b4da-300528c7d793 | tickbox | 7. Short branches of copper that feed rehau do not need individual flushing
b8871cfd-d894-5857-9236-248be85ca6fd | checkpoint | Which fixtures are being used to flush the system (Point of Connection & Point of Discharge)
cdfb0da9-8da8-561a-a7dc-55408dd2b9ca | note | Fixture 1
9577e8cb-39b9-5d62-ac8b-3159431438cd | textbox | Start time of flushing
6aa572e2-e41b-586d-ae60-8ec47bfae425 | textbox | Zone/branch to be flushed
62fd0ad3-4584-506f-86ab-f7b867275f34 | textbox | Finish time of flushing
6a3d0718-efef-5bef-b6aa-ec5651746668 | textbox | Zone/branch to be flushed
7ce9f1cc-9f3d-56c7-b821-f7e41cc577b0 | note | .. ..
3c9b2bbc-45a8-54d8-af7b-acac7bb42edc | note | Fixture 2
9e7b2ae9-9f82-58ce-aaaf-7806ee5ad521 | textbox | Start time of flushing
1add0bfd-7ea2-5b86-a3e5-e8e278228a85 | textbox | Zone/branch to be flushed
e5500dd1-6ee2-5330-9b83-3d4f8afc4845 | textbox | Finish time of flushing
0012f34c-0c2a-55ef-a9d0-11c11087093c | textbox | Zone/branch to be flushed
03b690ad-827b-5df0-94d0-8fc1be67b69b | note | .. ..
715e45d7-33bf-5df6-9cab-f9dc2c9e821b | note | Fixture 3
3b961fc4-98bf-5e11-b7fe-f58d222b2a2a | textbox | Start time of flushing
3b45cf52-af6b-5e87-9e42-5c49a9e7e3b0 | textbox | Zone/branch to be flushed
dddf2579-34a5-5e4c-9d74-af72729fbca3 | textbox | Finish time of flushing
11c7eee3-6580-55e1-b1b3-4236385d16db | textbox | Zone/branch to be flushed
74ffc707-4c12-521c-8be7-c8af7eba48e4 | note | .. ..
dfc67b06-a031-5b2f-84e2-4d4fb87877dd | note | Fixture 4
ce13de99-f351-59ba-ac36-d658c7fb4f11 | textbox | Start time of flushing
efb1dc6d-0c2d-5f69-9202-2140ad900924 | textbox | Zone/branch to be flushed
8fbd05d3-b443-5b39-b3ab-2f631976c7ef | textbox | Finish time of flushing
17eebb25-70a0-52c7-9e0a-1559d4e52a0d | textbox | Zone/branch to be flushed
19df8e61-1f11-51c5-a20f-f8f81462420a | note | .. ..
99d1a2d9-e8d1-5d7b-b854-3bc2382f80c5 | note | Fixture 5
9896504b-030c-543f-bb02-03c1e3db9dca | textbox | Start time of flushing
a478cfc2-683f-5adc-9a15-1d01ce5ed022 | textbox | Zone/branch to be flushed
2ec13bc7-8b11-5425-94ef-e4950caa0aa4 | textbox | Finish time of flushing
1270cdde-a99d-5cbd-9375-bbf58147bc4d | textbox | Zone/branch to be flushed
cf660ccf-2e0f-5f72-8c10-80ec6d356f57 | note | .. ..
16fe33ed-dca3-5011-9fd6-f50ff87a1740 | checkpoint | Sign-Off - Pass once entered
ca622f3b-d1bd-5f3b-9e43-f9491c175c1a | note | Add comments/photos below as applicable
ef2ad896-5038-5b96-87e8-c4b0a70a2851 | button | a. Has the schematic / layout of the flushed zone been highlighted, attached and flush points nominated | Yes, No
fc5129fd-e3bd-5648-a7b5-1ae4d657f161 | button | b. Is the flushed water clear with no visible debris or dirt. If NO, discuss with project foreman and or head office on why this might be the case | Yes, No
dbca4f9f-0741-5694-8b22-1e329d0b22f2 | button | c. Have you set a reminder for the next flushing of this pipework | Yes, No
a5a2cf9c-1411-5fdf-be6c-bbd8ee514949 | textbox | Test completed by
d0dff097-67d8-5ad4-84b1-85b1c10bc2aa | textbox | Date for next flushing (Flushing to be performed every 4 weeks at a minimum)
72eda57a-1f0b-5e7e-995c-d96b6e49dfcc | signoff | Click to add Builders Signature(s)
7c9a9e1a-1d4e-5ea4-a9bb-a82737153162 | checkpoint | Reference Table
ba92ffbf-ef7b-5d98-9be2-354484227217 | note | 25mm Pipe / 0.49 (L/m) / Flush for 0.15 (Mins)
92c1ca36-90ff-5c84-832c-b8c414f1577b | note | 32mm Pipe / 0.80 (L/m) / Flush for 0.25 (Mins)
98e44198-4a8a-5f20-ba53-a128e83c81a2 | note | 40mm Pipe / 1.26 (L/m) / Flush for 0.39 (Mins)
67087260-04fc-5a9d-9d8c-272b4ab28478 | note | 50mm Pipe / 1.96 (L/m) / Flush for 0.61 (Mins)
d0b82f22-83ac-54d4-9226-7c5121c04a17 | note | 65mm Pipe / 3.32 (L/m) / Flush for 1.04 (Mins)
ece32ea9-e6f8-52ed-9908-308dea4bb8b3 | note | 80mm Pipe / 5.02 (L/m) / Flush for 1.57 (Mins)
e9731a23-b9d5-5c1b-bb1e-e1a9849e0248 | note | 100mm Pipe / 7.85 (L/m) / Flush for 2.46 (Mins)
e84c2bd9-4927-5fdb-b42a-2afb1bd9c419 | note | 150mm Pipe / 17.66 (L/m) / Flush for 5.53 (Mins)
a8ca5914-ec89-598a-a33e-5d54a2f086b3 | note | NOTE: The table flushing time is based on 100 metres of pipework discharging through 16mm nozzle at 350KPa
431f5903-29b6-5f4c-bd3d-31ba409ddb70 | section | Part 2 - Water Quality Testing Frequency
061d1007-5427-5484-9010-724ad045be72 | checkpoint | Water Quality Testing Details
4cad266e-f3dd-5ca8-8225-c0dd77d2e5ff | note | Stage of water quality testing during the project
f1323cc2-208d-5270-813d-f7ec443609b2 | tickbox | 1. Periodic water quality testing during construction (to be completed every 3 months)
ea7af0d4-d5a5-5951-b6cc-f7101ea08957 | tickbox | 2. Water quality testing post final flush
09f91e64-7f74-41c9-8af3-8a3fbf4e237f | checkpoint | Sign-Off - Pass once entered
38ce1d14-ee5e-5937-8518-d466ffe1d6be | note | Add comments/photos below as applicable
5fe20241-cab8-5014-a263-4cfe4a87f95a | button | a. Geschke and John Holland management informed of sample / testing | Yes, No
92dc9e8c-cd9c-592d-857d-241abdecce38 | button | b. Has the schematic / location of the sample collection been highlighted, attached, and nominated | Yes, No
41ef2235-966a-5a10-a83c-69104b8b0eed | button | c. Sample captured as per laboratory requirements | Yes, No
bd7b5737-42ed-586f-bd43-5194c8d054ab | button | d. Time and date of sample recorded | Yes, No
f434af43-132e-55d4-8ba0-ca19640d884e | textbox | Time of Sample
09ad9cd2-6420-55fd-baeb-826a49a0d75f | textbox | Date of Sample
01329bfa-7873-5948-9989-46c05c34dc24 | textbox | Location of Sample
94850d26-fd8e-5068-8bf2-3e4cbba33fb2 | note | .. ..
eb981d73-4fb0-5906-8813-caf839fdd903 | textbox | Sample collected by
429d63ca-ae20-5c19-b8cf-ed9ef8cd2a9d | textbox | Date for next Water Quality Sample (Water quality testing to be performed every 3 months at a minimum during construction)
c8cdcd60-f957-5d5e-b2fa-bdaf57a8901b | signoff | Click to add Builders Signature(s)
4ecf8bfe-5836-55ec-b9df-1d5234e6182c | section | Part 3 - Disinfection of Pipework & Tank
46345207-4520-5b88-b10c-408665b0e340 | checkpoint | Disinfection Checks - Pass once below completed
e6e740dc-b3cb-5901-99b4-f631a4c39b95 | note | Add comments/photos below as applicable
52c8136b-76cb-53e7-85ed-54e63c1f35b8 | button | a. Geschke and John Holland management informed of disinfection with plan provided | Yes, No
02f71b91-dc2f-58b7-bf4f-4dc69cae6967 | button | b. Has disinfection occurred for 6 hours as per AS/NZS 3500.1 appendix I | Yes, No
208783e5-25c1-503b-b137-ce9e1016b2ff | button | c. Time and date of disinfection | Yes, No
26180882-c7d8-5581-9204-90d2c73ee6d3 | button | d. Flush all levels and branches until chlorination levels have reached safe chlorine levels as per Australian drinking water guidelines. | Yes, No
7a9959a7-ea24-5920-93d8-a57bf7313d70 | textbox | Time of Disinfection
b459ff69-10b5-5d36-a11c-b4ed70288867 | textbox | Date of Disinfection
2283b912-d3e8-580f-a3bc-2c977a40b50f | note | .. ..
a59575c6-9598-5a37-a010-b30b6707cca6 | textbox | Disinfection Completed by
309d5d01-8cdf-55cf-af85-cb80b487d829 | signoff | Click to add Builders Signature(s)

## Project Checklist Templates
Id | Type | Name | Values | Prompting Name
6f8e6637-3632-4011-9a78-c545b816b6b0 | checklist | QA 4_Installation Test Sheet (Waste, Vent, Downpipes etc.) - NMH |  | Installation Test Sheet (Waste, Vent, Downpipes etc.)
646c52fd-1d53-45b5-8417-0bb5fe5a5835 | section | Details
6baed2fb-a9ca-4315-ba50-77a43c6378e4 | checkpoint | Installation Test Sheet:
612c1095-1e87-52f5-9166-2373abd6c331 | textbox | Drawing No.:
de0c3037-6569-56e1-b59d-0c4174aa875a | textbox | Rev.:
bc0b0b2f-f39f-4b12-afb3-5fee569d6c85 | checkpoint | PIPE CLIP HANGERS
6828e1b6-5bda-51c4-b885-d2a8c25bbfef | textbox | Details:
f5687ac9-b524-50a0-be0a-8515558efbb9 | textbox | Tester:
2c4b5981-a657-5513-86e7-fb546ee19dad | textbox | Date:
30a80c4d-a63d-538c-b035-d6fb91111b66 | textbox | Notes:
28230616-73ce-4b2c-9b6f-08f91fb1be1f | checkpoint | MATERIAL AND SIZE
32740b6c-b008-5eb2-8769-b88c53f48f09 | textbox | Details:
6f12145c-3113-5f0c-a0a2-f6845ce2682b | textbox | Tester:
96510d46-ea25-5248-a115-cd830625a603 | textbox | Date:
73735099-5675-55db-b0e8-3229e8b97b95 | textbox | Notes:
b7b2c727-9eaf-455f-97c5-2ebd9e4d5619 | checkpoint | ALIGNMENT
25236c03-69a1-5890-8ff4-d59da240e6b1 | textbox | Details:
43a57ecc-f625-571c-bff2-d58fde1ca45f | textbox | Tester:
0d7f759b-e927-5eaa-84eb-0973015b836b | textbox | Date:
2dae1808-9267-51a3-9575-f81003e52dd8 | textbox | Notes:
41c85227-7f67-43a0-92f9-32e7bd58323f | checkpoint | LABELLING AND IDENTIFICATION
0cb244c5-2d9e-57f2-8df2-ea3503cadca6 | textbox | Details:
e65d88b7-4715-5f84-8672-564eb3a2bb30 | textbox | Tester:
4e8cbf61-754b-5a50-9ba0-a1871ec8aec0 | textbox | Date:
61b43eb0-59b6-5215-b3ac-a1f7d9558af5 | textbox | Notes:
57850d55-7342-417f-91e2-7b8042abf5e5 | checkpoint | JOINTING
baa54902-a391-591b-b9cd-a5c42168b07e | textbox | Details:
9540e238-df84-5908-b2b9-78871dc68d61 | textbox | Tester:
4841a55b-3805-5d74-bf01-486e93f6bc18 | textbox | Date:
9a526f4f-4606-5630-9506-a52e274cc195 | textbox | Notes:
fcf16c27-e585-4b8c-b47d-c171ece33511 | checkpoint | PENETRATION SEALING
9a138212-0996-577b-8abe-3eff1f76b4a0 | textbox | Details:
1433a160-ae3c-5547-aa68-eff4b0704114 | textbox | Tester:
65812b97-5d79-5ddc-9d91-e8d3024a35df | textbox | Date:
516c0098-a187-5121-a097-1be65089ee1a | textbox | Notes:
f33ac2e5-8a50-4c00-8131-f6b12c44348e | checkpoint | FIRE STOP COLLARS
a3e64fcc-f56b-5ff9-85f9-d4147967b73a | textbox | Details:
5c186d27-acbc-5206-a271-f19aef8ce59c | textbox | Tester:
e3eb240d-19d9-5436-9244-80ff144bdafd | textbox | Date:
88c22cf2-ce2a-5dc8-8e6a-6e3623df63ea | textbox | Notes:
146da8c7-c197-445c-ac1b-9b4ecc321545 | checkpoint | TESTING
df19a199-dd92-5f63-b3bc-4fe649da0cbf | textbox | Details:
0e89326b-2a7d-52f8-a888-e3a253a2093d | textbox | Tester:
20481d4c-a3cb-505d-b1f9-92f343692db5 | textbox | Date:
736b1f55-1eec-5cc1-ab3d-7916c59f9e53 | textbox | Notes:
dda752d8-e9cd-4970-b47a-67248ec69ce4 | checkpoint | AUTHORITY INSPECTION (if applicable)
b1e52c19-c580-5231-b164-d325a1ad7800 | textbox | Details:
86e22599-1061-521b-ba25-60cd6f2abb55 | textbox | Tester:
e425159b-3d52-5008-a105-381f96675d18 | textbox | Date:
45d10bef-2a65-5c2a-8bf0-bed09dc157da | textbox | Notes:
36cc8542-a55f-4141-a7c2-4fdee202fe0e | checkpoint | AS BUILT INFORMATION UPDATED ONTO DRAWINGS
9f81105a-fc7e-5e31-b988-26af9a5e0a4f | textbox | Details:
05cf65c0-d09e-5ef9-8a6a-d28058099679 | textbox | Tester:
0fb65325-4d5f-5e4d-b616-181022caba2c | textbox | Date:
5587b1b7-fba8-59c2-855f-9caf4696fd3a | textbox | Notes:
f942574c-e1ff-4281-a35a-3b8ef4d0f9e4 | checkpoint | Sign Off
3244be60-6601-5434-a575-525c69a0f856 | button | Geschke Group Signature added below | Yes,No,N/A
eb9d7436-c56b-5e33-84ec-b5d88edad118 | button | LendLease Signature added below | Yes,No,N/A
163aca38-18a3-5eb2-ba17-1cfbdb8898c4 | button | ARUP Group Signature added below | Yes,No,N/A
fe53e166-e43b-4321-bc60-24a788867b1b | checklist | QA 5_Installation Test Sheet (Cold Water, Hot Water & Flusher Line) - NMH |  | Installation Test Sheet (Cold Water, Hot Water & Flusher Line)
61ba9b3c-17a5-4497-843c-63893e9cfda2 | section | Details
a148829e-f2d5-457e-92a6-7004a7b5c9a9 | checkpoint | Installation Test Sheet:
630a218d-6bc8-59c1-8f1d-6195be89c0cb | textbox | Drawing No.:
71b877d6-7bd2-57fd-be00-684df6a7f7fb | textbox | Rev.:
aa9a8e27-0841-47ce-913c-fb205b338aab | checkpoint | PIPE CLIP HANGERS
c0f6602d-6f5b-533c-a70a-d165aedc858d | textbox | Details:
18ba6ab1-ae70-54dc-bf5c-573fd17c225f | textbox | Tester:
1669df67-608d-545e-9e82-4759fe3f7677 | textbox | Date:
94997e0e-c207-5fb1-b33c-5205cc5cdd52 | textbox | Notes:
73936a69-7440-4c89-9bd5-2f6ae914d263 | checkpoint | MATERIAL AND SIZE
80ae4b1b-69bf-56f0-ab51-715361dd990c | textbox | Details:
e887deec-2fcc-5e08-b822-01c2e03e2922 | textbox | Tester:
7755c09a-5ccb-5f69-8ea1-19d85e16ea1f | textbox | Date:
ca6d9951-47b6-5ed5-bb94-ab167e86bc22 | textbox | Notes:
b15cdec5-3173-4047-9ff5-dcddac425b56 | checkpoint | ALIGNMENT
4478ff09-cf2a-5e9a-9e2a-74a13777d564 | textbox | Details:
ba57c135-6ecc-5474-bf83-44c0e353aa25 | textbox | Tester:
7efb35ab-0ec8-5417-8e8b-7c2e37c65ee3 | textbox | Date:
6d924f6d-cbca-59c2-b224-e175c697b792 | textbox | Notes:
473c5bba-5f0d-4f1f-a623-52bdba28c484 | checkpoint | LABELLING AND IDENTIFICATION
74f31af2-b0a7-5911-9f1c-976f4d2f43bf | textbox | Details:
72f8786d-2c26-5574-a116-fd12669966db | textbox | Tester:
b67f3681-b68c-51d6-832a-05ae5425e21d | textbox | Date:
ac55a667-2bc6-57b7-bbee-76cec23210b7 | textbox | Notes:
3abec63c-90c8-4d56-9a66-e104ecbd8949 | checkpoint | JOINTING
53cc5b62-e499-5022-ae22-37aaf9460b36 | textbox | Details:
ff92b988-cff8-5873-a29b-a26213208e74 | textbox | Tester:
70919d0f-63ca-58f0-9ccc-b1c70f160313 | textbox | Date:
279a9823-e471-5103-9f69-efaa70651706 | textbox | Notes:
086e4b5f-26c1-48f0-a920-6a2d6f7a1a31 | checkpoint | PENETRATION SEALING
e02f03e9-5d72-56fd-aa70-b2d6f80bc677 | textbox | Details:
15067faf-3220-5ec7-a134-988f6322362d | textbox | Tester:
a96ce179-e4e2-5c7a-939b-80519b8e93f3 | textbox | Date:
64ea3a1b-2998-521b-913d-bc5f068b96f4 | textbox | Notes:
64e3fc18-cf0e-4b5f-ba52-1d0a1d0da69b | checkpoint | FIRE STOP COLLARS
51b0f44a-05a4-5af2-96d1-6bee44a7d526 | textbox | Details:
88102046-8871-587c-9147-9fbf2d87025f | textbox | Tester:
15d99e32-4162-5ab2-a713-73243cdb871f | textbox | Date:
513b1e05-9ee4-5e22-8517-7944b3815e9e | textbox | Notes:
3b63e7c4-04aa-4f5a-813f-e3c6c71ea858 | checkpoint | PRESSURE TESTING COMPLTED (QA6)
122f5a09-b5eb-5816-ae87-c7bbc9c92b3e | textbox | Details:
c39fe8fc-4371-5cd2-934c-787046507920 | textbox | Tester:
cce6714c-5551-521b-8235-c11ca08d176a | textbox | Date:
7d0357cf-6e4e-5db5-b33c-45ec8a923284 | textbox | Notes:
ba1bc570-85c5-4270-b7b0-3fafff545524 | checkpoint | AUTHORITY INSPECTION (if applicable)
c0796a45-7757-53b7-8fc3-17af56b5ea1d | textbox | Details:
164e0303-3483-5d91-8961-74d862a78640 | textbox | Tester:
bdd4a46b-b6f8-56f4-a0c8-75bf6d52bebb | textbox | Date:
1524b333-6e5c-5925-8136-2c9b07b45d9e | textbox | Notes:
9d5a1b90-842a-4216-8055-b32a13fa732b | checkpoint | AS BUILT INFORMATION UPDATED ONTO DRAWINGS
9a5d29cf-6cb5-56ab-9c5a-fbfde52c7b80 | textbox | Details:
3712072c-d5b3-507a-ad3f-f98e8e774ae3 | textbox | Tester:
d81d1f2d-b146-5b65-9d72-9756763c2074 | textbox | Date:
1cbb6e91-1eae-59ed-9dfd-ddada845c9f1 | textbox | Notes:
2e2d5be8-1c11-4746-b9ec-bdcf70dd6fd3 | checkpoint | WATER FLUSHING PROCEDURE
ca118dfb-a0fb-5aea-a166-2f45fc3973a6 | textbox | Details:
3c3eff4c-2a45-58e5-b24e-3e6abdfd1fb5 | textbox | Tester:
11f7b25b-a232-5847-8a16-6cb991303ca1 | textbox | Date:
a306151d-fd9e-5791-bbdb-4948c57d62cc | note | No stagnant water to be left in mains. Refer separate GPL procedure QA29 and confirm compliance Yes/No
7b5e0aea-d12d-455e-a926-cefd4f8df431 | checkpoint | Sign Off
8acd09b6-027f-5b7c-b006-10cabbd79144 | button | Geschke Group Signature added below | Yes,No,N/A
281a0a58-18b9-5da7-88ba-fa5074d8b7de | button | LendLease Signature added below | Yes,No,N/A
995a7a4d-b106-50d4-b1b2-901e6f1a2589 | button | ARUP Group Signature added below | Yes,No,N/A
14cd05c6-8a3c-4467-96e4-dd42a92fee7e | checklist | QA 6_Quality Control Pressure Test Report - NMH |  | Quality Control Pressure Test Report
37412267-351e-41c9-a077-9c68889a1e41 | section | Details
38bd704c-2338-4d45-b385-acea3dd176f7 | checkpoint | Quality Control Pressure Test Report:
f1ea0539-2ddb-5cf2-a12e-6968a9f4f1ba | textbox | Drawing No.:
5346f552-1b45-5f76-a846-b45cd20b1ed8 | textbox | Rev.:
9160e0aa-bde4-57fa-90de-c8885b903423 | button | Test: | Air,Water
f107e52d-2bc5-5ee6-8a88-591c5d9d0022 | textbox | Section
058f0ce9-8f6a-56d0-9db0-f7b9305a9b73 | textbox | From
c7bc9172-2f9d-5bf5-8d53-46beb35ff1ff | textbox | To
2892e761-fa74-5d0c-bec0-a7f3beba6f82 | note | Specified System Working
5f2ed617-3893-5d65-adfb-8f883226a4b2 | textbox | Pressure (KPA)
808ff92d-c62c-5c09-a6c6-b654875f42f7 | textbox | Duration (HRS)
ddd0c906-b028-5202-b5f1-3e20b8a758a5 | note | Specified System Test
9eb9d932-384a-521f-97ab-9b8e8616aaac | textbox | Pressure (KPA)
a0565770-bea3-5457-b5f4-0e8471546981 | textbox | Duration (HRS)
68cb87fd-3c82-4251-89db-8b31cd99fc31 | checkpoint | 1st Reading
71448bc2-13b3-585e-8d6a-3037e3648aab | textbox | Time
ff59fae3-cf46-5c3d-b583-dca0fae406e6 | textbox | KPA
e150308c-87c7-5a4c-9461-d98e4d366906 | textbox | Ambient Temp
28359b75-f216-43e0-9ec6-859d75b1d224 | checkpoint | 2nd Reading
e989982a-0869-5c2f-ab17-f4a244284055 | textbox | Time
7d525d33-565d-5fe3-8953-fc993bef69ed | textbox | KPA
b654c60d-f395-5baf-be97-3f26a0915751 | textbox | Ambient Temp
38c7a11c-97a9-448e-92a9-0434332c836f | checkpoint | Test Result - Passed?
3572676a-0a96-5175-b763-b4cfbc077e2c | textbox | Repeat
ce37d76e-0013-4082-8b96-2334192153da | checkpoint | Sign Off
a949035a-9b5b-5bd8-986b-43ae94eb4fc9 | button | Geschke Group Signature added below | Yes,No,N/A
1f03f8a9-9489-545d-a9c8-c0395fdb4d40 | button | LendLease Signature added below | Yes,No,N/A
c92b883b-f76e-5705-9a81-5b07f9d0f6b1 | button | ARUP Group Signature added below | Yes,No,N/A
061ead0c-13e5-53bf-aef3-1af2c0a4da22 | date | Date of Satisfactory Completion
058a058b-9617-4d40-8c8a-10744bcbb78a | checklist | QA 6C_Quality Control Flow Test and Compliance Report - Safety Showers - NMH |  | Quality Control Flow Test and Compliance Report - Safety Showers
2e26e035-5713-4ca9-8b9b-a046749ce7ae | section | Details
528210ee-7efa-4d1d-99ef-2f9933737689 | checkpoint | Quality Control Flow Test and Compliance Report - Safety Showers:
976b410c-f032-558d-bc8c-9c22e7f2388d | textbox | Drawing no./rev:
0ba8e460-5934-5c9f-b102-3d38aceea443 | textbox | Appliance Tested:
c7cf65f5-2cdd-5062-bbd3-d027881ad4f3 | textbox | Room No.:
81463eab-d641-4717-a32e-59d655ffe35b | checkpoint | Specified System Working
5647fe25-11e7-5a17-8586-13d2f42c1e29 | textbox | Pressure:
f968ba11-375f-5978-b24c-3ac0f0cb6968 | textbox | Flow Rate:
eb05e63f-9913-4f51-81b1-492555f93ecc | checkpoint | International Standard ANSI Z358.1 2004
1bedf9de-3455-54ee-b2d8-8dc4545eb672 | textbox | Pressure:
aa916ab8-18a5-5198-8b66-700ae51d0926 | textbox | Flow Rate:
57bc4500-4812-47b2-ba92-7be8b455a2bf | checkpoint | Pipe Installed
f0e14b3e-9b04-56da-877b-7c4c1d251d96 | textbox | Pressure set on each floor: KPA
9b9e8fad-05cc-55e0-a5f3-c7d256684148 | textbox | Cold - Size:
fb3d3a85-db31-579c-a38f-f94aa1dd8973 | textbox | Capable Flow Rate:
1a0f026d-2e34-58ee-b651-a60140f335ab | textbox | Hot - Size:
cd970e43-0156-5514-84a0-43f0d97be95f | textbox | Capable Flow Rate:
734d7f14-5183-4ba3-8b4e-df5519e6188d | checkpoint | TMV Installed
1dccd502-5c9f-5b15-9cae-0e347d5893a7 | textbox | Brand:
21e9a241-2a5c-5584-b672-d0b791a4eb79 | textbox | Model:
d496e620-6895-5072-8431-fd0d94ae0baa | textbox | Flow Rate:
aff82706-9e2d-51d9-8695-620dabea399a | textbox | Temp Set:
33f8cf35-f15b-40d9-a6d9-1dbb1e0be5f0 | checkpoint | Pull Lever Confirm Flow
038b41ba-f5ed-45db-92d2-f0e0403e3634 | checkpoint | Riser Valves Open
3af666cd-973e-4d52-8bcf-35dd07808ed0 | checkpoint | Safety Shower Valve Open
9c4c5244-b86d-47eb-9fc4-ab277cdf07a1 | checkpoint | Drain Outlet not Obstructed
0b3b1756-1ba0-45a8-8929-d326b95ed9e1 | checkpoint | Temperature Test
bc5220e5-9f2c-5b39-acd8-77195e090318 | note | Disconnect shower head, connect hose and extend to drain, turn on shower, test temperature.
00e6aaae-6873-53f8-8d3a-9186ab141606 | textbox | Temperature:
a78a2214-354a-4c5d-b783-7194171de0a6 | checkpoint | Sign Off
79edeeb9-1577-55b2-a5ff-bf88b46a12ab | button | Geschke Group Signature added below | Yes,No,N/A
2ffbc0f9-e236-53c1-bb5a-ac492cb11813 | button | LendLease Signature added below | Yes,No,N/A
7fdded16-4282-5e65-bb85-0e33458ba259 | button | ARUP Group Signature added below | Yes,No,N/A
13c41cc2-3483-5333-926a-d59a492e52ee | date | Date of Completion of Satisfactory Test
422ea28d-5bcc-4dad-9b7d-2318191ad099 | checklist | QA 8_Below Ground Pipework Checklist - Fire - NMH |  | Below Ground Pipework Checklist - Fire
3733e933-6357-487f-bb70-34692e7e91fb | section | Details
93371cdf-4aa4-4057-adb2-974f64b19193 | checkpoint | LendLease Permits Issued
9a65c7ab-a7d6-4f0e-94fa-7e1d638738f8 | checkpoint | Set out pits depths and trench runs.
65160080-0b92-5934-befc-7cb1f60c0047 | note | As per DRG#
469e5ad2-43b9-5c51-a7ff-3e161f337bef | textbox | Drawing No.:
489b5f77-3513-4009-ba35-a70dfa0a6612 | checkpoint | Pipes and fittings comply with relevant Authority and Specification.
33a99224-edd1-5d87-bdc4-29f494f5636a | note | Spec#: AS3500
4711c2ac-e3c4-5196-a476-90c04e759528 | textbox | Material used
126a4b02-adc3-4a13-9b2e-554b819cf12a | checkpoint | Bedding placement and compaction and material meets specification.
50069f88-3f33-534f-b438-a8973f9435c7 | note | Spec#: AS3500 and Hydraulic Specification
a2e2ac4a-9a3f-4f89-b915-34097698d1c4 | checkpoint | Jointing of pipes
446e4ad8-b1a5-5b75-91fb-88f600a28235 | button | Jointing type | Electrofusion, Butt Welding, Both
d64c466d-45f7-51f1-b980-3fc21d2c3feb | note | Refer to 'QA16 EF Welding' and/or 'QA 25 Butt Welding' ITP
1ade1978-3930-4ed7-ad93-e516ada6ec49 | checkpoint | Connections to pits and existing services as per spec and Australian Standards
44f37535-6334-4758-9238-bc329fdf22fd | checkpoint | Hydrostatic tests are carried out as required.
ff544108-612f-5efe-86fe-c5a3591bf167 | button | GPL QA6 form completed | Yes,No
2176ae98-d92c-5b08-861e-440e09b71b49 | note | Fire system tested to 1700 kpa regularly prior to finished surfaces installed. Independent fire test at completion.
f3597d9f-c36c-40fe-acc2-3cfe0cb26ff4 | checkpoint | Placement and compaction of backfill and material meets spec.
c0abc56e-b0fa-50f8-a4b7-9c0c6858b32f | button | Compacted backfill as per the Specification | Yes,No
30dd5746-acea-5134-9069-6d551b01af02 | note | Detectable marker tape
911f02f7-cfc8-4c76-aad7-c5f37b285f90 | checkpoint | Temporary cover provided to open drain.
8df1978d-a182-456b-a2c5-3e9e48449806 | checkpoint | PVC/ Plastic caps to open ends
62f4a740-27a0-4f1f-b126-a51840d1ead0 | checkpoint | As built information updated onto drawings
67d59e1f-db1a-5d28-ae03-0dcf2d74712c | note | Ongoing, to be provided
b58d587d-ab48-4b4d-941f-a5cb79562ac7 | checkpoint | Sign Off
2f122cb4-c08b-5c31-8151-1881ab2234c1 | button | Geschke Group Signature added below | Yes,No,N/A
c53d7746-7417-532a-a847-55978b461da3 | button | LendLease Signature added below | Yes,No,N/A
43c88c71-0059-543d-9e51-4153a9e7e59e | button | ARUP Group Signature added below | Yes,No,N/A
63e54f5b-282c-4af6-aecf-876e5c12c379 | checklist | QA 8_Below Ground Pipework Checklist - Sewer - NMH |  | Below Ground Pipework Checklist - Sewer
91bcd7ac-18ab-4180-b87f-58ddea93fc34 | section | Details
ebfc9db2-a6a1-4f7d-b589-14c64700266f | checkpoint | LendLease Permits Issued
9f4630ac-f1a2-4601-bdfd-b2f01ee4f19b | checkpoint | Set out pits depths and trench runs.
5e98f1b0-8b66-5eec-b278-6e2be52e762d | note | As per DRG#
73b36896-6cb2-50c5-8adc-893cd50612ad | textbox | Drawing No.:
2a9cdea1-8703-40dd-8510-fbe283cc69d7 | checkpoint | Pipes and fittings comply with relevant Authority and Specification.
bdd6b96d-73f5-5832-974d-4f81061a60bc | note | Spec#: AS3500
c3c27ccc-fe26-5b00-894d-4b3758379289 | textbox | Material used
e391c9b6-194a-425f-8acc-7ee75ac58edc | checkpoint | Bedding placement and compaction and material meets specification.
40051253-be0c-572d-8853-82346b1b5076 | note | Spec#: AS3500 and Hydraulic Specification
4619d6e4-1085-52e1-9897-529d3b305733 | note | 75mm Q-Minus Bedding and Encasement to top of pipe
db9241d5-83d0-4c3f-a31a-d30ff73a41ee | checkpoint | Laying and jointing of pipes R.Ls and falls
975c4f11-36b4-5609-85fb-afaae5fc59f9 | note | PVC solvent welded
dd31d92e-fa5c-520a-b15f-1336fe14167e | note | 1:60 fall
5c2ec4cc-071c-5af3-95d4-2503e6f647f8 | note | AS3500
299b4869-2488-5b37-9f51-f823430f580e | note | RLs as per hyd drgs
af7f5841-0f53-42d2-aa94-9660a2ff194a | checkpoint | Connections to pits and existing services
937f0538-6438-458d-9866-2a30840640a7 | checkpoint | Hydrostatic tests are carried out as required.
3ac827b6-11f4-58b5-ad6c-bd40730197bb | button | Air or Water? | Water,Air
4279fd4e-8d50-5ad9-a835-fe2b17b0e768 | note | Inspected and recorded by Independent Certifier or PIC (See attached)
eb7b06ef-f1f7-4394-b54a-dcba673c26ac | checkpoint | Mirror tests are completed if required.
2c087100-f618-4c56-9d1f-c9d75b1a4f18 | checkpoint | Placement and compaction of backfill and material meets spec.
f0a9ef93-eb66-559f-9047-645b16b16d82 | note | Compacted crushed rock backfill 80% to 100% compaction
630d9e6c-9aa8-4488-8246-d77e174f26b2 | checkpoint | Temporary cover provided to open drain.
ae0c0310-ea1c-41bb-ae98-e4c17ff01cff | checkpoint | PVC/ Plastic caps to open ends
ad0cafdf-36c5-4406-be47-0322b8ca4636 | checkpoint | As built information updated onto drawings
c03dba40-4097-5e4c-a633-10ed5f6eae6e | note | Ongoing
b7c235d7-a332-582e-be3a-2a41809c7490 | note | To be provided
9bdd10e3-9d29-486d-befc-704efd0c8ba1 | checkpoint | Sign Off
876148c5-f961-58b0-9514-53fa5decab58 | button | Geschke Group Signature added below | Yes,No,N/A
44df2575-9ed7-52c1-aa52-f48beb40d559 | button | LendLease Signature added below | Yes,No,N/A
10105dbd-f030-52cf-9783-3d34fcc9d941 | button | ARUP Group Signature added below | Yes,No,N/A
7e9c7ba0-dffe-4408-90db-9c08bc02105d | checklist | QA 8_Below Ground Pipework Checklist - Water - NMH |  | Below Ground Pipework Checklist - Water
c21fd6f2-605b-405c-b907-4cbb96d21766 | section | Details
274cee94-1968-4c0f-b844-6a13b58eff84 | checkpoint | LendLease Permits Issued
f53d1377-8d8f-4a94-8db7-3056f838370c | checkpoint | Set out pits depths and trench runs.
d0719476-655f-5d7f-9820-9cd3577928bd | note | As per DRG#
c17b7923-2a55-5fa2-9973-5503d0b9ad0f | textbox | Drawing No.:
d512d945-5162-472f-b663-2eb39473d194 | checkpoint | Pipes and fittings comply with relevant Authority and Specification.
b4ca88a8-0bb5-532d-ade4-5c891489e3fd | note | Spec#: AS3500
2e4fcf1a-ef8a-4d63-98a7-4a5ead3df4ac | checkpoint | Bedding placement and compaction and material meets specification.
ac85ce93-fb80-5758-b5a1-53d92a804a26 | note | Spec#: AS3500 and Hydraulic Specification
deeaeaf0-91d1-40a9-a8c0-31d88684ac07 | checkpoint | Jointing of pipes
c600fccf-f627-55ce-87f3-8ab44d6c9119 | button | Jointing type | Electrofusion, Butt Welding, Both
c6e5c305-875e-5e08-bd46-f97adba7e636 | note | Refer to 'QA16 EF Welding' and/or 'QA 25 Butt Welding' ITP
581a5aed-6758-4c94-8125-29833eb556bf | checkpoint | Connections to pits and existing services as per spec and Australian Standards
2423a87d-cd68-4133-a973-88a67cfeba84 | checkpoint | Hydrostatic tests are carried out as required.
bcf27f23-709a-5237-9cf6-d181c49f00b7 | button | GPL QA6 form completed | Yes,No
33121f62-8cf9-5005-9f58-b2b3f53f79af | textbox | Water system tested to (kPa)
2b49010c-09df-4b80-9267-fed3c5554939 | checkpoint | Placement and compaction of backfill and material meets spec.
69e79f56-c83c-5150-8a76-9754aa2ea48f | button | Compacted backfill as per the Specification | Yes,No
8a03e774-14cd-5229-a670-702ee88135cb | note | Detectable marker tape
3a72bfcc-c3a9-47d1-a32f-67ec42c6e15f | checkpoint | Temporary cover provided to open drain.
528bc3ee-b046-4ff9-9bc7-97068defe3ba | checkpoint | PVC/ Plastic caps to open ends
a4726ee7-4675-4a80-95d0-5d91fdb77776 | checkpoint | As built information updated onto drawings
890fe4c9-b5be-560f-8ddf-26a398f9dd79 | note | Ongoing
75cb5cf2-a570-504e-aa11-a7354415e1d6 | note | To be provided
46bda824-1635-45de-985f-57bea19ea315 | checkpoint | Sign Off
8b7db3c4-a310-537f-aca8-681e7ec882b5 | button | Geschke Group Signature added below | Yes,No,N/A
2a1c8686-d724-5841-980f-84d69c853ceb | button | LendLease Signature added below | Yes,No,N/A
f1f5b11b-19b0-5031-9d3a-a70c4cbe3af0 | button | ARUP Group Signature added below | Yes,No,N/A
60072010-15cb-4033-99ee-29f4aae33744 | checklist | QA 8A_Grease Trap Checklist - NMH |  | Grease Trap Checklist
a2029d16-038a-4b59-a66a-5dde13d33921 | section | Details
b63cc243-02c4-431e-b334-14eaa64d366e | checkpoint | Set out of pits.
07aeb428-7f5a-4f1b-9d80-f0a036196ddb | checkpoint | Pipes and fittings comply with relevant Authority and Specification.
d5922bdc-dd81-448f-a8d1-45aa47d99ba4 | checkpoint | Bedding placement and compaction and material meets specification.
d0a9a925-8ee7-4327-af94-7743c67bd175 | checkpoint | Laying and jointing of pipes R.Ls and falls
0c729385-2d62-4358-94fa-3db1d5c42426 | checkpoint | Connections to pits.
7d618bdd-5118-47f6-b796-3058811456e3 | checkpoint | Baffle is in place.
fa0d4e60-e63e-46fb-9337-3130cd2b6b81 | checkpoint | Penetrations are patched and made watertight.
8ea6517d-9f18-4d1f-95ee-0e27df8d15e7 | checkpoint | Suction line is installed as per spec.
46b01b4e-9040-4a2a-8938-c2c5e8ad60cf | checkpoint | Outlet pipework is installed as per spec.
162fe674-6628-42ff-b411-aaf2fe62a601 | checkpoint | Vents are connected and terminated to comply with Authority and Specification.
d3c19a19-3d73-4b23-86cc-db5325a165ad | checkpoint | As built information updated onto drawings
d50fe153-495e-4a6a-bb4e-2f8d94520631 | checkpoint | Sign Off
ac88610b-aada-5572-8ecf-e93b871dd03e | button | Geschke Group Signature added below | Yes,No,N/A
2ed70533-ee26-51fd-9ba1-bda6a595fad2 | button | LendLease Signature added below | Yes,No,N/A
1a079de5-d552-5b46-a402-3442908945ae | button | ARUP Group Signature added below | Yes,No,N/A
ba01ff88-747d-4f74-ad48-fe2bae9a638e | checklist | QA 8B_Stormwater Drainage Inspection Report - NMH |  | Stormwater Drainage Inspection Report
8f4e8010-7a57-47d7-98e9-c4ab98873394 | section | Details
edfbdcd0-bf99-4992-93b9-9090ccae172c | checkpoint | Stormwater Drainage Inspection Report Details:
860c3c60-02fa-5b8a-b9cb-31b4fdd12b74 | textbox | Spec No.:
8c967bca-4931-54dd-9256-c4d14fc4f502 | textbox | Drawing no.:
5cb5547c-5bfb-5f99-b4ff-fac7f6092965 | textbox | Zone:
5b23c958-c9c2-4ff3-8c07-20654ff45ebb | checkpoint | Pipe Lines
536ff7fb-ecdd-5642-8d12-ff2802e21bfb | textbox | Date started:
40d03787-2208-576f-bed0-986f8c7ba8b2 | textbox | Drainage Line Number:
2dea8040-9c90-5c1c-84f5-a7531f12e70e | button | Pipe Damaged? | No,Yes
4ae9cbb1-c510-5829-9424-80ea176da66b | textbox | Size and Class
4ac8879e-ea4c-52b6-a925-64eaccd0484b | textbox | Jointing Required
519cb3d5-670b-5dc2-a874-85ec5172a6b4 | note | Bedding and Haunching
5032c3a8-26fc-5b67-a476-70fc87949480 | textbox | GPL - Initial/Date
9e78e0bd-4038-5ced-9e10-093edf6502a6 | textbox | LendLease - Initial/Date
0582ed1b-9be9-547e-9e9e-e47d0963ee5d | note | Backfill
233df84e-9bd1-56cb-a31b-ced8134a227d | textbox | GPL - Initial/Date
73b63d65-639d-561d-aabb-fd5e8521ffaf | textbox | LendLease - Initial/Date
40d771d6-526a-52c7-ba4b-cde7094a89dc | textbox | Comments
4ee53eb8-1339-5cbc-8e54-9d8c8595247f | note | Final Sign Off (Initial & Date)
68dcfc9a-15a8-5ba2-9fbe-62d1317370c4 | textbox | GPL
bae43d34-8032-5ba1-95c2-beef68bceabe | textbox | Lendlease - Initial/Date
ae773bcb-0dbb-44da-82fd-8d5ee5b69428 | checkpoint | Drainage Pits
25eb6d63-7972-5c9f-90fb-14026a1d7ce2 | textbox | Date Installed:
4d42b486-fe51-5f07-926f-a7d0c7d84284 | textbox | Pit Number:
19dc2aa6-4050-5776-ad8a-7e39b2eacd0c | textbox | Pit Base:
3dbdaad8-333c-5129-8a70-5b4ad35bb44a | textbox | Step Irons - GPL Initial/Date
c1fcbe8a-670a-5a58-bb1b-eda9a9d769f0 | textbox | Bedding - GPL Initial/Date
d4493030-fb3e-563b-b582-2764b8cd230c | note | Benching, Grouting and Patching
e7e687f7-d920-5ba5-9fd8-d1bc2bd939ac | textbox | GPL - Initial/Date
63c19b89-80c0-58c5-bb51-1db71c276678 | textbox | Lendlease - Initial/Date
c3fdafbd-3062-5ccb-a061-f4cabb3b7de0 | note | Placement of cover
e801e243-e47a-5fe4-82ca-2d6643b3a06d | textbox | GPL - Initial/Date
fc92a033-ca25-56ee-90ef-fef7928302b6 | textbox | LendLease - Initial/Date
b6edb717-5597-5c88-8ff9-659566b6d3f6 | textbox | Comments
8944aa8d-4ef6-504b-9b6b-89eac512df47 | note | Final Sign Off (Initial & Date)
52094092-28cb-5207-a885-ac309ea27128 | button | Geschke Group Signature added below | Yes,No,N/A
ddc7b107-c39b-5c98-b17c-6c1627f407ef | button | LendLease Signature added below | Yes,No,N/A
a71cdd46-af02-54e5-a6b3-71f438d82464 | button | BG&E Signature added below | Yes,No,N/A
446a03f7-f557-5adf-b62d-0f1a05588694 | button | ARUP Group Signature added below | Yes,No,N/A
c7489eab-1d3e-40e1-b14a-616c68a60686 | checkpoint | Compaction Test Report No.
a4e27b02-5bb5-50a5-8177-17b5f8ece50b | textbox | Compaction Test Report No.:
6d655e1a-32e2-46a8-971a-3d55ace806a3 | checklist | QA 15_Pre Cast Slab Penetration Placement Checklist - NMH |  | Pre Cast Slab Penetration Placement Checklist
18f8de6f-f4ff-467f-a2fc-bcac1b04ed22 | section | Details
35c9b2d6-3525-434f-b086-905e45dc9720 | checkpoint | Pre Cast Slab Penetration Placement Details:
2dd1e744-8acb-5173-aa52-ce92c4c32f37 | textbox | Drawing No. / Rev:
1e5e7a16-b871-5091-b4c1-64ca581205d7 | textbox | Slab No.
d548beaa-9feb-55e5-b9ae-bbb157467288 | textbox | Total: Sewer - waste penetrations
12daf191-8b95-5382-b799-8e5c009ca713 | textbox | Total: Stormwater penetrations
31cf0ae4-845d-580b-b759-980f07bbbf6a | textbox | Total: Water
f2dc595c-089b-5a05-b4f0-9ca490f0fc4e | textbox | Other:
1ef43e31-5120-450e-8382-b37046a1606f | checkpoint | Sign Off
7e9dbba0-9de2-5e0f-a5ac-a4fa269bef62 | button | Geschke Group Signature added below | Yes,No,N/A
95c00560-f2c3-5927-bdd9-761aab9331a4 | button | LendLease Signature added below | Yes,No,N/A
7e654a48-1646-51e8-ab4d-fc9c1055411c | button | ARUP Group Signature added below | Yes,No,N/A
61148dfe-c9f3-4cd8-a29f-d62bb0453852 | checklist | QA 29_Periodic Flushing / Copper Protection Test Sheet - NMH |  | Periodic Flushing / Copper Protection Test Sheet
411e9ffb-13f5-495f-a741-3f899928c41a | section | Details
6a37b32c-6508-4f9e-b2ec-4c215d3b8573 | checkpoint | ITP QA 29 Periodic Flushing / Copper Protection Test Sheet
8b4718b7-426d-5316-84da-06bb6d0ce321 | note | Copper systems are failing in the construction industry due to stagnate water being left in both hot and cold copper pipelines. Copper needs to form a protective layer of copper oxide on the internal surface which is formed by the contact with fresh aerated and oxygenated water. Periodic flushing of the systems is the only way to ensure this occurs.
3fabac19-48d2-5b02-af17-e8c94ebb65bb | note | The purpose of this ITP is to help you create the strategy to get this water out and replaced with fresh water every four weeks.
76325a75-5df9-442c-9bae-f18646e4f63f | checkpoint | Flushing Details:
441c302e-5e88-5a81-b4b0-d64a70a2047b | textbox | Level / building being flushed:
d1f5c4ae-27e4-507a-bc5c-6130a8d5d175 | button | Time and Type of flushing: | Ring main Single point for flushing; the entire loop can be achieved in a maximum 10-minute flush., Non ring mains Any copper sub-branch from the main feed requires individual flush time of 5 minutes (an example of this would be a corridor feed)., Short branches of copper that feed rehau do not need individual flushing., Multi storey projects will require flushing on each level. Starting from the top and working your way down
24740ef4-cda7-575c-880f-e526f59367f2 | textbox | Which fixtures are being used to flush the system (Point of connection and point of discharge):
36c7270f-865a-549a-97bf-57828bab918f | textbox | Start time of flushing:
7084cebd-4a3c-5c28-9fec-2cf50eb39606 | textbox | Zone/branch to be flushed:
78633a19-8335-51a1-bf07-3bcc5dbab3df | textbox | Finish time of flushing:
7accf84d-fdad-5310-ae82-c8670559c715 | textbox | Zone/branch to be flushed:
fa23fff9-fffa-4a6d-b1be-0753fbf45320 | checkpoint | Has the schematic / layout of the flushed zone been highlighted, attached and flush points nominated.
86e0d1ff-7cd9-4aa3-a530-0e58503797f0 | checkpoint | Is the flushed water clear with no visible debris or dirt. If NO, discuss with project foreman and or head office on why this might be the case.
33f206c1-c5f9-4e24-848b-e8710d9e909d | checkpoint | Have you set a reminder for the next flushing of this pipework?
54f69a7d-2708-40b4-8080-ac21fc75233d | checkpoint | Have the hot and cold been interconnected for flushing purposes?
b566bf39-e315-4573-b761-acd8f635b3e4 | checkpoint | Date for next flushing (Flushing to be performed every 4 weeks):
3599150a-a9a4-539f-95e8-bf5830bad203 | textbox | Date for next flushing:
1192265a-0575-5306-ae60-18726a41fbe9 | textbox | Test completed by:
2ca2aa63-4c9e-5c68-b6d6-f14c0764014b | textbox | LendLease Representative: