## Sheet1
3.1 | Survey/as-builts | IFC Drawings | Survey final position and top R.L. of each pile, produce As-Built drawings including stated measurements of pile lengths; record bedrock level | Each Pile | Pile tolerance is to be: - 75mm horizontally of the location as shown in the drawings - Vertical location of the pile top at plus 40mm or minus 75mm of the position shown in the drawings - Pile verticality of 1H:75V or straighter | H | R | As-Built | 3.1 - Survey/as-builts | Method/Description - Survey final position and top R.L. of each pile, produce As-Built drawings including stated measurements of pile lengths; record bedrock level | Test frequency - Each Pile | Contractor - H | Designer - R | Lab - | Verifying Records Checklists, Test and Supplier Certificates - As-Built | 3.1 - Survey/as-builts
3.2 | Red-Line As-built | . | Draewings updated to reflect any changes during construction Any RFI's and NCR's noted on drawings and closed out prior to drawing re-issue | On Completion of Works | Accepted by CPS Manager & Quality Manger | H | R | Red-Line As-Built | 3.2 - Red-Line As-built | Method/Description - Draewings updated to reflect any changes during construction Any RFI's and NCR's noted on drawings and closed out prior to drawing re-issue | Test frequency - On Completion of Works | Contractor - H | Designer - R | Lab - | Verifying Records Checklists, Test and Supplier Certificates - Red-Line As-Built | Method/Description - Survey final position and top R.L. of each pile, produce As-Built drawings including stated measurements of pile lengths; record bedrock level
Test frequency - Each Pile
Contractor - H
Designer - R
Lab -
Verifying Records Checklists, Test and Supplier Certificates - As-Built
3.2 - Red-Line As-built
Method/Description - Draewings updated to reflect any changes during construction Any RFI's and NCR's noted on drawings and closed out prior to drawing re-issue
Test frequency - On Completion of Works
Contractor - H
Designer - R
Lab -
Verifying Records Checklists, Test and Supplier Certificates - Red-Line As-Built