## res
type | name | values | prefix | postfix | usage count | user addable | template name
checklist | 561469-ITP-0003 - Pipelines (DG-QA-TP018) | itp |  |  |  |  | 561469-ITP-0003 - Pipelines (DG-QA-TP018)
section | SECTION 3 – RECEIVING INSPECTIONS
checkpoint | 3.1 - Review all Drawings and Documents
label | Inspection Point: Quality Control Activity - Review all drawings and documentation provided to the Contractor.
label | Acceptance Criteria - Prior to the commencement of Works it must be ensure that all necessary documentation has been provided.
label | Verifying Document - ITP
label | Frequency - Prior to the commencement of Works
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - R
label | Inspection: By (Role Key) - PM/QE
checkpoint | 3.2 - Setting Out Levels and Alignment
label | Inspection Point: Quality Control Activity - All setting out shall be performed by or under the control of a licensed surveyor, who shall certify the accuracy of key dimensions of the as constructed works. Specs 1000: 3.2.4
label | Acceptance Criteria - Levels and allignment Set Out matches marks shown on the Drawings, 2D data and linework provided or agreed with the Engineer
label | Verifying Document - Compliance surveys or spot checks
label | Frequency - Prior to the commencement of Works
label | Inspection Type (Visual, other) - Visual, Instrumental
label | Inspection: Key - H
label | Inspection: By (Role Key) - SP/QE/SV
holdpoint | HOLD POINT
checkpoint | 3.3 - Service location and Hydro Vacumming
label | Inspection Point: Quality Control Activity - Physically locate the services inside and close to the alignment area and levels depth. Specs 1131: 15.2.1
label | Acceptance Criteria - All services identified in B4UDig, plans and mark outs has been physically located
label | Verifying Document - Plans Mark out, photos
label | Frequency - Prior to the commencement of Works
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - H
label | Inspection: By (Role Key) - CR
holdpoint | HOLD POINT
checkpoint | 3.4 - Pipes Delivery
label | Inspection Point: Quality Control Activity - Pipes and pipe fittings shall be of the material, pipe class and joint type nominated on the Drawings. Specs 1131: 14.1 and Drawings C152 - C153
label | Acceptance Criteria - The charasteritics of the pipes delivered to site match the corresponding drawings details or approved equivalent
label | Verifying Document - Delivery docket, Supplier certificate, Photo
label | Frequency - Prior to the commencement of Works
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - C
label | Inspection: By (Role Key) - QE/CR
checkpoint | 3.5 - Valves Delivery
label | Inspection Point: Quality Control Activity - Gate valves shall comply with AS/NZS 2638. Valves greater than DN50 shall be resilient seated sluice valves. DN50 shall be gate valves. Sluice valves shall be anti-clockwise closing. DN50 gate valves shall be clockwise closing. Valves shall be provided with a surface box according to the asset owner’s engineering standards. Specs 1131: 14.3.1
label | Acceptance Criteria - The charasteritics of the valves delivered to site match the corresponding specifications, drawings details or approved equivalent
label | Verifying Document - Delivery docket, Supplier certificate, Photo
label | Frequency - Prior to the commencement of Works
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - C
label | Inspection: By (Role Key) - QE/CR
checkpoint | 3.6 - Joints and Fittings
label | Inspection Point: Quality Control Activity - All joints and fittings must comply with wath is estipulated on Specs 1131: 14.3.2
label | Acceptance Criteria - The charasteritics of the fittings delivered to site match the corresponding specifications, drawings details or approved equivalent
label | Verifying Document - Delivery docket, Supplier certificate, Photo
label | Frequency - Prior to the commencement of Works
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - C
label | Inspection: By (Role Key) - QE/CR
checkpoint | 3.7 - Pipe Bedding and Haunching Agregate
label | Inspection Point: Quality Control Activity - Pipe bedding should be AP20 and in accordance with AS/NZS 2566.2 or AS/NZA 3725. Maximum Dry Density (MDD) and Optimum Water Content (OWC) of the aggregate must be provided. Specs 1131: 14.9.1
label | Acceptance Criteria - Visual Inspection, Engineer approval
label | Verifying Document - Delivery Docket, Laboratory test results
label | Frequency - Prior to the commencement of Works
label | Inspection Type (Visual, other) - Visual, Lab Test
label | Inspection: Key - H
label | Inspection: By (Role Key) - QE/SP/MC
holdpoint | HOLD POINT
checkpoint | 3.8 - Buried Warning Tape
label | Inspection Point: Quality Control Activity - Metallic detector tape shall be provided to comply with the NZUAG code of practice. Tapes shall comply with AS/NZS 2648.1. Tapes shall incorporate a 316 stainless steel detectable tracer wire where required. Specs 1131: 14.6.1
label | Acceptance Criteria - Received warning tape comply with specifications and standard
label | Verifying Document - Delivery docket, Supplier certificate, Photo
label | Frequency - Prior to the commencement of Works
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - C
label | Inspection: By (Role Key) - QE/SP/MC
checkpoint | 3.9 - Backfill Aggregate
label | Inspection Point: Quality Control Activity - Backfill aggregate should be GAP 65. Samples of backfill material should be tested in accordence of NZS 4402 to determine the MDD at OMC. The solid density of aggregate should be tested in accordance with NZS 4407. Specs 1131: 16.1.1
label | Acceptance Criteria - Visual Inspection, Engineer approval
label | Verifying Document - Delivery Docket, Laboratory test results
label | Frequency - Prior to the commencement of Works
label | Inspection Type (Visual, other) - Visual, Lab Test
label | Inspection: Key - H
label | Inspection: By (Role Key) - QE/SP/MC
holdpoint | HOLD POINT
checkpoint | 3.10 - Concrete Manhole, Catchpits and Access Chambers
label | Inspection Point: Quality Control Activity - Precast concrete estructures shall comply with NZS 3106. Specs 1131: 14.5
label | Acceptance Criteria - Manhole charasteritics Match NZS 3106
label | Verifying Document - Delivery docket, Supplier certificate, Photo
label | Frequency - Prior to the commencement of Works
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - C
label | Inspection: By (Role Key) - QE/SP/MC
checkpoint | 3.11 - Route Markers
label | Inspection Point: Quality Control Activity - Route markers shall be provided where shown on the Drawings or as required by the Principal. Specs 1131: 14.6.3
label | Acceptance Criteria - Route marker supplied according to the drawings and requirements
label | Verifying Document - Delivery docket, Photo
label | Frequency - Prior to the commencement of Works
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - C
label | Inspection: By (Role Key) - QE/SP/MC
checkpoint | 3.12 - Material Storage
label | Inspection Point: Quality Control Activity - Storage for materiales must be arranged as it is described in: Specs 1131: 14.10
label | Acceptance Criteria - Pipe stored according to specifications
label | Verifying Document - Photo
label | Frequency - Prior to the commencement of Works
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - C
label | Inspection: By (Role Key) - QE/SP/MC
checkpoint | 3.13 - Backfill Trail Compaction Testing
label | Inspection Point: Quality Control Activity - Prior to commencement of fill compaction. Trial compaction plateau test should be conducted under presense of Engineer or principal. Methodology to be confirmed in advance generally in accordance with TNZ B/02 specification. Specs 1131: 16.1.1, 16.1.2, 16.1.4.
label | Acceptance Criteria - Compaction Value ≥ Specification Value
label | Verifying Document - Nuclear Density Meter (NDM) Results Sheet, or Clegg Hamer test records
label | Frequency - Prior to the commencement of Works.
label | Inspection Type (Visual, other) - On site Test
label | Inspection: Key - H
label | Inspection: By (Role Key) - QE/CR
holdpoint | HOLD POINT
checkpoint | 3.14 - Defective Materials
label | Inspection Point: Quality Control Activity - Any materials that do not comply with this specification or that have been damaged as a result of the Contractor’s operations shall be removed from site and replaced at the Contractor’s expense. Repairs may be considered at the sole discretion of the Engineer. Specs 1131: 14.12
label | Acceptance Criteria - Defective material detected and removed from site
label | Verifying Document - Delivery docket, Photo
label | Frequency - Prior to the commencement of Works
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - C
label | Inspection: By (Role Key) - QE/SP/MC
section | SECTION 4 – IN-PROCESS INSPECTIONS
checkpoint | 4.1 - Site Clearance
label | Inspection Point: Quality Control Activity - The material obtained from site celarance must be dumped at an approved location outside the Site. Specs 1100: 5.1
label | Acceptance Criteria - Location approved by the Engineer
label | Verifying Document - Dumping Docket
label | Frequency - After site clearance
label | Inspection Type (Visual, other) - Document Check
label | Inspection: Key - C
label | Inspection: By (Role Key) - QE/SP/CR
checkpoint | 4.2 - Trees Removal
label | Inspection Point: Quality Control Activity - No tree shall be cut down until the Engineer has given written authorisation for such work to commence. Specs 1100: 6.2
label | Acceptance Criteria - Engineer Approval
label | Verifying Document - Engineer Writen Authorisation
label | Frequency - Before remove any tree
label | Inspection Type (Visual, other) - Client Consultation
label | Inspection: Key - H
label | Inspection: By (Role Key) - CR
holdpoint | HOLD POINT
checkpoint | 4.3 - Removal of Topsoil
label | Inspection Point: Quality Control Activity - Topsoil shall be stockpiled in areas approved by the Engineer for this purpose. stockpiling operations must ensure the maximum utilisation of each area. Specs 1110: 9.4, TNZ F/1 Clause 4
label | Acceptance Criteria - Engineer Approval
label | Verifying Document - Engineer Writen Authorisation
label | Frequency - Before Topsoil Removal
label | Inspection Type (Visual, other) - Client Consultation
label | Inspection: Key - C
label | Inspection: By (Role Key) - CR
checkpoint | 4.4 - Hazardous Waste and Contaminated soils
label | Inspection Point: Quality Control Activity - Contaminated soils (Type H materials) encountered shall be treated and/or disposed off site in accordance with statutory requirements. Specs 1110: 9.3
label | Acceptance Criteria - Dumping site approval for contamiantion type
label | Verifying Document - Dumping Docket
label | Frequency - If constaminated soils are found
label | Inspection Type (Visual, other) - Document Check
label | Inspection: Key - C
label | Inspection: By (Role Key) - QE/SP/CR
checkpoint | 4.5 - Trench Excavation
label | Inspection Point: Quality Control Activity - Trenches for flexible pipes shall be excavated within tollerances in table from Specs 1131: 15.2.5 unless otherwise stated.
label | Acceptance Criteria - Trench width and pipe clearance to walls comply with requirements
label | Verifying Document - Installation Check Sheet
label | Frequency - During trench excavation
label | Inspection Type (Visual, other) - Visual, Measurement Check
label | Inspection: Key - C
label | Inspection: By (Role Key) - QE/SP
checkpoint | 4.6 - Pipe Bedding and Haunching
label | Inspection Point: Quality Control Activity - Bedding and Haunching for flexible pipes should be in accordance with AS/NZS 2556.2 and have minimum embedment zone as shown in table from Specs 1131: 15.2.8.2
label | Acceptance Criteria - Bedding and haunching high and with comply width requirements
label | Verifying Document - Installation Check Sheet
label | Frequency - During bedding and haunching installation
label | Inspection Type (Visual, other) - Visual, Measurement Check
label | Inspection: Key - C
label | Inspection: By (Role Key) - QE/SP
checkpoint | 4.7 - Pipe Line and Level
label | Inspection Point: Quality Control Activity - Pipes shall be laid true to the design line and level within the tolerances specified in Specs 1131: 15.9. Invert levels shall take precedence over depths. Specs 1131: 15.3.12
label | Acceptance Criteria - Pipe levels are within the tolerance and according to the drawings, 2D data and linework provided or agreed with the Engineer
label | Verifying Document - Grade Check sheet
label | Frequency - During pipe installation
label | Inspection Type (Visual, other) - Visual, Instrumental
label | Inspection: Key - C
label | Inspection: By (Role Key) - SP/QE/SV
checkpoint | 4.8 - PE Pipe Installation
label | Inspection Point: Quality Control Activity - Buried PE pipes shall be installed in accordance with AS/NZS 2033 and AS/NZA 2566.2, as applicable. Specs 1131: 15.3.2.2
label | Acceptance Criteria - PE Pipe Joints and Intallation comply with standard and specifications
label | Verifying Document - Pipe welds QA records, welding checksheets and machine printouts, destructive tests results (if required)
label | Frequency - Per weld, and during pipe installation
label | Inspection Type (Visual, other) - Visual, Document Check, Lab test (if required)
label | Inspection: Key - C
label | Inspection: By (Role Key) - QE/SP
checkpoint | 4.9 - PVC Pipe Installation
label | Inspection Point: Quality Control Activity - Buried PVC pipes shall be installed in accordance with AS/NZS 2032 and AS/NZS 2566.2, as applicable. Fusible PVC pipes shall be welded and installed in accordance with the pipe manufacturers recommendations. Specs 1131: 15.3.1.
label | Acceptance Criteria - PVC Pipes Joints and Intallation comply with standard and specifications
label | Verifying Document - Methodology, Pipe welds QA records, welding checksheets and machine printouts, destructive tests results (if required)
label | Frequency - Per joint or weld, and during pipe installation
label | Inspection Type (Visual, other) - Visual, Document Check, Lab test (if required)
label | Inspection: Key - C
label | Inspection: By (Role Key) - QE/SP
checkpoint | 4.10 - Precast Concrete Pipe Installation
label | Inspection Point: Quality Control Activity - Joints between precast pipe units shall be self-centering and shall be sealed with butyl mastic or similar approved to form a watertight joint. Concrete pipes shall be installed in accordance with AS/NZS 3725. Specs 1131: 15.3.6
label | Acceptance Criteria - Precast concrete pipes Joints and Intallation comply with standard and specifications
label | Verifying Document - Methodology. QA records
label | Frequency - Per joint, and during pipe installation
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - C
label | Inspection: By (Role Key) - QE/SP
checkpoint | 4.11 - Aggregate Compaction
label | Inspection Point: Quality Control Activity - Compaction shall be as stated in Specs 1131: 15.4.4. For concrete pipes the verification testing of compaction shall use a method recommended in table 3 of the CPAA Technical Note on Installing Concrete Pipe and approved by the Engineer. Specs 1131: 15.3.6
label | Acceptance Criteria - Compaction Value ≥ Specification Value
label | Verifying Document - Depending of Pipe material or Aggregate: CBR Checksheet, Nuclear Density Meter (NDM) Results Sheet, Clegg Hamer test records
label | Frequency - Every 50m of trench (not confirmed) or specified by Engineer
label | Inspection Type (Visual, other) - On site Test
label | Inspection: Key - H
label | Inspection: By (Role Key) - QE/CR
holdpoint | HOLD POINT
checkpoint | 4.12 - Backfill Compaction
label | Inspection Point: Quality Control Activity - Selected fill within 0.8m depth from finished surface shall be AP 65. Subgrade and subbase shall be compacted in layers no greater than 200 mm thick unless otherwise agreed with the Engineer. Under carriageway basecourse shall be compacted in layers no greater than 150mm thick unless otherwise aggred with the engineer. Specs 1131: 15.4.3.2, 15.4.3.3
label | Acceptance Criteria - Dry Density ≥ 95% MDD (Under Carriageway). Dry Density ≥ 90% MDD (Outside Carriageway)
label | Verifying Document - Nuclear Density Meter (NDM) Results Sheet or Clegg Hamer test records
label | Frequency - Every 20m of trench, each layer (Under Carriageway). Every 50m of trench, each layer (Outside Carriageway)
label | Inspection Type (Visual, other) - On site Test
label | Inspection: Key - H
label | Inspection: By (Role Key) - QE/CR
checkpoint | 4.13 - Cutting pipes
label | Inspection Point: Quality Control Activity - Where pipes need to be cut to form non-stardard lengths, pipes shall be cut by a method which complies with manufacturers recommendations and provides a clean square profile. Specs 1131: 15.3.7
label | Acceptance Criteria - Pipe cutted up to the specifications
label | Verifying Document - Methodology, Photos
label | Frequency - During pipe installation
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - C
label | Inspection: By (Role Key) - QE/SP
checkpoint | 4.14 - Manhole Benching
label | Inspection Point: Quality Control Activity - Benching concrete shall have a crushing strength of 20MPa at 28 days. Semi-circular channels and fittings shall be placed in possition simultaneously with concrete benching and be embedded in true to grade level and line. All benching and sloping surfaces on manhole floor shall be rendered in 20mm thick 1:3 mortar and finished with steel trowel and rounded at corners. Specs 1131: 15.5
label | Acceptance Criteria - Benching built up to the specifications
label | Verifying Document - Methodology, Delivery Dockey, Photos
label | Frequency - During benching contruction
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - C
label | Inspection: By (Role Key) - QE/SP
checkpoint | 4.15 - Subsoil Drains Installation
label | Inspection Point: Quality Control Activity - Drains shall be constructed, geotextile layed and backfill carried out in accordance with TNZ Specification F/6. Specs 1131: 15.7
label | Acceptance Criteria - Benching built up to the specifications
label | Verifying Document - Methodology, TNZ Specifications F/6 and F/7, Photos, QA records
label | Frequency - During Drains Installation
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - C
label | Inspection: By (Role Key) - QE/SP
checkpoint | 4.16 - Topsoiling and grassing
label | Inspection Point: Quality Control Activity - Topsoil shall be used to dress areas disturbed by the contrat works to a minimum thickness of 100mm. Grass seed shall be sown evenly over the prepared topsoil area. Specs 1131: 15.8.6
label | Acceptance Criteria - Topsoil installed and grass seed spread in the specified rate and mixture.
label | Verifying Document - QA records, Photos
label | Frequency - After compaction of final layer of backfill
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - C
label | Inspection: By (Role Key) - QE/SP
checkpoint | 4.17 - Tracing Wire
label | Inspection Point: Quality Control Activity - Tracing wire shall be installed and tested according to what is detailed in: Specs 1131: 14.6.2
label | Acceptance Criteria - Tracer wire installation complies with the specifications
label | Verifying Document - QA records, Photos
label | Frequency - Before pipe and fittings installation, testing after the completion of the network section installation
label | Inspection Type (Visual, other) - Visual, On site test
label | Inspection: Key - C
label | Inspection: By (Role Key) - QE/SP
checkpoint | Welding PE pipes
label | Inspection Point: Quality Control Activity - Jointing shall be done in accordance with pipe manufactures specifications. Where unspecified PE butt welding shall be in accordance with PIPA POP003 and PE electrofusion welding in accordance with PIPA POP001. All welds shall be marked with weld number and welder identification. (maybe put here that everything must be in accordance to the specs)
label | Acceptance Criteria - Specification 1131 15.3.2.1
label | Verifying Document - Weld records
label | Frequency - each weld
checkpoint | Bulkheads
label | Inspection Point: Quality Control Activity - Shall be placed and constructed as per DCC typical detail 10328
label | Acceptance Criteria - Drawing C120, C220
label | Verifying Document - methodology
label | Frequency - During installation
checkpoint | Joint inspections
label | Inspection Point: Quality Control Activity - Each butt-welded joint will be visually inspected by the engineer
label | Acceptance Criteria - Specification 1131 16.3.2.1
label | Verifying Document - QA records
checkpoint | Lab Testing
label | Inspection Point: Quality Control Activity - Three butt welded joints and one section of virgin pipe shall be tested in accordance with ISO 13953.
label | Acceptance Criteria - Specification 1131 16.3.2.2
checkpoint | Joint inspections
label | Inspection Point: Quality Control Activity - Each electrofusion joint shall be visually inspected by the contractor
label | Acceptance Criteria - Specification 1131 16.3.1
label | Verifying Document - QA records
checkpoint | Lab Testing
label | Inspection Point: Quality Control Activity - pipes with nominal diameters 90mm and larger shall be tested in accordance with ISO 13954
label | Acceptance Criteria - Specification 1131 16.3.2.3
checkpoint | Ductile Iron Pipe Installation
label | Inspection Point: Quality Control Activity - a) Ductile iron pipes shall be installed in accordance with AS/NZS 2566.2.
label | b) Ductile Iron Pipes shall be cement mortar lined in accordance with AS 1281 or AS/NZS 1516 and comply with NZS 3122 and be externally painted with a bituminous coating in accordance with AS/NZS 3750.4 for Bitumen Paint.
label | c) When laid underground, DI pipes shall have a loose polyethylene protective sleeve to AS 3680 and applied in accordance with AS 3681. Specs 1131: 15.3.3
checkpoint | Steel Pipe Installation
label | Inspection Point: Quality Control Activity - a) Steel pipes shall be installed in accordance with AS/NZS 2566.2.
label | b) Steel pipes shall have spigot and socket joints with rubber rings or shall be plain ended and butt welded as appropriate. Steel pipes shall be flanged where shown on the Drawings.
label | c) Flanges shall be drilled as specified.
label | d) Pipes for welding shall be joined by an automatic arc welding process capable of consistently producing welds complying with the requirements of NZS 4442.
label | e) Manual arc welding with automatic wire feed and automatic fluxing may only be used for the repair of weld defects. Manual welding shall occupy no more than 2 % of the total weld length in any pipe, and no weld repair shall be longer than 300 mm.
label | f) Full details of the welding procedure and of the edge preparation proposed to be used shall be supplied to the Engineer prior to welding.
label | g) Any faulty welds shall be cut out and rewelded. On no account shall leaks be sealed by caulking.
label | h) On completion and acceptance of the welding, the external corrosion protection shall be suitably repaired, and both the weld and coating inspected by the Principal or Engineer.
label | i) Steel pipes shall be externally protected with one of the following:
label | i. for buried pipes, a high-density polyethylene sleeve, “black jacket” complying with AS/NZS 1518 or “Polyken Synergy” wrapping, or “Polyken YG111” wrapping.
label | ii. for pipe above ground, a zinc metal spray sealed with vinyl or epoxy coating complying with AS/NZS 2312, or a fusion bonded epoxy coating complying with AS/NZS 3862.
label | j) Steel pipes shall be fitted with cathodic protection complying with AS 2239 and AS 2832.1. Specs 1131: 15.3.4
checkpoint | Stainless Steel Pipe Installation
label | Inspection Point: Quality Control Activity - a) Stainless steel pipes shall be installed in accordance with AS/NZS 2566.2.
label | b) All welds between stainless steel components shall be in accordance with AS 4041. Butt welds shall be full penetration. The weld preparation shall be in accordance with AS/NZS 1554.1.
label | c) All stainless-steel welding shall be carried out using approved welding techniques and appropriate procedures. Welds shall be chemically cleaned and fully passivated to an approved procedure. Specs 1131: 15.3.5
checkpoint | Pipes in a Common Trench
label | Inspection Point: Quality Control Activity - a) Parallel pipelines in a common trench shall be laid sufficiently apart to ensure that the required compaction and support of the side support material is achieved.
label | b) Minimum clear distances between pipes can be reduced where flowable fill embedment materials are used, in line with the applicable pipeline installation standards. Specs 1131: 15.3.8
checkpoint | Clearances to other Services
label | Inspection Point: Quality Control Activity - Unless agreed with the Engineer or specified elsewhere herein or on the Drawings:
label | • The minimum clearance of sewer to other services is in table 5.6 to other utility services and structures in clause 5.3.7.10 of NZS4404.
label | • The minimum clearance of water pipelines is in table 6.4 to other utility services and structures in clause 6.3.9.2 of NZS4404. Specs 1131: 15.3.9
checkpoint | Pipes Connected to Structures
label | Inspection Point: Quality Control Activity - a) Where a pipe is built into an underground structure, a flexible joint shall be provided as close as possible to the outside face of the structure. A short length of rocker pipe shall be connected to the flexible joint. The length of the rocker pipe shall not exceed 8 times the diameter or three (3) metres, whichever is the shorter and shall be a minimum of 1,200 mm.
label | b) PE, PVC connections through walls and floors: an annular space of not less than 6 mm shall be left around the pipe or fitting and the clearance shall be sealed with a flexible sealant such as loosely packed felt, a rubber convolute sleeve or other suitable flexible sealing material such as PE foam or neoprene.
label | c) Water-tightness at penetrations. Unless otherwise specified, for (material A, etc.) penetrations through a chamber or manhole wall shall be secured either with a concrete anchor block extending 1.5 x pipe diameters and puddle flange with rubber ‘O’ ring and hydrophilic sealant strip. For (material X, etc.) penetrations shall be secured with a concrete anchor block extending 1.5 x pipe diameter with hydrophilic sealant strips. Specs 1131: 15.3.10
checkpoint | Cast in-situ Concrete
label | Inspection Point: Quality Control Activity - Concrete cast in-situ for bedding, haunching, thrust blocks, anchor blocks and minor structures shall have a minimum strength of 20 Mpa at 28 days
label | Acceptance Criteria - Specification 1131 14.7
section | SECTION 5 – FINAL INSPECTION AND HANDOVER
checkpoint | 5.1 - As-built Drawings
label | Inspection Point: Quality Control Activity - Two hard copies and one electronic copy of As-built drawings shall be prepared in draft and final versions following Schedule 1D in NZS4404:2010. Specs 1000: 3.9.2
label | Acceptance Criteria - Engineer Approval
label | Verifying Document - QA records
label | Frequency - At completion
label | Inspection: Key - H
label | Inspection: By (Role Key) - QE/CR
holdpoint | HOLD POINT
checkpoint | 5.2 - Gravity Pipes Testing
label | Inspection Point: Quality Control Activity - Stormwater pipes shall be by visual inspection for pipe diameters greater than 750mm and by water testing for diameters up to 750mm. Testing shall be in the presence of the engineer. Specs 1131: 16.2.1
label | Acceptance Criteria - Engineer Approval
label | Verifying Document - Test Records
label | Frequency - For every section of pipe installed (24hr prior notice to the engineer before test)
label | Inspection Type (Visual, other) - Test
label | Inspection: Key - H
label | Inspection: By (Role Key) - QE/CR
holdpoint | HOLD POINT
checkpoint | 5.3 - Manholes
label | Inspection Point: Quality Control Activity - Manholes should be tested seperately to pipeline for water tightness up to lower rim of manhole cover frame. Testing shall be in the presence of the engineer. Specs 1131: 16.2.2.5
label | Acceptance Criteria - A maximum drop in water level over 30 min should not exceed 2mL/hr/mm of diameter/meter height of the manhole. Engineer Approval
label | Verifying Document - Test Records
label | Frequency - For every manhole installed (24hr prior notice to the engineer before test)
label | Inspection Type (Visual, other) - Test
label | Inspection: Key - H
label | Inspection: By (Role Key) - QE/CR
holdpoint | HOLD POINT
checkpoint | 5.4 - CCTV Inspection
label | Inspection Point: Quality Control Activity - All pipelines shall pass a CCTV instpection. All pipelines shall be free of debris and flushed 24hrs prior to inspection. Specs 1131: 16.2.3
label | Acceptance Criteria - A pipeline will fail its inspection if:
label | – The pipe is horizontally misaligned or deformed by more than 5 % of the pipe diameter.
label | – The pipe has visible dips or ponding of water.
label | – The pipe has visible defects, such as open or displaced joints, defective or protruding laterals, cracked barrels or similar defects.
label | – There is evidence of infiltration at joints or laterals.
label | Verifying Document - CCTV footage and log sheets
label | Frequency - At every section of pipe installed.
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - H
label | Inspection: By (Role Key) - QE/CR
holdpoint | HOLD POINT
checkpoint | 5.5 - Surplus Materials and Refuse Disposal
label | Inspection Point: Quality Control Activity - All surplus, redundant and faulty materials must be removed from the Site and dispose of them in a safe and legal manner. Any demolition material or rubbish coming from the execution of the project must be removed as well. Specs 1000: 3.13.2
label | Frequency - At completion
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - C
label | Inspection: By (Role Key) - QE/SP/CR
checkpoint | 5.6 - Cleaning
label | Inspection Point: Quality Control Activity - Completed items of construction about to be placed in service or occupied for their intended use must be properly and thoroughly cleaned of all foreign matter and other debris. Specs 1000: 3.13.3
label | Frequency - At completion
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - C
label | Inspection: By (Role Key) - QE/SP/CR
checkpoint | Air testing
label | Acceptance Criteria - Specification 1131 16.2.2.1
label | Verifying Document - Test Records
checkpoint | Pressure Testing
label | Inspection Point: Quality Control Activity - PE pipelines shall be completed in accordance with AS/NZS 2566.2:2002 relevant appendices
label | Acceptance Criteria - Specification 1131 16.3.1
label | Verifying Document - Test records
checkpoint | Corrosin Protection
label | Inspection Point: Quality Control Activity - a) Metallic connections shall be appropriately protected against galvanic / dissimilar material corrosion.
label | b) Metallic connections in contact with soil, regardless of any factory applied corrosion protection (e.g. HDG, FBE), shall be fully protected with a suitable petrolatum based wrapping tape (e.g. Denso Petrolatum, Polyken tape), including appropriate filler treatment (e.g. Densyl Mastic, Polyken Mastic) as and where required to ensure the tape does not bridge voids.
label | c) Corrosion protection systems shall be made available for inspection once they have been installed in situ, unless the Engineer permits otherwise. Specs 1131: 14.4