## Site QA Sheet
31-01-24 V0
Haven Parade (ST-11, ST-13, ST-15) | Work Zones | Work Lots | Work Elements | Checklists pulled from (Master Checklists Tab)
Folder Tier - 1 | Folder Tier - 2 | Folder Tier - 3 | Folder Tier - 3 | Folder Tier - 4
Site QA | Stage 11 | Lot 1101 | Authority Connections | Authority Main to Meter Installation
Site QA | Stage 11
Site QA | Stage 11 |  | In-ground Plumbing Services | Drainage Installation (In-ground)
Site QA | Stage 11 |  |  | Water Service Installation (In-ground)
Site QA | Stage 11 |  |  | Gas Service Installation (In-ground)
Site QA | Stage 11
Site QA | Stage 11 |  | Plumbing Services Rough-in | Waste & Vent Installation
Site QA | Stage 11 |  |  | Water Service Installation (Rough-ins)
Site QA | Stage 11 |  |  | Gas Service Installation (Rough-ins)
Site QA | Stage 11
Site QA | Stage 11 |  | Plumbing Services Fit-off | Toilet & Cistern Installation
Site QA | Stage 11 |  |  | Wash Basin & Tapware Installation
Site QA | Stage 11 |  |  | Shower & Tapware Installation
Site QA | Stage 11 |  |  | Bath & Tapware Installation
Site QA | Stage 11 |  |  | Kitchen Sink & Tapware Installation
Site QA | Stage 11 |  |  | Dishwasher Installation
Site QA | Stage 11 |  |  | Laundry Trough & Tapware Installation
Site QA | Stage 11 |  |  | Washing Machine Stops Installation
Site QA | Stage 11 |  |  | Tundish Installation
Site QA | Stage 11 |  |  | Hose Tap Installation
Site QA | Stage 11 |  |  | Gas Appliance Installation
Site QA | Stage 11 |  |  | Hot Water Unit Installation
Site QA | Stage 11
Site QA | Stage 11 |  | Plumbing Services Testing | Testing Drainage Pipework (Hydrostatic Test)
Site QA | Stage 11 |  |  | Testing Water Pipework
Site QA | Stage 11 |  |  | Testing Gas Service
Site QA | Stage 11
Site QA | Stage 11 |  | Plumbing Services Commissioning | Commission Rain Water Pressure Pump Set
Site QA | Stage 11 |  |  | Commission Water Storage Tank
Site QA | Stage 11 |  |  | Commission Hot Water Generating Plant
Site QA | Stage 11 |  |  | Commission Reduced Pressure Zone Device
Site QA | Stage 11 |  |  | Commission Fixture Group
Site QA | Stage 11
Site QA | Stage 11 | Lot 1102 | Repeat above work elements | Repeat above checklist
Site QA | Stage 11 | Lot 1103 | Repeat above work elements | Repeat above checklist
Site QA | Stage 11 | Lot 1104 | Repeat above work elements | Repeat above checklist
Site QA | Stage 11 | Lot 1105 | Repeat above work elements | Repeat above checklist
Site QA | Stage 11 | Lot 1106 | Repeat above work elements | Repeat above checklist
Site QA | Stage 11 | Lot 1107 | Repeat above work elements | Repeat above checklist
Site QA | Stage 11 | Lot 1108 | Repeat above work elements | Repeat above checklist
Site QA | Stage 11 | Lot 1109 | Repeat above work elements | Repeat above checklist
Site QA | Stage 11 | Lot 1110 | Repeat above work elements | Repeat above checklist
Site QA | Stage 11 | Lot 1111 | Repeat above work elements | Repeat above checklist
Site QA | Stage 11 | Lot 1112 | Repeat above work elements | Repeat above checklist
Site QA | Stage 11 | Lot 1113 | Repeat above work elements | Repeat above checklist
Site QA | Stage 11 | Lot 1114 | Repeat above work elements | Repeat above checklist
Site QA | Stage 11 | Lot 1115 | Repeat above work elements | Repeat above checklist
Site QA | Stage 11 | Lot 1116 | Repeat above work elements | Repeat above checklist
Site QA | Stage 11 | Lot 1117 | Repeat above work elements | Repeat above checklist
Site QA | Stage 11 | Lot 1118 | Repeat above work elements | Repeat above checklist
Site QA | Stage 11 | Lot 1119 | Repeat above work elements | Repeat above checklist
Site QA | Stage 11 | Lot 1120 | Repeat above work elements | Repeat above checklist
Site QA | Stage 11 | Lot 1121 | Repeat above work elements | Repeat above checklist
Site QA | Stage 11 | Lot 1122 | Repeat above work elements | Repeat above checklist
Site QA | Stage 11 | Lot 1123 | Repeat above work elements | Repeat above checklist
Site QA | Stage 11 | Lot 1124 | Repeat above work elements | Repeat above checklist
Site QA | Stage 11 | Lot 1125 | Repeat above work elements | Repeat above checklist
Site QA
Site QA
Site QA | Stage 13 | Lot 1301 | Authority Connections | Authority Main to Meter Installation
Site QA | Stage 13
Site QA | Stage 13 |  | In-ground Plumbing Services | Drainage Installation (In-ground)
Site QA | Stage 13 |  |  | Water Service Installation (In-ground)
Site QA | Stage 13 |  |  | Gas Service Installation (In-ground)
Site QA | Stage 13
Site QA | Stage 13 |  | Plumbing Services Rough-in | Waste & Vent Installation
Site QA | Stage 13 |  |  | Water Service Installation (Rough-ins)
Site QA | Stage 13 |  |  | Gas Service Installation (Rough-ins)
Site QA | Stage 13
Site QA | Stage 13 |  | Plumbing Services Fit-off | Toilet & Cistern Installation
Site QA | Stage 13 |  |  | Wash Basin & Tapware Installation
Site QA | Stage 13 |  |  | Shower & Tapware Installation
Site QA | Stage 13 |  |  | Bath & Tapware Installation
Site QA | Stage 13 |  |  | Kitchen Sink & Tapware Installation
Site QA | Stage 13 |  |  | Dishwasher Installation
Site QA | Stage 13 |  |  | Laundry Trough & Tapware Installation
Site QA | Stage 13 |  |  | Washing Machine Stops Installation
Site QA | Stage 13 |  |  | Tundish Installation
Site QA | Stage 13 |  |  | Hose Tap Installation
Site QA | Stage 13 |  |  | Gas Appliance Installation
Site QA | Stage 13 |  |  | Hot Water Unit Installation
Site QA | Stage 13
Site QA | Stage 13 |  | Plumbing Services Testing | Testing Drainage Pipework (Hydrostatic Test)
Site QA | Stage 13 |  |  | Testing Water Pipework
Site QA | Stage 13 |  |  | Testing Gas Service
Site QA | Stage 13
Site QA | Stage 13 |  | Plumbing Services Commissioning | Commission Rain Water Pressure Pump Set
Site QA | Stage 13 |  |  | Commission Water Storage Tank
Site QA | Stage 13 |  |  | Commission Hot Water Generating Plant
Site QA | Stage 13 |  |  | Commission Reduced Pressure Zone Device
Site QA | Stage 13 |  |  | Commission Fixture Group
Site QA | Stage 13
Site QA | Stage 13 | Lot 1302 | Repeat above work elements | Repeat above checklist
Site QA | Stage 13 | Lot 1303 | Repeat above work elements | Repeat above checklist
Site QA | Stage 13 | Lot 1304 | Repeat above work elements | Repeat above checklist
Site QA | Stage 13 | Lot 1305 | Repeat above work elements | Repeat above checklist
Site QA | Stage 13 | Lot 1306 | Repeat above work elements | Repeat above checklist
Site QA | Stage 13 | Lot 1307 | Repeat above work elements | Repeat above checklist
Site QA | Stage 13 | Lot 1308 | Repeat above work elements | Repeat above checklist
Site QA | Stage 13 | Lot 1309 | Repeat above work elements | Repeat above checklist
Site QA | Stage 13 | Lot 1310 | Repeat above work elements | Repeat above checklist
Site QA | Stage 13 | Lot 1311 | Repeat above work elements | Repeat above checklist
Site QA | Stage 13 | Lot 1312 | Repeat above work elements | Repeat above checklist
Site QA | Stage 13 | Lot 1313 | Repeat above work elements | Repeat above checklist
Site QA | Stage 13 | Lot 1314 | Repeat above work elements | Repeat above checklist
Site QA | Stage 13 | Lot 1315 | Repeat above work elements | Repeat above checklist
Site QA | Stage 13 | Lot 1316 | Repeat above work elements | Repeat above checklist
Site QA | Stage 13 | Lot 1317 | Repeat above work elements | Repeat above checklist
Site QA | Stage 13 | Lot 1318 | Repeat above work elements | Repeat above checklist
Site QA | Stage 13 | Lot 1319 | Repeat above work elements | Repeat above checklist
Site QA | Stage 13 | Lot 1320 | Repeat above work elements | Repeat above checklist
Site QA | Stage 13 | Lot 1321 | Repeat above work elements | Repeat above checklist
Site QA | Stage 13 | Lot 1322 | Repeat above work elements | Repeat above checklist
Site QA | Stage 13 | Lot 1323 | Repeat above work elements | Repeat above checklist
Site QA | Stage 13 | Lot 1324 | Repeat above work elements | Repeat above checklist
Site QA | Stage 13 | Lot 1325 | Repeat above work elements | Repeat above checklist
Site QA | Stage 13 | Lot 1326 | Repeat above work elements | Repeat above checklist
Site QA
Site QA
Site QA | Stage 15 | Lot 1501 | Authority Connections | Authority Main to Meter Installation
Site QA | Stage 15
Site QA | Stage 15 |  | In-ground Plumbing Services | Drainage Installation (In-ground)
Site QA | Stage 15 |  |  | Water Service Installation (In-ground)
Site QA | Stage 15 |  |  | Gas Service Installation (In-ground)
Site QA | Stage 15
Site QA | Stage 15 |  | Plumbing Services Rough-in | Waste & Vent Installation
Site QA | Stage 15 |  |  | Water Service Installation (Rough-ins)
Site QA | Stage 15 |  |  | Gas Service Installation (Rough-ins)
Site QA | Stage 15
Site QA | Stage 15 |  | Plumbing Services Fit-off | Toilet & Cistern Installation
Site QA | Stage 15 |  |  | Wash Basin & Tapware Installation
Site QA | Stage 15 |  |  | Shower & Tapware Installation
Site QA | Stage 15 |  |  | Bath & Tapware Installation
Site QA | Stage 15 |  |  | Kitchen Sink & Tapware Installation
Site QA | Stage 15 |  |  | Dishwasher Installation
Site QA | Stage 15 |  |  | Laundry Trough & Tapware Installation
Site QA | Stage 15 |  |  | Washing Machine Stops Installation
Site QA | Stage 15 |  |  | Tundish Installation
Site QA | Stage 15 |  |  | Hose Tap Installation
Site QA | Stage 15 |  |  | Gas Appliance Installation
Site QA | Stage 15 |  |  | Hot Water Unit Installation
Site QA | Stage 15
Site QA | Stage 15 |  | Plumbing Services Testing | Testing Drainage Pipework (Hydrostatic Test)
Site QA | Stage 15 |  |  | Testing Water Pipework
Site QA | Stage 15 |  |  | Testing Gas Service
Site QA | Stage 15
Site QA | Stage 15 |  | Plumbing Services Commissioning | Commission Rain Water Pressure Pump Set
Site QA | Stage 15 |  |  | Commission Water Storage Tank
Site QA | Stage 15 |  |  | Commission Hot Water Generating Plant
Site QA | Stage 15 |  |  | Commission Reduced Pressure Zone Device
Site QA | Stage 15 |  |  | Commission Fixture Group
Site QA | Stage 15
Site QA | Stage 15 | Lot 1502 | Repeat above work elements | Repeat above checklist
Site QA | Stage 15 | Lot 1503 | Repeat above work elements | Repeat above checklist
Site QA | Stage 15 | Lot 1504 | Repeat above work elements | Repeat above checklist
Site QA | Stage 15 | Lot 1505 | Repeat above work elements | Repeat above checklist
Site QA | Stage 15 | Lot 1506 | Repeat above work elements | Repeat above checklist
Site QA | Stage 15 | Lot 1507 | Repeat above work elements | Repeat above checklist
Site QA | Stage 15 | Lot 1508 | Repeat above work elements | Repeat above checklist
Site QA | Stage 15 | Lot 1509 | Repeat above work elements | Repeat above checklist
Site QA | Stage 15 | Lot 1510 | Repeat above work elements | Repeat above checklist
Site QA | Stage 15 | Lot 1511 | Repeat above work elements | Repeat above checklist
Site QA | Stage 15 | Lot 1512 | Repeat above work elements | Repeat above checklist
z | z | z |  | z | z | z

## MCL Index
| Type | Name | Values | Prefix | Postfix
1 | checklist | Add New Task | PASS, FAIL, N/A
2 | checklist | Drainage Installation (In-ground) | PASS, FAIL, N/A
3 | checklist | Stack & Vent Installation | PASS, FAIL, N/A
4 | checklist | Waste & Vent Installation | PASS, FAIL, N/A
5 | checklist | Cast-in Waste & Vent | PASS, FAIL, N/A
6 | checklist | Downpipe & Overflow Installation | PASS, FAIL, N/A
7 | checklist | Pump Line Installation | PASS, FAIL, N/A
8 | checklist | Suction Line Installation | PASS, FAIL, N/A
9 | checklist | Authority Main to Meter Installation | PASS, FAIL, N/A
10 | checklist | Water Service Installation (In-ground) | PASS, FAIL, N/A
11 | checklist | Water Service Installation (Mains/Risers) | PASS, FAIL, N/A
12 | checklist | Water Service Installation (Rough-ins) | PASS, FAIL, N/A
13 | checklist | Backflow Prevention Device Installation | PASS, FAIL, N/A
14 | checklist | Water Meter Installation | PASS, FAIL, N/A
15 | checklist | Gas Service Installation (In-ground) | PASS, FAIL, N/A
16 | checklist | Gas Service Installation (Mains/Risers) | PASS, FAIL, N/A
17 | checklist | Gas Service Installation (Rough-ins) | PASS, FAIL, N/A
18 | checklist | Penetration Installation | PASS, FAIL, N/A
19 | checklist | Toilet & Cistern Installation | PASS, FAIL, N/A
20 | checklist | Urinal & Cistern Installation | PASS, FAIL, N/A
21 | checklist | Wash Basin & Tapware Installation | PASS, FAIL, N/A
22 | checklist | Shower & Tapware Installation | PASS, FAIL, N/A
23 | checklist | Bath & Tapware Installation | PASS, FAIL, N/A
24 | checklist | Kitchen Sink & Tapware Installation | PASS, FAIL, N/A
25 | checklist | Dishwasher Installation | PASS, FAIL, N/A
26 | checklist | Laundry Trough & Tapware Installation | PASS, FAIL, N/A
27 | checklist | Washing Machine Stops Installation | PASS, FAIL, N/A
28 | checklist | Tundish Installation | PASS, FAIL, N/A
29 | checklist | Hose Tap Installation | PASS, FAIL, N/A
30 | checklist | Gas Appliance Installation | PASS, FAIL, N/A
31 | checklist | Cleaners Sink & Tapware Installations | PASS, FAIL, N/A
32 | checklist | Hot Water Unit Installation | PASS, FAIL, N/A
33 | checklist | Plant & Equipment Installation | PASS, FAIL, N/A
34 | checklist | Testing Drainage Pipework (Air Test) | PASS, FAIL, N/A
35 | checklist | Testing Drainage Pipework (Hydrostatic Test) | PASS, FAIL, N/A
36 | checklist | Testing Water Pipework | PASS, FAIL, N/A
37 | checklist | Testing Gas Service | PASS, FAIL, N/A
38 | checklist | Commission Drainage Pump Station | PASS, FAIL, N/A
39 | checklist | Commission Water Pressure Pump Set | PASS, FAIL, N/A
40 | checklist | Commission Rain Water Pressure Pump Set | PASS, FAIL, N/A
41 | checklist | Commission Water Storage Tank | PASS, FAIL, N/A
42 | checklist | Commission Hot Water Generating Plant | PASS, FAIL, N/A
43 | checklist | Commission Rain Water Diversion Valve | PASS, FAIL, N/A
44 | checklist | Commission Thermostatic Mixing Valves | PASS, FAIL, N/A
45 | checklist | Commission Reduced Pressure Zone Device | PASS, FAIL, N/A
46 | checklist | Commission Fixture Group | PASS, FAIL, N/A

## Master Checklists
| Type | Haven Pde (Stages 11, 13, 15) |  | Values | Prefix | Postfix
Checklist Resources - Updated 30/01/2024
1 | checklist | Add New Task | 1
1 | checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation. If no variation mark as 'N/A'. You must still proceed with the following checks | 1 | PASS, FAIL, N/A
1 | checkpoint | New task checked off (add brief description of this task) | 1 | PASS, FAIL, N/A
1 |  |  | 1
2 | checklist | Drainage Installation (In-ground) | 1
2 | checkpoint | Mark this checkpoint 'FAIL' if you think this task should be a variation or additional scope of works. If ok mark as 'Pass' | 1 | PASS, FAIL, N/A
2 | checkpoint | Installation complies with current AS/NZS-3500 | 1 | PASS, FAIL, N/A
2 | checkpoint | Installation complies with current drawings & specifications | 1 | PASS, FAIL, N/A
2 | checkpoint | Installation & materials were used, comply with manufacturer requirements | 1 | PASS, FAIL, N/A
2 | checkpoint | Check for damage & leaks | 1 | PASS, FAIL, N/A
2 | checkpoint | Check materials & joining methods | 1 | PASS, FAIL, N/A
2 | checkpoint | Check alignments & levels | 1 | PASS, FAIL, N/A
2 | checkpoint | Check bedding & clearances | 1 | PASS, FAIL, N/A
2 | checkpoint | Check connections to pits, tanks, etc | 1 | PASS, FAIL, N/A
2 | checkpoint | Check covers, venting & conduits to pits, tanks, etc | 1 | PASS, FAIL, N/A
2 | checkpoint | Check pipework & traps are clear of debris | 1 | PASS, FAIL, N/A
2 | checkpoint | Check inspection openings | 1 | PASS, FAIL, N/A
2 | checkpoint | Check open ends are sealed | 1 | PASS, FAIL, N/A
2 | checkpoint | If trench is to be left open, make sure pipe can not float | 1 | PASS, FAIL, N/A
2 | checkpoint | Check pipe trench marking tape (if specified) | 1 | PASS, FAIL, N/A
2 | checkpoint | Check trench backfill & compaction | 1 | PASS, FAIL, N/A
2 | checkpoint | Testing by approved method has been complete (must provide test photos) | 1 | PASS, FAIL, N/A
2 |  |  | 1
3 | checklist | Stack & Vent Installation
3 | checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation. If no variation mark as 'N/A'. You must still proceed with the following checks |  | PASS, FAIL, N/A
3 | checkpoint | Installation complies with current AS/NZS-3500 |  | PASS, FAIL, N/A
3 | checkpoint | Installation complies with current drawings & specifications |  | PASS, FAIL, N/A
3 | checkpoint | Installation & materials were used, comply with manufacturer requirements |  | PASS, FAIL, N/A
3 | checkpoint | Check for damage & leaks |  | PASS, FAIL, N/A
3 | checkpoint | Check materials & joining methods |  | PASS, FAIL, N/A
3 | checkpoint | Check alignments & levels |  | PASS, FAIL, N/A
3 | checkpoint | Check clip spacing & pipe separation |  | PASS, FAIL, N/A
3 | checkpoint | Check expansion joints and anchor points |  | PASS, FAIL, N/A
3 | checkpoint | Check inspection openings |  | PASS, FAIL, N/A
3 | checkpoint | Check pipework is clear of debris |  | PASS, FAIL, N/A
3 | checkpoint | Check open ends are sealed |  | PASS, FAIL, N/A
3 | checkpoint | Check acoustic insulation (if specified) |  | PASS, FAIL, N/A
3 | checkpoint | Check pipe labelling |  | PASS, FAIL, N/A
3 | checkpoint | Check floor/wall penetration fire proofing |  | PASS, FAIL, N/A
3 | checkpoint | Check roof vent pipes weather proofing is complete |  | PASS, FAIL, N/A
3 | checkpoint | Testing by approved method has been complete (must provide test photos) |  | PASS, FAIL, N/A
3
4 | checklist | Waste & Vent Installation | 1
4 | checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation. If no variation mark as 'N/A'. You must still proceed with the following checks | 1 | PASS, FAIL, N/A
4 | checkpoint | Installation complies with current AS/NZS-3500 | 1 | PASS, FAIL, N/A
4 | checkpoint | Installation complies with current drawings & specifications | 1 | PASS, FAIL, N/A
4 | checkpoint | Installation & materials were used, comply with manufacturer requirements | 1 | PASS, FAIL, N/A
4 | checkpoint | Check for damage & leaks | 1 | PASS, FAIL, N/A
4 | checkpoint | Check materials & joining methods | 1 | PASS, FAIL, N/A
4 | checkpoint | Check alignments & levels | 1 | PASS, FAIL, N/A
4 | checkpoint | Check clip spacing & pipe separation | 1 | PASS, FAIL, N/A
4 | checkpoint | Check expansion joints and anchor points | 1 | PASS, FAIL, N/A
4 | checkpoint | Check in-wall fixture mounting brackets | 1 | PASS, FAIL, N/A
4 | checkpoint | Check in-wall waste pipes & vents | 1 | PASS, FAIL, N/A
4 | checkpoint | Check inspection openings | 1 | PASS, FAIL, N/A
4 | checkpoint | Check pipework & traps are clear of debris | 1 | PASS, FAIL, N/A
4 | checkpoint | Check open ends are sealed | 1 | PASS, FAIL, N/A
4 | checkpoint | Check acoustic insulation (if specified) | 1 | PASS, FAIL, N/A
4 | checkpoint | Check pipe labelling | 1 | PASS, FAIL, N/A
4 | checkpoint | Check floor/wall penetration fire proofing | 1 | PASS, FAIL, N/A
4 | checkpoint | Check roof vent pipes weather proofing is complete | 1 | PASS, FAIL, N/A
4 | checkpoint | Testing by approved method has been complete (must provide test photos) | 1 | PASS, FAIL, N/A
4 |  |  | 1
5 | checklist | Cast-in Waste & Vent
5 | checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation. If no variation mark as 'N/A'. You must still proceed with the following checks |  | PASS, FAIL, N/A
5 | checkpoint | Installation complies with current AS/NZS-3500 |  | PASS, FAIL, N/A
5 | checkpoint | Installation complies with current drawings & specifications |  | PASS, FAIL, N/A
5 | checkpoint | Installation & materials were used, comply with manufacturer requirements |  | PASS, FAIL, N/A
5 | checkpoint | Check for damage & leaks |  | PASS, FAIL, N/A
5 | checkpoint | Check materials & joining methods |  | PASS, FAIL, N/A
5 | checkpoint | Check alignments & levels |  | PASS, FAIL, N/A
5 | checkpoint | Check clip spacing & pipe separation |  | PASS, FAIL, N/A
5 | checkpoint | Check pipework & traps are clear of debris |  | PASS, FAIL, N/A
5 | checkpoint | Check open ends are sealed |  | PASS, FAIL, N/A
5 | checkpoint | Testing by approved method has been complete (must provide test photos) |  | PASS, FAIL, N/A
5
6 | checklist | Downpipe & Overflow Installation | 1
6 | checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation. If no variation mark as 'N/A'. You must still proceed with the following checks | 1 | PASS, FAIL, N/A
6 | checkpoint | Installation complies with current AS/NZS-3500 | 1 | PASS, FAIL, N/A
6 | checkpoint | Installation complies with current drawings & specifications | 1 | PASS, FAIL, N/A
6 | checkpoint | Installation & materials were used, comply with manufacturer requirements | 1 | PASS, FAIL, N/A
6 | checkpoint | Check for damage & leaks | 1 | PASS, FAIL, N/A
6 | checkpoint | Check materials & joining methods | 1 | PASS, FAIL, N/A
6 | checkpoint | Check alignments & levels | 1 | PASS, FAIL, N/A
6 | checkpoint | Check clip spacing & pipe separation | 1 | PASS, FAIL, N/A
6 | checkpoint | Check expansion joints and anchor points | 1 | PASS, FAIL, N/A
6 | checkpoint | Check connection to roof & floor outlets | 1 | PASS, FAIL, N/A
6 | checkpoint | Check inspection openings | 1 | PASS, FAIL, N/A
6 | checkpoint | Check pipework is clear of debris | 1 | PASS, FAIL, N/A
6 | checkpoint | Check open ends are sealed | 1 | PASS, FAIL, N/A
6 | checkpoint | Check acoustic insulation (if specified) | 1 | PASS, FAIL, N/A
6 | checkpoint | Check pipe labelling | 1 | PASS, FAIL, N/A
6 | checkpoint | Check floor/wall penetration fire proofing | 1 | PASS, FAIL, N/A
6 | checkpoint | Testing by approved method has been complete (must provide test photos) | 1 | PASS, FAIL, N/A
6 |  |  | 1
7 | checklist | Pump Line Installation | 1
7 | checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation. If no variation mark as 'N/A'. You must still proceed with the following checks | 1 | PASS, FAIL, N/A
7 | checkpoint | Installation complies with current AS/NZS-3500 | 1 | PASS, FAIL, N/A
7 | checkpoint | Installation complies with current drawings & specifications | 1 | PASS, FAIL, N/A
7 | checkpoint | Installation & materials were used, comply with manufacturer requirements | 1 | PASS, FAIL, N/A
7 | checkpoint | Check for damage & leaks | 1 | PASS, FAIL, N/A
7 | checkpoint | Check materials & joining methods | 1 | PASS, FAIL, N/A
7 | checkpoint | Check alignments & levels | 1 | PASS, FAIL, N/A
7 | checkpoint | Check clip spacing & pipe separation | 1 | PASS, FAIL, N/A
7 | checkpoint | Check pipework is clear of debris | 1 | PASS, FAIL, N/A
7 | checkpoint | Check open ends are sealed | 1 | PASS, FAIL, N/A
7 | checkpoint | Check pipe labelling | 1 | PASS, FAIL, N/A
7 | checkpoint | Check floor/wall penetration fire proofing | 1 | PASS, FAIL, N/A
7 | checkpoint | Testing by approved method has been complete (must provide test photos) | 1 | PASS, FAIL, N/A
7 |  |  | 1
8 | checklist | Suction Line Installation
8 | checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation. If no variation mark as 'N/A'. You must still proceed with the following checks |  | PASS, FAIL, N/A
8 | checkpoint | Installation complies with current AS/NZS-3500 |  | PASS, FAIL, N/A
8 | checkpoint | Installation complies with current drawings & specifications |  | PASS, FAIL, N/A
8 | checkpoint | Installation & materials were used, comply with manufacturer requirements |  | PASS, FAIL, N/A
8 | checkpoint | Check for damage & leaks |  | PASS, FAIL, N/A
8 | checkpoint | Check materials & joining methods |  | PASS, FAIL, N/A
8 | checkpoint | Check alignments & levels |  | PASS, FAIL, N/A
8 | checkpoint | Check clip spacing & pipe separation |  | PASS, FAIL, N/A
8 | checkpoint | Check pipework is clear of debris |  | PASS, FAIL, N/A
8 | checkpoint | Check open ends are sealed |  | PASS, FAIL, N/A
8 | checkpoint | Check pipe labelling |  | PASS, FAIL, N/A
8 | checkpoint | Check floor/wall penetration fire proofing |  | PASS, FAIL, N/A
8 | checkpoint | Testing by approved method has been complete (must provide test photos) |  | PASS, FAIL, N/A
8
9 | checklist | Authority Main to Meter Installation | 1
9 | checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation. If no variation mark as 'N/A'. You must still proceed with the following checks | 1 | PASS, FAIL, N/A
9 | checkpoint | Installation complies with current AS/NZS-3500 | 1 | PASS, FAIL, N/A
9 | checkpoint | Installation complies with current drawings & specifications | 1 | PASS, FAIL, N/A
9 | checkpoint | Installation & materials were used, comply with manufacturer requirements | 1 | PASS, FAIL, N/A
9 | checkpoint | Check for damage & leaks | 1 | PASS, FAIL, N/A
9 | checkpoint | Check materials & joining methods | 1 | PASS, FAIL, N/A
9 | checkpoint | Check alignments & levels | 1 | PASS, FAIL, N/A
9 | checkpoint | Check bedding & clearances | 1 | PASS, FAIL, N/A
9 | checkpoint | Check valve connections | 1 | PASS, FAIL, N/A
9 | checkpoint | Check pipework is clear of debris | 1 | PASS, FAIL, N/A
9 | checkpoint | Check pipe trench marking tape (if specified) | 1 | PASS, FAIL, N/A
9 | checkpoint | Check trench backfill & compaction | 1 | PASS, FAIL, N/A
9 | checkpoint | Check water meter assemblies | 1 | PASS, FAIL, N/A
9 | checkpoint | Check RPZD assemblies | 1 | PASS, FAIL, N/A
9 | checkpoint | Check pipe labelling | 1 | PASS, FAIL, N/A
9 | checkpoint | Testing by approved method has been complete (must provide test photos) | 1 | PASS, FAIL, N/A
9 |  |  | 1
10 | checklist | Water Service Installation (In-ground) | 1
10 | checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation. If no variation mark as 'N/A'. You must still proceed with the following checks | 1 | PASS, FAIL, N/A
10 | checkpoint | Installation complies with current AS/NZS-3500 | 1 | PASS, FAIL, N/A
10 | checkpoint | Installation complies with current drawings & specifications | 1 | PASS, FAIL, N/A
10 | checkpoint | Installation & materials were used, comply with manufacturer requirements | 1 | PASS, FAIL, N/A
10 | checkpoint | Check for damage & leaks | 1 | PASS, FAIL, N/A
10 | checkpoint | Check materials & joining methods | 1 | PASS, FAIL, N/A
10 | checkpoint | Check alignments & levels | 1 | PASS, FAIL, N/A
10 | checkpoint | Check bedding & clearances | 1 | PASS, FAIL, N/A
10 | checkpoint | Check valve connections | 1 | PASS, FAIL, N/A
10 | checkpoint | Check pipework is clear of debris | 1 | PASS, FAIL, N/A
10 | checkpoint | Check open ends are sealed | 1 | PASS, FAIL, N/A
10 | checkpoint | Check pipe colour coding | 1 | PASS, FAIL, N/A
10 | checkpoint | Check pipe trench marking tape (if specified) | 1 | PASS, FAIL, N/A
10 | checkpoint | If trench is to be left open, make sure pipe can not float | 1 | PASS, FAIL, N/A
10 | checkpoint | Check trench backfill & compaction | 1 | PASS, FAIL, N/A
10 | checkpoint | Testing by approved method has been complete (must provide test photos) | 1 | PASS, FAIL, N/A
10 |  |  | 1
11 | checklist | Water Service Installation (Mains/Risers)
11 | checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation. If no variation mark as 'N/A'. You must still proceed with the following checks |  | PASS, FAIL, N/A
11 | checkpoint | Installation complies with current AS/NZS-3500 |  | PASS, FAIL, N/A
11 | checkpoint | Installation complies with current drawings & specifications |  | PASS, FAIL, N/A
11 | checkpoint | Installation & materials were used, comply with manufacturer requirements |  | PASS, FAIL, N/A
11 | checkpoint | Check for damage & leaks |  | PASS, FAIL, N/A
11 | checkpoint | Check crimp fittings |  | PASS, FAIL, N/A
11 | checkpoint | Check materials & joining methods |  | PASS, FAIL, N/A
11 | checkpoint | Check alignments & levels |  | PASS, FAIL, N/A
11 | checkpoint | Check clip spacing & pipe separation |  | PASS, FAIL, N/A
11 | checkpoint | Check expansion joints and anchor points |  | PASS, FAIL, N/A
11 | checkpoint | Check valves & meter assemblies |  | PASS, FAIL, N/A
11 | checkpoint | Check valves & meter assemblies fixings & brackets |  | PASS, FAIL, N/A
11 | checkpoint | Check hot water pipe clips & thermal insulation (if specified) |  | PASS, FAIL, N/A
11 | checkpoint | Check pipework is clear of debris |  | PASS, FAIL, N/A
11 | checkpoint | Check for cross connections |  | PASS, FAIL, N/A
11 | checkpoint | Check open ends are sealed |  | PASS, FAIL, N/A
11 | checkpoint | Check pipe labelling |  | PASS, FAIL, N/A
11 | checkpoint | Check pipe colour coding |  | PASS, FAIL, N/A
11 | checkpoint | Check floor/wall penetration fire proofing |  | PASS, FAIL, N/A
11 | checkpoint | Testing by approved method has been complete (must provide test photos) |  | PASS, FAIL, N/A
11
12 | checklist | Water Service Installation (Rough-ins) | 1
12 | checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation. If no variation mark as 'N/A'. You must still proceed with the following checks | 1 | PASS, FAIL, N/A
12 | checkpoint | Installation complies with current AS/NZS-3500 | 1 | PASS, FAIL, N/A
12 | checkpoint | Installation complies with current drawings & specifications | 1 | PASS, FAIL, N/A
12 | checkpoint | Installation & materials were used, comply with manufacturer requirements | 1 | PASS, FAIL, N/A
12 | checkpoint | Check for damage & leaks | 1 | PASS, FAIL, N/A
12 | checkpoint | Check crimp fittings | 1 | PASS, FAIL, N/A
12 | checkpoint | Check for cross connections | 1 | PASS, FAIL, N/A
12 | checkpoint | Check alignment & levels | 1 | PASS, FAIL, N/A
12 | checkpoint | Check materials & joining methods | 1 | PASS, FAIL, N/A
12 | checkpoint | Check clip spacing & pipe separation | 1 | PASS, FAIL, N/A
12 | checkpoint | Check TMV/TV | 1 | PASS, FAIL, N/A
12 | checkpoint | Check mixer bodies & lugged elbows | 1 | PASS, FAIL, N/A
12 | checkpoint | Check in-wall pan & cistern brackets | 1 | PASS, FAIL, N/A
12 | checkpoint | Check noggings for future fixture | 1 | PASS, FAIL, N/A
12 | checkpoint | Check sharp edge pipe protection | 1 | PASS, FAIL, N/A
12 | checkpoint | Check heat trace (if specified) | 1 | PASS, FAIL, N/A
12 | checkpoint | Check hot water pipe clips & thermal insulation (if specified) | 1 | PASS, FAIL, N/A
12 | checkpoint | Check pipe colour coding | 1 | PASS, FAIL, N/A
12 | checkpoint | Check floor/wall penetration fire proofing | 1 | PASS, FAIL, N/A
12 | checkpoint | Testing by approved method has been complete (must provide test photos) | 1 | PASS, FAIL, N/A
12 |  |  | 1
13 | checklist | Backflow Prevention Device Installation
13 | checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation. If no variation mark as 'N/A'. You must still proceed with the following checks |  | PASS, FAIL, N/A
13 | checkpoint | Installation complies with current AS/NZS-3500 |  | PASS, FAIL, N/A
13 | checkpoint | Installation complies with current drawings & specifications |  | PASS, FAIL, N/A
13 | checkpoint | Installation & materials were used, comply with manufacturer requirements |  | PASS, FAIL, N/A
13 | checkpoint | Check for damage & leaks |  | PASS, FAIL, N/A
13 | checkpoint | Check materials & joining methods |  | PASS, FAIL, N/A
13 | checkpoint | Check alignments & levels |  | PASS, FAIL, N/A
13 | checkpoint | Check clip spacing & pipe separation |  | PASS, FAIL, N/A
13 | checkpoint | Check pressure relief pipe to tundish |  | PASS, FAIL, N/A
13
14 | checklist | Water Meter Installation | 1
14 | checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation. If no variation mark as 'N/A'. You must still proceed with the following checks | 1 | PASS, FAIL, N/A
14 | text | Meter Type: | 1 | PASS, FAIL, N/A
14 | text | Meter Number: | 1 | PASS, FAIL, N/A
14 | text | Meter Location: | 1 | PASS, FAIL, N/A
14 | text | Meter Size: | 1 | PASS, FAIL, N/A
14 | checkpoint | Installation complies with current AS/NZS-3500 | 1 | PASS, FAIL, N/A
14 | checkpoint | Installation complies with current drawings & specifications | 1 | PASS, FAIL, N/A
14 | checkpoint | Installation & materials were used, comply with manufacturer requirements | 1 | PASS, FAIL, N/A
14 |  |  | 1
15 | checklist | Gas Service Installation (In-ground) | 1
15 | checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation. If no variation mark as 'N/A'. You must still proceed with the following checks | 1 | PASS, FAIL, N/A
15 | checkpoint | Installation complies with current AS/NZS-3500 | 1 | PASS, FAIL, N/A
15 | checkpoint | Installation complies with current drawings & specifications | 1 | PASS, FAIL, N/A
15 | checkpoint | Installation & materials were used, comply with manufacturer requirements | 1 | PASS, FAIL, N/A
15 | checkpoint | Check for damage & leaks | 1 | PASS, FAIL, N/A
15 | checkpoint | Check materials & joining methods | 1 | PASS, FAIL, N/A
15 | checkpoint | Check alignments & levels | 1 | PASS, FAIL, N/A
15 | checkpoint | Check bedding & clearances | 1 | PASS, FAIL, N/A
15 | checkpoint | Check valve connections | 1 | PASS, FAIL, N/A
15 | checkpoint | Check pipework is clear of debris | 1 | PASS, FAIL, N/A
15 | checkpoint | Check open ends are sealed | 1 | PASS, FAIL, N/A
15 | checkpoint | Check pipe colour coding | 1 | PASS, FAIL, N/A
15 | checkpoint | Check pipe trench marking tape (if specified) | 1 | PASS, FAIL, N/A
15 | checkpoint | If trench is to be left open, make sure pipe can not float | 1 | PASS, FAIL, N/A
15 | checkpoint | Check trench backfill & compaction | 1 | PASS, FAIL, N/A
15 | checkpoint | Testing by approved method has been complete (must provide test photos) | 1 | PASS, FAIL, N/A
15 |  |  | 1
16 | checklist | Gas Service Installation (Mains/Risers)
16 | checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation. If no variation mark as 'N/A'. You must still proceed with the following checks |  | PASS, FAIL, N/A
16 | checkpoint | Installation complies with current AS/NZS-3500 |  | PASS, FAIL, N/A
16 | checkpoint | Installation complies with current drawings & specifications |  | PASS, FAIL, N/A
16 | checkpoint | Installation & materials were used, comply with manufacturer requirements |  | PASS, FAIL, N/A
16 | checkpoint | Check for damage & leaks |  | PASS, FAIL, N/A
16 | checkpoint | Check materials & joining methods |  | PASS, FAIL, N/A
16 | checkpoint | Check crimp fittings |  | PASS, FAIL, N/A
16 | checkpoint | Check alignments & levels |  | PASS, FAIL, N/A
16 | checkpoint | Check clip spacing & pipe separation |  | PASS, FAIL, N/A
16 | checkpoint | Check valves & meter assemblies |  | PASS, FAIL, N/A
16 | checkpoint | Check valves & meter assemblies fixings & brackets |  | PASS, FAIL, N/A
16 | checkpoint | Check pipework is clear of debris |  | PASS, FAIL, N/A
16 | checkpoint | Check for cross connections |  | PASS, FAIL, N/A
16 | checkpoint | Check open ends are sealed |  | PASS, FAIL, N/A
16 | checkpoint | Check pipe colour coding |  | PASS, FAIL, N/A
16 | checkpoint | Check pipe labelling |  | PASS, FAIL, N/A
16 | checkpoint | Check floor/wall penetration fire proofing |  | PASS, FAIL, N/A
16 | checkpoint | Testing by approved method has been complete (must provide test photos) |  | PASS, FAIL, N/A
16
17 | checklist | Gas Service Installation (Rough-ins) | 1
17 | checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation. If no variation mark as 'N/A'. You must still proceed with the following checks | 1 | PASS, FAIL, N/A
17 | checkpoint | Installation complies with current AS/NZS-3500 | 1 | PASS, FAIL, N/A
17 | checkpoint | Installation complies with current drawings & specifications | 1 | PASS, FAIL, N/A
17 | checkpoint | Installation & materials were used, comply with manufacturer requirements | 1 | PASS, FAIL, N/A
17 | checkpoint | Check for damage & leaks | 1 | PASS, FAIL, N/A
17 | checkpoint | Check crimp fittings | 1 | PASS, FAIL, N/A
17 | checkpoint | Check for cross connections | 1 | PASS, FAIL, N/A
17 | checkpoint | Check alignment & levels | 1 | PASS, FAIL, N/A
17 | checkpoint | Check materials & joining methods | 1 | PASS, FAIL, N/A
17 | checkpoint | Check clip spacing & pipe separation | 1 | PASS, FAIL, N/A
17 | checkpoint | Check lugged elbows | 1 | PASS, FAIL, N/A
17 | checkpoint | Check noggings for future fixture | 1 | PASS, FAIL, N/A
17 | checkpoint | Check sharp edge pipe protection | 1 | PASS, FAIL, N/A
17 | checkpoint | Check pipe colour coding | 1 | PASS, FAIL, N/A
17 | checkpoint | Check floor/wall penetration fire proofing | 1 | PASS, FAIL, N/A
17 | checkpoint | Testing by approved method has been complete (must provide test photos) | 1 | PASS, FAIL, N/A
17 |  |  | 1
18 | checklist | Penetration Installation
18 | checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation. If no variation mark as 'N/A'. You must still proceed with the following checks |  | PASS, FAIL, N/A
18 | checkpoint | Installation complies with current AS/NZS-3500 |  | PASS, FAIL, N/A
18 | checkpoint | Installation complies with current drawings & specifications |  | PASS, FAIL, N/A
18 | checkpoint | Installation & materials were used, comply with manufacturer requirements |  | PASS, FAIL, N/A
18 | checkpoint | Check for damage & missing penos |  | PASS, FAIL, N/A
18 | checkpoint | Check penetration sizes, locations & finished levels are corrrect |  | PASS, FAIL, N/A
18 | checkpoint | Check fire collars types & ratings are correct |  | PASS, FAIL, N/A
18 | checkpoint | Check blank sleeves are correct |  | PASS, FAIL, N/A
18 | checkpoint | Check cast-in outlets location & finished levels are correct |  | PASS, FAIL, N/A
18 | checkpoint | Check open ends are sealed |  | PASS, FAIL, N/A
18 | checkpoint | Check photos have been provided |  | PASS, FAIL, N/A
18
19 | checklist | Toilet & Cistern Installation | 1
19 | checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation. If no variation mark as 'N/A'. You must still proceed with the following checks | 1 | PASS, FAIL, N/A
19 | checkpoint | Installation complies with current AS/NZS-3500 | 1 | PASS, FAIL, N/A
19 | checkpoint | Installation complies with current drawings & specifications | 1 | PASS, FAIL, N/A
19 | checkpoint | Installation & materials were used, comply with manufacturer requirements | 1 | PASS, FAIL, N/A
19 | checkpoint | Check for damage or leaks | 1 | PASS, FAIL, N/A
19 | checkpoint | Check level & alignment | 1 | PASS, FAIL, N/A
19 | checkpoint | Check mini stops | 1 | PASS, FAIL, N/A
19 | checkpoint | Check flexible connections are not twisted or kinked | 1 | PASS, FAIL, N/A
19 | checkpoint | Check button assembly is securely fitted | 1 | PASS, FAIL, N/A
19 | checkpoint | Check seat & lid function | 1 | PASS, FAIL, N/A
19 | checkpoint | Check special DDA accessories (if applicable) | 1 | PASS, FAIL, N/A
19 | checkpoint | Check operation, controls & remote sensors | 1 | PASS, FAIL, N/A
19 | checkpoint | Check trap is clear of debris | 1 | PASS, FAIL, N/A
19 | checkpoint | Check caulking | 1 | PASS, FAIL, N/A
19 | checkpoint | Must provide photo | 1 | PASS, FAIL, N/A
19 |  |  | 1
20 | checklist | Urinal & Cistern Installation
20 | checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation. If no variation mark as 'N/A'. You must still proceed with the following checks |  | PASS, FAIL, N/A
20 | checkpoint | Installation complies with current AS/NZS-3500 |  | PASS, FAIL, N/A
20 | checkpoint | Installation complies with current drawings & specifications |  | PASS, FAIL, N/A
20 | checkpoint | Installation & materials were used, comply with manufacturer requirements |  | PASS, FAIL, N/A
20 | checkpoint | Check for damage or leaks |  | PASS, FAIL, N/A
20 | checkpoint | Check level & alignment |  | PASS, FAIL, N/A
20 | checkpoint | Check mini stops |  | PASS, FAIL, N/A
20 | checkpoint | Check flexible connections are not twisted or kinked |  | PASS, FAIL, N/A
20 | checkpoint | Check button assembly |  | PASS, FAIL, N/A
20 | checkpoint | Check operation, controls & remote sensors |  | PASS, FAIL, N/A
20 | checkpoint | Check trap is clear of debris |  | PASS, FAIL, N/A
20 | checkpoint | Check caulking is correct |  | PASS, FAIL, N/A
20 | checkpoint | Must provide photo |  | PASS, FAIL, N/A
20
21 | checklist | Wash Basin & Tapware Installation | 1
21 | checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation. If no variation mark as 'N/A'. You must still proceed with the following checks | 1 | PASS, FAIL, N/A
21 | checkpoint | Installation complies with current AS/NZS-3500 | 1 | PASS, FAIL, N/A
21 | checkpoint | Installation complies with current drawings & specifications | 1 | PASS, FAIL, N/A
21 | checkpoint | Installation & materials were used, comply with manufacturer requirements | 1 | PASS, FAIL, N/A
21 | checkpoint | Check for damage or leaks | 1 | PASS, FAIL, N/A
21 | checkpoint | Check level & alignment | 1 | PASS, FAIL, N/A
21 | checkpoint | Check mini stops | 1 | PASS, FAIL, N/A
21 | checkpoint | Check flexible connections are not twisted or kinked | 1 | PASS, FAIL, N/A
21 | checkpoint | Check special DDA accessories (if applicable) | 1 | PASS, FAIL, N/A
21 | checkpoint | Check waste & trap connections | 1 | PASS, FAIL, N/A
21 | checkpoint | Check operation, controls & remote sensors | 1 | PASS, FAIL, N/A
21 | checkpoint | Check trap is clear of debris | 1 | PASS, FAIL, N/A
21 | checkpoint | Check caulking | 1 | PASS, FAIL, N/A
21 | checkpoint | Must provide photo | 1 | PASS, FAIL, N/A
21 |  |  | 1 | PASS, FAIL, N/A
22 | checklist | Shower & Tapware Installation | 1 | PASS, FAIL, N/A
22 | checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation. If no variation mark as 'N/A'. You must still proceed with the following checks | 1 | PASS, FAIL, N/A
22 | checkpoint | Installation complies with current AS/NZS-3500 | 1 | PASS, FAIL, N/A
22 | checkpoint | Installation complies with current drawings & specifications | 1 | PASS, FAIL, N/A
22 | checkpoint | Installation & materials were used, comply with manufacturer requirements | 1 | PASS, FAIL, N/A
22 | checkpoint | Check for damage or leaks | 1 | PASS, FAIL, N/A
22 | checkpoint | Check level & alignment | 1 | PASS, FAIL, N/A
22 | checkpoint | Check wall plates, mixers & diversion valves | 1 | PASS, FAIL, N/A
22 | checkpoint | Check outlets, wall rails & hand showers | 1 | PASS, FAIL, N/A
22 | checkpoint | Check special DDA accessories (if applicable) | 1 | PASS, FAIL, N/A
22 | checkpoint | Check waste & trap connections | 1 | PASS, FAIL, N/A
22 | checkpoint | Check operation & controls | 1 | PASS, FAIL, N/A
22 | checkpoint | Check floor grate level & alignment | 1 | PASS, FAIL, N/A
22 | checkpoint | Check trap is clear of debris | 1 | PASS, FAIL, N/A
22 | checkpoint | Check caulking | 1 | PASS, FAIL, N/A
22 | checkpoint | Must provide photo | 1 | PASS, FAIL, N/A
22 |  |  | 1
23 | checklist | Bath & Tapware Installation | 1
23 | checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation. If no variation mark as 'N/A'. You must still proceed with the following checks | 1 | PASS, FAIL, N/A
23 | checkpoint | Installation complies with current AS/NZS-3500 | 1 | PASS, FAIL, N/A
23 | checkpoint | Installation complies with current drawings & specifications | 1 | PASS, FAIL, N/A
23 | checkpoint | Installation & materials were used, comply with manufacturer requirements | 1 | PASS, FAIL, N/A
23 | checkpoint | Check for damage or leaks | 1 | PASS, FAIL, N/A
23 | checkpoint | Check level & alignment | 1 | PASS, FAIL, N/A
23 | checkpoint | Check wall plates, mixers & diversion valves | 1 | PASS, FAIL, N/A
23 | checkpoint | Check outlets, wall rails & hand showers | 1 | PASS, FAIL, N/A
23 | checkpoint | Check special DDA accessories (if applicable) | 1 | PASS, FAIL, N/A
23 | checkpoint | Check waste & trap connections | 1 | PASS, FAIL, N/A
23 | checkpoint | Check operation & controls | 1 | PASS, FAIL, N/A
23 | checkpoint | Check floor grate level & alignment | 1 | PASS, FAIL, N/A
23 | checkpoint | Check trap is clear of debris | 1 | PASS, FAIL, N/A
23 | checkpoint | Check caulking | 1 | PASS, FAIL, N/A
23 | checkpoint | Must provide photo | 1 | PASS, FAIL, N/A
23 |  |  | 1
24 | checklist | Kitchen Sink & Tapware Installation | 1
24 | checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation. If no variation mark as 'N/A'. You must still proceed with the following checks | 1 | PASS, FAIL, N/A
24 | checkpoint | Installation complies with current AS/NZS-3500 | 1 | PASS, FAIL, N/A
24 | checkpoint | Installation complies with current drawings & specifications | 1 | PASS, FAIL, N/A
24 | checkpoint | Installation & materials were used, comply with manufacturer requirements | 1 | PASS, FAIL, N/A
24 | checkpoint | Check for damage or leaks | 1 | PASS, FAIL, N/A
24 | checkpoint | Check level & alignment | 1 | PASS, FAIL, N/A
24 | checkpoint | Check mini stops | 1 | PASS, FAIL, N/A
24 | checkpoint | Check flexible connections are not twisted or kinked | 1 | PASS, FAIL, N/A
24 | checkpoint | Check waste & trap connections | 1 | PASS, FAIL, N/A
24 | checkpoint | Check dishwasher waste & water connections | 1 | PASS, FAIL, N/A
24 | checkpoint | Check stop valves for future connections are capped | 1 | PASS, FAIL, N/A
24 | checkpoint | Check operation & controls | 1 | PASS, FAIL, N/A
24 | checkpoint | Check trap is clear of debris | 1 | PASS, FAIL, N/A
24 | checkpoint | Check caulking | 1 | PASS, FAIL, N/A
24 | checkpoint | Must provide photo | 1 | PASS, FAIL, N/A
24 |  |  | 1
25 | checklist | Dishwasher Installation | 1
25 | checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation. If no variation mark as 'N/A'. You must still proceed with the following checks | 1 | PASS, FAIL, N/A
25 | checkpoint | Installation complies with current AS/NZS-3500 | 1 | PASS, FAIL, N/A
25 | checkpoint | Installation complies with current drawings & specifications | 1 | PASS, FAIL, N/A
25 | checkpoint | Installation & materials were used, comply with manufacturer requirements | 1 | PASS, FAIL, N/A
25 | checkpoint | Check for damage or leaks | 1 | PASS, FAIL, N/A
25 | checkpoint | Check level & alignment | 1 | PASS, FAIL, N/A
25 | checkpoint | Check isolation valves & non-return valves | 1 | PASS, FAIL, N/A
25 | checkpoint | Check pressure reduction valve (if specified) | 1 | PASS, FAIL, N/A
25 | checkpoint | Check flexible waste & water hoses are not twisted or kinked | 1 | PASS, FAIL, N/A
25 | checkpoint | Check flexible waste hose height under cabinet | 1 | PASS, FAIL, N/A
25 | checkpoint | Check waste connection to trap | 1 | PASS, FAIL, N/A
25 | checkpoint | Check operation & controls | 1 | PASS, FAIL, N/A
25 | checkpoint | Must provide photo | 1 | PASS, FAIL, N/A
25 |  |  | 1
26 | checklist | Laundry Trough & Tapware Installation | 1
26 | checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation. If no variation mark as 'N/A'. You must still proceed with the following checks | 1 | PASS, FAIL, N/A
26 | checkpoint | Installation complies with current AS/NZS-3500 | 1 | PASS, FAIL, N/A
26 | checkpoint | Installation complies with current drawings & specifications | 1 | PASS, FAIL, N/A
26 | checkpoint | Installation & materials were used, comply with manufacturer requirements | 1 | PASS, FAIL, N/A
26 | checkpoint | Check for damage or leaks | 1 | PASS, FAIL, N/A
26 | checkpoint | Check level & alignment | 1 | PASS, FAIL, N/A
26 | checkpoint | Check mini stops | 1 | PASS, FAIL, N/A
26 | checkpoint | Check flexible connections are not twisted or kinked | 1 | PASS, FAIL, N/A
26 | checkpoint | Check waste & water connections | 1 | PASS, FAIL, N/A
26 | checkpoint | Check stop valves for future connections are capped | 1 | PASS, FAIL, N/A
26 | checkpoint | Check operation & controls | 1 | PASS, FAIL, N/A
26 | checkpoint | Check trap is clear of debris | 1 | PASS, FAIL, N/A
26 | checkpoint | Check caulking | 1 | PASS, FAIL, N/A
26 | checkpoint | Must provide photo | 1 | PASS, FAIL, N/A
26 |  |  | 1
27 | checklist | Washing Machine Stops Installation | 1
27 | checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation. If no variation mark as 'N/A'. You must still proceed with the following checks | 1 | PASS, FAIL, N/A
27 | checkpoint | Installation complies with current AS/NZS-3500 | 1 | PASS, FAIL, N/A
27 | checkpoint | Installation complies with current drawings & specifications | 1 | PASS, FAIL, N/A
27 | checkpoint | Installation & materials were used, comply with manufacturer requirements | 1 | PASS, FAIL, N/A
27 | checkpoint | Check for damage or leaks | 1 | PASS, FAIL, N/A
27 | checkpoint | Check level & alignment | 1 | PASS, FAIL, N/A
27 | checkpoint | Check stops are firmly turned off | 1 | PASS, FAIL, N/A
27 | checkpoint | Check stops hose connections are capped off | 1 | PASS, FAIL, N/A
27 | checkpoint | Must provide photo | 1 | PASS, FAIL, N/A
27 |  |  | 1 | PASS, FAIL, N/A
28 | checklist | Tundish Installation | 1
28 | checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation. If no variation mark as 'N/A'. You must still proceed with the following checks | 1 | PASS, FAIL, N/A
28 | checkpoint | Installation complies with current AS/NZS-3500 | 1 | PASS, FAIL, N/A
28 | checkpoint | Installation complies with current drawings & specifications | 1 | PASS, FAIL, N/A
28 | checkpoint | Installation & materials were used, comply with manufacturer requirements | 1 | PASS, FAIL, N/A
28 | checkpoint | Check for damage or leaks | 1 | PASS, FAIL, N/A
28 | checkpoint | Check level & alignment | 1 | PASS, FAIL, N/A
28 | checkpoint | Check waste & trap connections | 1 | PASS, FAIL, N/A
28 | checkpoint | Check trap is clear of debris | 1 | PASS, FAIL, N/A
28 | checkpoint | Must provide photo | 1 | PASS, FAIL, N/A
28 |  |  | 1
29 | checklist | Hose Tap Installation | 1
29 | checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation. If no variation mark as 'N/A'. You must still proceed with the following checks | 1 | PASS, FAIL, N/A
29 | checkpoint | Installation complies with current AS/NZS-3500 | 1 | PASS, FAIL, N/A
29 | checkpoint | Installation complies with current drawings & specifications | 1 | PASS, FAIL, N/A
29 | checkpoint | Installation & materials were used, comply with manufacturer requirements | 1 | PASS, FAIL, N/A
29 | checkpoint | Check for damage or leaks | 1 | PASS, FAIL, N/A
29 | checkpoint | Vacuum breaker fitted | 1 | PASS, FAIL, N/A
29 | checkpoint | Check pipe colour coding | 1 | PASS, FAIL, N/A
29 | checkpoint | Must provide photo | 1 | PASS, FAIL, N/A
29 |  |  | 1
30 | checklist | Gas Appliance Installation | 1
30 | checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation. If no variation mark as 'N/A'. You must still proceed with the following checks | 1 | PASS, FAIL, N/A
30 | checkpoint | Installation complies with current AS/NZS-3500 | 1 | PASS, FAIL, N/A
30 | checkpoint | Installation complies with current drawings & specifications | 1 | PASS, FAIL, N/A
30 | checkpoint | Installation & materials were used, comply with manufacturer requirements | 1 | PASS, FAIL, N/A
30 | checkpoint | Check for damage or leaks | 1 | PASS, FAIL, N/A
30 | checkpoint | Check level & alignment is correct | 1 | PASS, FAIL, N/A
30 | checkpoint | Check surrounding wall material is fire rated | 1 | PASS, FAIL, N/A
30 | checkpoint | Check distance from cook-top to range hood complies with manufacturer specification | 1 | PASS, FAIL, N/A
30 | checkpoint | Check surrounding walls to closest burner distance complies with manufacturer specification | 1 | PASS, FAIL, N/A
30 | checkpoint | Check flexible connections are not twisted or kinked | 1 | PASS, FAIL, N/A
30 | checkpoint | Check gas isolation valve | 1 | PASS, FAIL, N/A
30 | checkpoint | Check gas pressure regulator | 1 | PASS, FAIL, N/A
30 | checkpoint | Check operation & controls | 1 | PASS, FAIL, N/A
30 | checkpoint | Must provide photo | 1 | PASS, FAIL, N/A
30 |  |  | 1
31 | checklist | Cleaners Sink & Tapware Installations
31 | checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation. If no variation mark as 'N/A'. You must still proceed with the following checks |  | PASS, FAIL, N/A
31 | checkpoint | Installation complies with current AS/NZS-3500 |  | PASS, FAIL, N/A
31 | checkpoint | Installation complies with current drawings & specifications |  | PASS, FAIL, N/A
31 | checkpoint | Installation & materials were used, comply with manufacturer requirements |  | PASS, FAIL, N/A
31 | checkpoint | Check for damage or leaks |  | PASS, FAIL, N/A
31 | checkpoint | Check level & alignment |  | PASS, FAIL, N/A
31 | checkpoint | Check tapware for fit & function |  | PASS, FAIL, N/A
31 | checkpoint | Check wall brackest & fixings |  | PASS, FAIL, N/A
31 | checkpoint | Check bucket grate |  | PASS, FAIL, N/A
31 | checkpoint | Check waste & trap connections |  | PASS, FAIL, N/A
31 | checkpoint | Check trap is clear of debris |  | PASS, FAIL, N/A
31 | checkpoint | Check caulking |  | PASS, FAIL, N/A
31 | checkpoint | Must provide photo |  | PASS, FAIL, N/A
31
32 | checklist | Hot Water Unit Installation | 1
32 | checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation. If no variation mark as 'N/A'. You must still proceed with the following checks | 1 | PASS, FAIL, N/A
32 | checkpoint | Installation complies with current AS/NZS-3500 | 1 | PASS, FAIL, N/A
32 | checkpoint | Installation complies with current drawings & specifications | 1 | PASS, FAIL, N/A
32 | checkpoint | Installation & materials were used, comply with manufacturer requirements | 1 | PASS, FAIL, N/A
32 | checkpoint | Check for damage or leaks | 1 | PASS, FAIL, N/A
32 | checkpoint | Check level & alignment | 1 | PASS, FAIL, N/A
32 | checkpoint | Check safe tray (if specified) | 1 | PASS, FAIL, N/A
32 | checkpoint | Check isolation valves & non-return valves | 1 | PASS, FAIL, N/A
32 | checkpoint | Check pressure reduction valve (if specified) | 1 | PASS, FAIL, N/A
32 | checkpoint | Check flexible connections are not twisted or kinked | 1 | PASS, FAIL, N/A
32 | checkpoint | Check waste & water connections | 1 | PASS, FAIL, N/A
32 | checkpoint | Check operation & controls | 1 | PASS, FAIL, N/A
32 | checkpoint | Check water temperatures are as specified | 1 | PASS, FAIL, N/A
32 | checkpoint | Check electrical power is available | 1 | PASS, FAIL, N/A
32 | checkpoint | Check conecting solar pipework & fittings | 1 | PASS, FAIL, N/A
32 | checkpoint | Check solar pump operation | 1 | PASS, FAIL, N/A
32 | checkpoint | Check solar panels & mounting brackets | 1 | PASS, FAIL, N/A
32 | checkpoint | Must provide photo | 1 | PASS, FAIL, N/A
32 |  |  | 1
33 | checklist | Plant & Equipment Installation
33 | checkpoint | Mark this checkpoint as 'FAIL' if you think this task should be a variation. If no variation mark as 'N/A'. You must still proceed with the following checks |  | PASS, FAIL, N/A
33 | checkpoint | Plant & Equipment Installation checked off as below |  | PASS, FAIL, N/A
33 | checkpoint | Installation complies with current AS/NZS-3500 |  | PASS, FAIL, N/A
33 | checkpoint | Installation complies with current drawings & specifications |  | PASS, FAIL, N/A
33 | checkpoint | Installation & materials were used in accordance with manufacturer requirements |  | PASS, FAIL, N/A
33 | checkpoint | Check for damage & leaks |  | PASS, FAIL, N/A
33 | checkpoint | Check tundishes are correct |  | PASS, FAIL, N/A
33 | checkpoint | Check electrical power is available |  | PASS, FAIL, N/A
33 | checkpoint | Check BMS is available |  | PASS, FAIL, N/A
33 | checkpoint | Must provide photo |  | PASS, FAIL, N/A
33
34 | checklist | Testing Drainage Pipework (Air Test)
34 | checkpoint | Installation complies with current AS/NZS-3500 |  | PASS, FAIL, N/A
34 | checkpoint | Installation complies with current drawings & specifications |  | PASS, FAIL, N/A
34 | checkpoint | Installation & materials were used, comply with manufacturer requirements |  | PASS, FAIL, N/A
34 | checkpoint | Check installation is clean and ready for testing |  | PASS, FAIL, N/A
34 | checkpoint | Apply air test as per AS/NZS-3500 |  | PASS, FAIL, N/A
34 | checkpoint | Must provide test start & finish photos |  | PASS, FAIL, N/A
34
35 | checklist | Testing Drainage Pipework (Hydrostatic Test) | 1
35 | checkpoint | Installation complies with current AS/NZS-3500 | 1 | PASS, FAIL, N/A
35 | checkpoint | Installation complies with current drawings & specifications | 1 | PASS, FAIL, N/A
35 | checkpoint | Installation & materials were used, comply with manufacturer requirements | 1 | PASS, FAIL, N/A
35 | checkpoint | Check installation is clean and ready for testing | 1 | PASS, FAIL, N/A
35 | checkpoint | Apply water test as per AS/NZS-3500 | 1 | PASS, FAIL, N/A
35 | checkpoint | Must provide test start & finish photos | 1 | PASS, FAIL, N/A
35 |  |  | 1
36 | checklist | Testing Potable Water Pipework | 1
36 | checkpoint | Installation complies with current AS/NZS-3500 | 1 | PASS, FAIL, N/A
36 | checkpoint | Installation complies with current drawings & specifications | 1 | PASS, FAIL, N/A
36 | checkpoint | Installation & materials were used, comply with manufacturer requirements | 1 | PASS, FAIL, N/A
36 | checkpoint | Check installation is clean and ready for testing | 1 | PASS, FAIL, N/A
36 | checkpoint | Apply water test as per AS/NZS-3500 | 1 | PASS, FAIL, N/A
36 | checkpoint | Must provide test start & finish photos | 1 | PASS, FAIL, N/A
36 |  |  | 1
36 | checklist | Testing Recycled Water Pipework | 1
36 | checkpoint | Installation complies with current AS/NZS-3500 | 1 | PASS, FAIL, N/A
36 | checkpoint | Installation complies with current drawings & specifications | 1 | PASS, FAIL, N/A
36 | checkpoint | Installation & materials were used, comply with manufacturer requirements | 1 | PASS, FAIL, N/A
36 | checkpoint | Check installation is clean and ready for testing | 1 | PASS, FAIL, N/A
36 | checkpoint | Apply water test as per AS/NZS-3500 (Provide test process photos) | 1 | PASS, FAIL, N/A
36 | checkpoint | Must provide test start & finish photos | 1 | PASS, FAIL, N/A
36 | checkpoint | R3 certification has taken place (Provide test process photos & attach copy of R3 report) | 1 | PASS, FAIL, N/A
37 |  |  | 1
38 | checklist | Commission Drainage Pump Station
38 | checkpoint | Installation complies with current AS/NZS-3500 |  | PASS, FAIL, N/A
38 | checkpoint | Installation complies with current drawings & specifications |  | PASS, FAIL, N/A
38 | checkpoint | Installation & materials were used, comply with manufacturer requirements |  | PASS, FAIL, N/A
38 | checkpoint | Check lifting rails & chains |  | PASS, FAIL, N/A
38 | checkpoint | Check water level sensor set points |  | PASS, FAIL, N/A
38 | checkpoint | Check pump motor rotation |  | PASS, FAIL, N/A
38 | checkpoint | Check dry pump fault |  | PASS, FAIL, N/A
38 | checkpoint | Check low water level fault |  | PASS, FAIL, N/A
38 | checkpoint | Check high water level fault |  | PASS, FAIL, N/A
38 | checkpoint | Check auto pump roll-over |  | PASS, FAIL, N/A
38 | checkpoint | Check pump package operational set points |  | PASS, FAIL, N/A
38 | checkpoint | Check control panel display & set points |  | PASS, FAIL, N/A
38 | checkpoint | Check fault warning alarms |  | PASS, FAIL, N/A
38 | checkpoint | Check BMS connection as specified |  | PASS, FAIL, N/A
38 | checkpoint | Provide the suppliers commissioning report & all plant documentation to this checkpoint |  | PASS, FAIL, N/A
38 | checkpoint | Must provide photos |  | PASS, FAIL, N/A
38
39 | checklist | Commission Water Pressure Pump Set
39 | checkpoint | Installation complies with current AS/NZS-3500 |  | PASS, FAIL, N/A
39 | checkpoint | Installation complies with current drawings & specifications |  | PASS, FAIL, N/A
39 | checkpoint | Installation & materials were used, comply with manufacturer requirements |  | PASS, FAIL, N/A
39 | checkpoint | Check water supply fault |  | PASS, FAIL, N/A
39 | checkpoint | Check pump motor rotation |  | PASS, FAIL, N/A
39 | checkpoint | Check dry pump fault |  | PASS, FAIL, N/A
39 | checkpoint | Check auto pump roll-over |  | PASS, FAIL, N/A
39 | checkpoint | Check pump package operational set points |  | PASS, FAIL, N/A
39 | checkpoint | Check control panel display & set points |  | PASS, FAIL, N/A
39 | checkpoint | Check fault warning alarms |  | PASS, FAIL, N/A
39 | checkpoint | Check BMS connection as specified |  | PASS, FAIL, N/A
39 | checkpoint | Provide the suppliers commissioning report & all plant documentation to this checkpoint |  | PASS, FAIL, N/A
39 | checkpoint | Must provide photos |  | PASS, FAIL, N/A
39
40 | checklist | Commission Rain Water Pressure Pump Set
40 | checkpoint | Installation complies with current AS/NZS-3500 |  | PASS, FAIL, N/A
40 | checkpoint | Installation complies with current drawings & specifications |  | PASS, FAIL, N/A
40 | checkpoint | Installation & materials were used, comply with manufacturer requirements |  | PASS, FAIL, N/A
40 | checkpoint | Check water supply fault |  | PASS, FAIL, N/A
40 | checkpoint | Check pump motor rotation |  | PASS, FAIL, N/A
40 | checkpoint | Check dry pump fault |  | PASS, FAIL, N/A
40 | checkpoint | Check auto pump roll-over |  | PASS, FAIL, N/A
40 | checkpoint | Check ultra violet lamps |  | PASS, FAIL, N/A
40 | checkpoint | Check filters & backwash |  | PASS, FAIL, N/A
40 | checkpoint | Check back-up water supply |  | PASS, FAIL, N/A
40 | checkpoint | Check pump package operational set points |  | PASS, FAIL, N/A
40 | checkpoint | Check control panel display & set points |  | PASS, FAIL, N/A
40 | checkpoint | Check fault warning alarms |  | PASS, FAIL, N/A
40 | checkpoint | Check BMS connection as specified |  | PASS, FAIL, N/A
40 | checkpoint | Provide the suppliers commissioning report & all plant documentation to this checkpoint |  | PASS, FAIL, N/A
40 | checkpoint | Must provide photos |  | PASS, FAIL, N/A
40
41 | checklist | Commission Water Storage Tank
41 | checkpoint | Installation complies with current AS/NZS-3500 |  | PASS, FAIL, N/A
41 | checkpoint | Installation complies with current drawings & specifications |  | PASS, FAIL, N/A
41 | checkpoint | Installation & materials were used, comply with manufacturer requirements |  | PASS, FAIL, N/A
41 | checkpoint | Check valves are fully open |  | PASS, FAIL, N/A
41 | checkpoint | Check water level sensor set points |  | PASS, FAIL, N/A
41 | checkpoint | Check tank fill valve |  | PASS, FAIL, N/A
41 | checkpoint | Check low level fault |  | PASS, FAIL, N/A
41 | checkpoint | Check high level fault |  | PASS, FAIL, N/A
41 | checkpoint | Check passive over-flow |  | PASS, FAIL, N/A
41 | checkpoint | Check statutory warning signage |  | PASS, FAIL, N/A
41 | checkpoint | Check control panel display & set points |  | PASS, FAIL, N/A
41 | checkpoint | Check BMS connection as specified |  | PASS, FAIL, N/A
41 | checkpoint | Provide the suppliers commissioning report & all plant documentation to this checkpoint |  | PASS, FAIL, N/A
41 | checkpoint | Must provide photos |  | PASS, FAIL, N/A
41
42 | checklist | Commission Hot Water Generating Plant
42 | checkpoint | Installation complies with current AS/NZS-3500 & AS/NZS-5600 |  | PASS, FAIL, N/A
42 | checkpoint | Installation complies with current drawings & specifications |  | PASS, FAIL, N/A
42 | checkpoint | Installation & materials were used, comply with manufacturer requirements |  | PASS, FAIL, N/A
42 | checkpoint | Check valves are fully open |  | PASS, FAIL, N/A
42 | checkpoint | Check water filters are clean |  | PASS, FAIL, N/A
42 | checkpoint | Check gas supply |  | PASS, FAIL, N/A
42 | checkpoint | Check circulating pumps |  | PASS, FAIL, N/A
42 | checkpoint | Check flue operation |  | PASS, FAIL, N/A
42 | checkpoint | Check system auto start |  | PASS, FAIL, N/A
42 | checkpoint | Check flow & return temperatures |  | PASS, FAIL, N/A
42 | checkpoint | Check control panel display & set points |  | PASS, FAIL, N/A
42 | checkpoint | Check BMS connection as specified |  | PASS, FAIL, N/A
42 | checkpoint | Provide the suppliers commissioning report & all plant documentation to this checkpoint |  | PASS, FAIL, N/A
42 | checkpoint | Must provide photos |  | PASS, FAIL, N/A
42
43 | checklist | Commission Rain Water Diversion Valve
43 | checkpoint | Installation complies with current AS/NZS-3500 |  | PASS, FAIL, N/A
43 | checkpoint | Installation complies with current drawings & specifications |  | PASS, FAIL, N/A
43 | checkpoint | Installation & materials were used, comply with manufacturer requirements |  | PASS, FAIL, N/A
43 | checkpoint | Check valve operation |  | PASS, FAIL, N/A
43 | checkpoint | Check valve defaults to storm-water if no power or tank full |  | PASS, FAIL, N/A
43 | checkpoint | Check control panel display & set points |  | PASS, FAIL, N/A
43 | checkpoint | Check BMS connection as specified |  | PASS, FAIL, N/A
43 | checkpoint | Provide the suppliers commissioning report & all plant documentation to this checkpoint |  | PASS, FAIL, N/A
43 | checkpoint | Must provide photos |  | PASS, FAIL, N/A
43
44 | checklist | Commission Thermostatic Mixing Valves
44 | checkpoint | Installation complies with current AS/NZS-3500 |  | PASS, FAIL, N/A
44 | checkpoint | Installation complies with current drawings & specifications |  | PASS, FAIL, N/A
44 | checkpoint | Installation & materials were used, comply with manufacturer requirements |  | PASS, FAIL, N/A
44 | checkpoint | Check water temperature does not exceed 45°C (Provide photo) |  | PASS, FAIL, N/A
44 | checkpoint | Must provide photos |  | PASS, FAIL, N/A
44
45 | checklist | Commission Reduced Pressure Zone Device | 1
45 | checkpoint | Installation complies with current AS/NZS-3500 | 1 | PASS, FAIL, N/A
45 | checkpoint | Installation complies with current drawings & specifications | 1 | PASS, FAIL, N/A
45 | checkpoint | Installation & materials were used, comply with manufacturer requirements | 1 | PASS, FAIL, N/A
45 | checkpoint | Commissioning by certified persons only | 1 | PASS, FAIL, N/A
45 | checkpoint | Check valves are fully open | 1 | PASS, FAIL, N/A
45 | checkpoint | Check inlet water pressure does not exceed manufacturer specification | 1 | PASS, FAIL, N/A
45 | checkpoint | Check outlet water pressure is as per manufacturer specification | 1 | PASS, FAIL, N/A
45 | checkpoint | Check exhaust tundish drain sized to accept a full flush | 1 | PASS, FAIL, N/A
45 | checkpoint | Provide the commissioning report & all plant documentation to this checkpoint | 1 | PASS, FAIL, N/A
45 | checkpoint | Must provide photos | 1 | PASS, FAIL, N/A
45 |  |  | 1
46 | checklist | Commission Fixture Group
46 | checkpoint | Installation complies with current AS/NZS-3500 or AS/NZS-5600 |  | PASS, FAIL, N/A
46 | checkpoint | Installation complies with current drawings & specifications |  | PASS, FAIL, N/A
46 | checkpoint | Installation & materials were used, comply with manufacturer requirements |  | PASS, FAIL, N/A
46 | checkpoint | Check for any damage, leaks or missing components |  | PASS, FAIL, N/A
46 | checkpoint | Check level & alignment of all fixtures |  | PASS, FAIL, N/A
46 | checkpoint | Check all fixtures, seats & covers are securely fastened |  | PASS, FAIL, N/A
46 | checkpoint | Check all valves are fully open |  | PASS, FAIL, N/A
46 | checkpoint | Check all flexible connections are not twisted or kinked |  | PASS, FAIL, N/A
46 | checkpoint | Check for water for cross connections |  | PASS, FAIL, N/A
46 | checkpoint | Check fixture wastes & connections |  | PASS, FAIL, N/A
46 | checkpoint | Check pipework & all traps are clear of debris |  | PASS, FAIL, N/A
46 | checkpoint | Check AAV is installed to correct height |  | PASS, FAIL, N/A
46 | checkpoint | Check future connection water valves are securely capped |  | PASS, FAIL, N/A
46 | checkpoint | Check TV do not exceed 50°C |  | PASS, FAIL, N/A
46 | checkpoint | Check TMV do not exceed 45°C |  | PASS, FAIL, N/A
46 | checkpoint | Check dishwasher function |  | PASS, FAIL, N/A
46 | checkpoint | Check gas valves & regulators |  | PASS, FAIL, N/A
46 | checkpoint | Check all gas burner functions |  | PASS, FAIL, N/A
46 | checkpoint | Check balcony hose tap |  | PASS, FAIL, N/A
46 | checkpoint | Check balcony floor grate & downpipe |  | PASS, FAIL, N/A
46 | checkpoint | Check all fixtures & tapware are operating as specified |  | PASS, FAIL, N/A
46 | checkpoint | Confirm area has been left clean |  | PASS, FAIL, N/A
46 | checkpoint | Must provide photos |  | PASS, FAIL, N/A
46
| z | z |  | z | z | z