## matrix
Matrix Name | Dimension | Name | Type / Data Field | Tag 1 | Tag 2
Inground Works
| Scope |  |  | Site QA | Inground Works
Rows
|  | Inground Works | dynamic | Site QA | Inground Works
Columns
|  | Area ready to start work |  | Area ready to start work
|  | Set out correct |  | Set out correct
|  | Correct size installed |  | Correct size installed
|  | Magslab installed for MD Ducts/Conduits, 75mm above |  | Magslab installed for MD Ducts / Conduits, 75mm above
|  | Warning Tape installed at half the depth of cover |  | Warning Tape installed at half the depth of cover
|  | Start & finish locations correct as per plan |  | Start and finish locations correct as per plan
|  | Separation from other services |  | separation from other services
|  | Clean inside & in good condition |  | Clean inside and in good condition
|  | Draw Wires Installed |  | Draw Wires Installed
|  | Duct entry holes sealed/water proofed |  | Duct entry holes sealed / water proofed
|  | Pits installed to correct height & level |  | Pits installed to correct height and level
|  | Photos |  | Photos
Cable Tray
| Scope |  |  | Site QA | Cable Tray
Rows
|  | Basement 2 | dynamic | Site QA | Cable Tray | Basement 2
|  | Basement 1 | dynamic | Site QA | Cable Tray | Basement 1
|  | Level 1-5 | grouping | Level 1-5
|  | Level 1 |  | Site QA | Cable Tray | Level 1
|  | Level 2 |  | Site QA | Cable Tray | Level 2
|  | Level 3 |  | Site QA | Cable Tray | Level 3
|  | Level 4 |  | Site QA | Cable Tray | Level 4
|  | Level 5 |  | Site QA | Cable Tray | Level 5
Columns
|  | Area ready to start work |  | Area ready to start work
|  | Unistrutt Filed & Painted |  | Unistrutt Filed & Painted
|  | Hangers Spaced as Specified |  | Hangers Spaced as Specified
|  | Correct Size Tray Installed |  | Correct Size Tray Installed
|  | Tray Joined Correctly |  | Tray Joined Correctly
|  | Hangers Seismically Restrained as per Design |  | Hangers Seismically Restrained as per Design
|  | Tray Fastened to Hangers |  | Tray Fastened to Hangers
|  | Correct Anchors used fixing to Ceiling |  | Correct Anchors used fixing to Ceiling
|  | Cable Tray Bonded |  | Cable Tray Bonded
|  | Photos |  | Photos
Switchboards
| Scope |  |  | Site QA | Switchboards
Rows
|  | Landlord | dynamic | Site QA | Switchboards | Landlord
|  | Commercial | dynamic | Site QA | Switchboards | Commercial
|  | Apartments | dynamic | Site QA | Switchboards | Apartments
Columns
|  | Area ready to start work |  | Area ready to start work
|  | Spatial certificate signed if required |  | Spatial certificate signed if required
|  | Fixings installed in wall correctly if board is wall mounted |  | Fixings installed in wall correctly if board is wall mounted
|  | All clearances sighted to ensure location is compliant |  | All clearances sighted to ensure location is compliant
|  | All cables correctly installed in protection device & earth & neutral bars & fully secured |  | All cables correctly installed in protection device and earth and neutral bars and fully secured
|  | Cables neatly dressed |  | Cables neatly dressed
|  | Phase tabs on chassy covered |  | Phase tabs on chassy covered
|  | All earths & neutrals labelled to match phase numbers |  | All earths and neutrals labelled to match phase numbers
|  | Switchboard is clean on the inside & outside |  | Switchboard is clean on the inside and outside
|  | Masking blanks installed |  | Masking blanks installed
|  | DB legend installed |  | DB legend installed
|  | Feisst label on the door installed |  | Feisst label on the door installed
|  | Photos |  | Photos
Mains Submains
| Scope |  |  | Site QA | Mains Submains
Rows
|  | Landlord | dynamic | Site QA | Mains Submains | Landlord
|  | Commercial | dynamic | Site QA | Mains Submains | Commercial
|  | Apartments | dynamic | Site QA | Mains Submains | Apartments
Columns
|  | Area ready to start work |  | Area ready to start work
|  | Correct Size & Type Installed |  | Correct Size and Type Installed
|  | Type & Size | Type & Size | Details
|  | Cable Clearly Labelled/Marked on both ends |  | Cable Clearly Labelled / Marked on both ends
|  | Trefoil Formation maintained throughout length of run & cables fixed in place with cleats |  | Trefoil Formation maintained throughout length of run and cables fixed in place with cleats
|  | Photos |  | Photos
First Fix
| Scope |  |  | Site QA | First Fix
Rows
|  | Basement 2 | dynamic | Site QA | First Fix | Basement 2
|  | Basement 1 | dynamic | Site QA | First Fix | Basement 1
|  | Level 1 | dynamic | Site QA | First Fix | Level 1
|  | Level 2 | dynamic | Site QA | First Fix | Level 2
|  | Level 3 | dynamic | Site QA | First Fix | Level 3
|  | Level 4 | grouping | Level 4
|  | Hallway |  | Site QA | First Fix | Level 4 | Hallway
|  | Stair 1 |  | Site QA | First Fix | Level 4 | Stair 1
|  | Service Cupboards |  | Site QA | First Fix | Level 4 | Service Cupboards
|  | Level 4 - Apartment 401 | dynamic | Site QA | First Fix | Level 4 | Apartment 401
|  | Level 4 - Apartment 402 | dynamic | Site QA | First Fix | Level 4 | Apartment 402
|  | Level 4 - Apartment 403 | dynamic | Site QA | First Fix | Level 4 | Apartment 403
|  | Level 5 | grouping | Level 5
|  | Hallway |  | Site QA | First Fix | Level 5 | Hallway
|  | Stair 1 |  | Site QA | First Fix | Level 5 | Stair 1
|  | Service Cupboards |  | Site QA | First Fix | Level 5 | Service Cupboards
|  | Level 5 - Apartment 501 | dynamic | Site QA | First Fix | Level 5 | Apartment 501
|  | Level 5 - Apartment 502 | dynamic | Site QA | First Fix | Level 5 | Apartment 502
|  | Level 5 - Apartment 503 | dynamic | Site QA | First Fix | Level 5 | Apartment 503
|  | Level 6 | grouping | Level 6
|  | Apartment 601 Balcony |  | Site QA | First Fix | Level 6 | Apartment 601 Balcony
Columns
|  | Area ready to start work |  | Area ready to start work | QA - First Fix
|  | Flushboxes - Height as per plan |  | Height as per plan | Flushboxes
|  | Flushboxes - Location as per plan |  | Location as per plan | Flushboxes
|  | Flushboxes - Fire rated boxes installed where necessary |  | Fire rated boxes installed where necessary | Flushboxes
|  | Flushboxes - Acoustic boxes installed where necessary |  | Acoustic boxes installed where necessary | Flushboxes
|  | Flushboxes - Flushboxes not back to back on Acoustic/Fire Walls |  | Flushboxes not back to back on Acoustic / Fire Walls | Flushboxes
|  | Flushboxes - Intumescent Pad in Place |  | Intumescent Pad in Place | Flushboxes
|  | Cat Wires - 300mm Seperation Between Power & Data |  | 300mm Seperation Between Power & Data | Cat Wires
|  | Cat Wires - Supported every 6 Meters or Adequately to avoid Sagging |  | Supported every 6 Meters or Adequately to avoid Sagging | Cat Wires
|  | Cat Wires - Correctly Secured at Each End |  | Correctly Secured at Each End | Cat Wires
|  | Cat Wires - Turn Buckle Installed & Accessible |  | Turn Buckle Installed and Accessible | Cat Wires
|  | Cat Wires - Number of cables per cat wire. 8 maximum or as per electrical spec |  | Number of cables per cat wire. 8 maximum or as per electrical spec | Cat Wires
|  | Cat Wires - Separation between other services maintained |  | Separation between other services maintained | Cat Wires
|  | Cat Wires - All cables secured via cable ties with ends cut |  | All cables secured via cable ties with ends cut | Cat Wires
|  | Cabling - Power cables installed correctly incl. correct type & size |  | Power cables installed correctly incl. correct type & size | Cabling
|  | Cabling - Lighting cables installed correctly incl. correct type & size |  | Lighting cables installed correctly incl. correct type & size | Cabling
|  | Cabling - Type & Size | Type & Size | Details | Cabling
|  | Cabling - Switching/Control cables installed correctly |  | Switching / Control cables installed correctly | Cabling
|  | Cabling - Circuits clearly labelled |  | Circuits clearly labelled | Cabling
|  | Cabling - Separation between Data & Power at 300mm or as specified |  | Separation between Data and Power at 300mm or as specified | Cabling
|  | Cable Tray - Minimum 25% spare capacity left on cable tray |  | Minimum 25% spare capacity left on cable tray | Cable Tray
|  | QA - Lights - Setout Correct |  | Setout Correct | QA - Lights
|  | QA - Lights - General Lighting Cabling installed & in correct locations |  | General Lighting Cabling installed and in correct locations | QA - Lights
|  | QA - Lights - Dali Cabling installed & in correct locations |  | Dali Cabling installed and in correct locations | QA - Lights
|  | QA - Lights - PIR Sensor Cabling Installed & in correct locations |  | PIR Sensor Cabling Installed and in correct locations | QA - Lights
|  | QA - Lights - Emergency/Exit Lighting Cabling Installed & in correct locations |  | Emergency/ Exit Lighting Cabling Installed and in correct locations | QA - Lights
|  | QA - Lights - Nogging installed for surface mounted fittings if required |  | Nogging installed for surface mounted fittings if required | QA - Lights
|  | Photos |  | Photos | Photos
Second Fix
| Scope |  |  | Site QA | Second Fix
Rows
|  | Basement 2 | dynamic | Site QA | Second Fix | Basement 2
|  | Basement 1 | dynamic | Site QA | Second Fix | Basement 1
|  | Level 1 | dynamic | Site QA | Second Fix | Level 1
|  | Level 2 | dynamic | Site QA | Second Fix | Level 2
|  | Level 3 | dynamic | Site QA | Second Fix | Level 3
|  | Level 4 | grouping | Level 4
|  | Hallway |  | Site QA | Second Fix | Level 4 | Hallway
|  | Stair 1 |  | Site QA | Second Fix | Level 4 | Stair 1
|  | Service Cupboards |  | Site QA | Second Fix | Level 4 | Service Cupboards
|  | Level 4 - Apartment 401 | dynamic | Site QA | Second Fix | Level 4 | Apartment 401
|  | Level 4 - Apartment 402 | dynamic | Site QA | Second Fix | Level 4 | Apartment 402
|  | Level 4 - Apartment 403 | dynamic | Site QA | Second Fix | Level 4 | Apartment 403
|  | Level 5 | grouping | Level 5
|  | Hallway |  | Site QA | Second Fix | Level 5 | Hallway
|  | Stair 1 |  | Site QA | Second Fix | Level 5 | Stair 1
|  | Service Cupboards |  | Site QA | Second Fix | Level 5 | Service Cupboards
|  | Level 5 - Apartment 501 | dynamic | Site QA | Second Fix | Level 5 | Apartment 501
|  | Level 5 - Apartment 502 | dynamic | Site QA | Second Fix | Level 5 | Apartment 502
|  | Level 5 - Apartment 503 | dynamic | Site QA | Second Fix | Level 5 | Apartment 503
|  | Level 6 | grouping | Level 6
|  | Apartment 601 Balcony |  | Site QA | Second Fix | Level 6 | Apartment 601 Balcony
Columns
|  | Area ready to start work |  | Area ready to start work | QA - Second Fix
|  | Power Outlets - Correct type installed |  | Correct type installed | Power Outlets
|  | Power Outlets - Correctly installed with terminations all secured properly |  | Correctly installed with terminations all secured properly | Power Outlets
|  | Power Outlets - Outlet Installed level |  | Outlet Installed level | Power Outlets
|  | Power Outlets - Circuit Tested & results recorded |  | Circuit Tested and results recorded | Power Outlets
|  | Power Outlets - Description Labelled on the outlet face with vivid & with dymo labeller on cover plate & ensure label is level |  | Description Labelled on the outlet face with vivid and with dymo labeller on cover plate and ensure label is level | Power Outlets
|  | Power Outlets - Photos |  | Photos | Power Outlets
|  | Light Switches - Correct type installed |  | Correct type installed | Light Switches
|  | Light Switches - Correctly installed with terminations all secured properly |  | Correctly installed with terminations all secured properly | Light Switches
|  | Light Switches - Light switch Installed level |  | Light switch Installed level | Light Switches
|  | Light Switches - Circuit Tested & results recorded |  | Circuit Tested and results recorded | Light Switches
|  | Light Switches - Description Labelled on the outlet face with vivid & with dymo labeller on cover plate & ensure label is level |  | Description Labelled on the outlet face with vivid and with dymo labeller on cover plate and ensure label is level | Light Switches
|  | Light Switches - Photos |  | Photos | Light Switches
|  | Light Fixtures & PIR Sensors - Correct type installed |  | Correct type installed | Light Fixtures & PIR Sensors
|  | Light Fixtures & PIR Sensors - Correctly installed with terminations all secured properly |  | Correctly installed with terminations all secured properly | Light Fixtures & PIR Sensors
|  | Light Fixtures & PIR Sensors - Tested for operation |  | Tested for operation | Light Fixtures & PIR Sensors
|  | Light Fixtures & PIR Sensors - Seismic Braces Installed as per design |  | Seismic Braces Installed as per design | Light Fixtures & PIR Sensors
|  | Light Fixtures & PIR Sensors - Photos |  | Photos | Light Fixtures & PIR Sensors
Exterior 1st & 2nd Fix
| Scope |  |  | Site QA | Exterior 1st & 2nd Fix
Rows
|  | Exterior 1st & 2nd Fix | dynamic | Site QA | Exterior 1st & 2nd Fix
Columns
|  | Area ready to start work |  | Area ready to start work | QA - First & Second Fix Exterior
|  | Cabling - Lighting cables installed correctly incl. correct type & size |  | Lighting cables installed correctly incl. correct type & size | Cabling
|  | Cabling - Type & Size | Type & Size | Details | Cabling
|  | Cabling - Circuits clearly labelled |  | Circuits clearly labelled | Cabling
|  | Cabling - Photos |  | Photos | Cabling
|  | Light Fittings - Correct Light Fitting type installed |  | Correct Light Fitting type installed | Light Fittings
|  | Light Fittings - Light Fitting is Level |  | Light Fitting is Level | Light Fittings
|  | Light Fittings - Correctly installed with terminations all secured properly |  | Correctly installed with terminations all secured properly | Light Fittings
|  | Light Fittings - Tested for operation |  | Tested for operation | Light Fittings
|  | Light Fittings - Circuit Tested & results recorded |  | Circuit Tested and results recorded | Light Fittings
|  | Light Fittings - Photos |  | Photos | Light Fittings
FEL SM Weekly Site Progress
| Scope |  |  | FEL SM Weekly Site Checklist
Rows
|  | FEL SM Weekly Site Checklist | dynamic | FEL SM Weekly Site Checklist
Columns
|  | Monday |  | Monday
|  | Prestart Meeting with Team |  | Prestart Meeting with Team
|  | Health Check |  | Health Check
|  | Review Tasks for the week |  | Review Tasks for the week
|  | Identify Targets Including Hours |  | Identify Targets Including Hours
|  | Approve hours by 9AM for previous week |  | Approve hours by 9AM for previous week
|  | Sign off Subcontractor Hours & Submit |  | Sign off Subcontractor Hours & Submit
|  | Review SWMS |  | Review SWMS
|  | Site Toolbox Meeting |  | Site Toolbox Meeting
|  | SSSP in Order |  | SSSP in Order
|  | Tuesday |  | Tuesday
|  | Follow up outstanding RFI's with PM |  | Follow up outstanding RFI's with PM
|  | Wednesday |  | Wednesday
|  | Review Roadblocks & Follow Up if still unresolved |  | Review Roadblocks & Follow Up if still unresolved
|  | QAs up to date |  | QAs up to date
|  | Thursday |  | Thursday
|  | Weekly planner filled out for week ahead |  | Weekly planner filled out for week ahead
|  | Roadblocks identified and actioned |  | Roadblocks identified and actioned
|  | Materials organized for week ahead |  | Materials organized for week ahead
|  | Plans printed with any relevant notes added |  | Plans printed with any relevant notes added
|  | Friday |  | Friday
|  | Submit Toolbox minutes to main contractor and FEL office |  | Submit Toolbox minutes to main contractor and FEL office
|  | Job Cards up to date and submitted |  | Job Cards up to date and submitted
|  | Team tasks for week ahead filled out on whiteboard |  | Team tasks for week ahead filled out on whiteboard