## res
type | name | values | prefix | postfix | usage count | user addable | template name | Resource Id
checklist | FIRE HOSE REEL - Inspection & Maintenance Report
section | SIX MONTHLY
checkpoint | CHECK that the hose reel is readily accessible with no obstacles restricting its access. Where a reel is installed in a recess or cabinet, CHECK that the clearances around the hose reel comply with the requirements of AS 2441
checkpoint | Where a location sign is required by AS2441, Check that it is correctly located and visible
checkpoint | CHECK that the operating instructions are legible
checkpoint | CHECK for any damage or corrosion of components that could adversely affect the operation of the hose reel
checkpoint | Check that any hose reel cabinet is accessible, clear of extraneous materials, clearly and correctly marked & in good repair
checkpoint | CHECK that the nozzle is retained in the nozzle interlock
checkpoint | Where fitted, TEST the swing arm to ensure it operates correctly and allows the hose to be run off in its intended direction
checkpoint | With the nozzle closed and stop valve open, TEST that the hose reel can be unwound freely in its intended direction by unwinding at least 5m of the hose
checkpoint | With the nozzle closed, pressurize the reel by opening the stop valve. DETERMINE if there are any leaks from the reels waterway, including glands, nozzle, stop valve, hose or any fittings
label | NOTE: In order to check there is noleakage of water from any part of the reel waterway, it is recommended that the hose be completely unwound off the reel, so that all parts of the waterway can be examined
checkpoint | TEST water to ensure it is able to flow through the reel by opening and closing the nozzle
checkpoint | CHECK that the service tag or label is firmly attached to the hose reel
checkpoint | After completing these actions, the nozzle shall be re-installed in the nozzle interlock and the hose depressurized
section | TWELVE MONTHLY
checkpoint | Complete all 6 monthly service activities listed above
checkpoint | CHECK that the hose reel is securely mounted and the anchor points are tight
checkpoint | CHECK that the hose guide fixed to the hose reel supply pipe is not able to move upwards and cause the hose to jamb
checkpoint | CHECK that all hose fittings and connections are tight
checkpoint | CHECK that the hose reel bearings are not damaged or excessively worn
checkpoint | With the stop valve and nozzle fully opened, MEASURE the water flow rate from the most disadvantaged hose reel
label | Minimum acceptable flow rates
label | (a) 0.33L/s for reels with 19mm hose
label | (b) 0.41L/s for reels with 25mm hose
checkpoint | CHECK hose for kinking, excessive damage or wear, or collapse
checkpoint | CHECK that any foam branch pipe or other equipment is in good repair and maintained in accordance with the manufacturer's instructions
checkpoint | CHECK that the hose reel is appropriate protection for the fire hazard/risk
checkpoint | CHECK that no alterations have been made to the building, which impede access to the hose reel or restrict the running out of the hose, and that the hose can reach the fire hazard/rick in accordance with AS 2441
section | SUMMARY
checkpoint | Inspected By
textbox | Name
date | Date
holdpoint | Signature