## Resources
Rich Type | Id | Warnings | type | name | values | prefix | postfix | Usage Count | User Addable | Template Name | Template Id
checklist-flat |  |  | checklist | Variable Speed Drive |  |  |  |  | Yes | Variable Speed Drive | 00138a1e-8a55-49a6-b552-52101cf42d6f
checkpoint-status |  |  | checkpoint | Installed as per drawing
text | a16979d9-2330-53cb-b07b-6fe7883b0ad2 |  | textbox | Drawing rev
text | aad20c75-25c3-5992-adc7-d2e6cd1752bf |  | textbox | Area/Level/Zone.
text | c7824135-cb52-5ed7-892d-a22f7b7f2967 |  | textbox | System Reference.
checkpoint-status |  |  | checkpoint | Equipment installed in correct location
checkpoint-status |  |  | checkpoint | Is the VSD mounted correctly
checkpoint-status |  |  | checkpoint | Is the VSD size correct
checkpoint-status |  |  | checkpoint | Termination at equipment
checkpoint-status |  |  | checkpoint | Is the cable shielded correctly
checkpoint-status |  |  | checkpoint | Tested operation
checkpoint-status |  |  | checkpoint | Unit labelled
checkpoint-status |  |  | checkpoint | Installation left clean & tidy.
checklist-sectioned |  |  | checklist | Fan Install Checklist |  |  |  |  | Yes | Fan Install Checklist | 43614efd-c78b-4536-ac1a-89178f237601
checkpoint-group |  |  | section | Set Out
checkpoint-status |  |  | checkpoint | Equipment installed in correct location
text | 32943e7e-3b86-5a44-84c5-3842a46bccec |  | textbox | Fan reference
checkpoint-status |  |  | checkpoint | External springs and mounts
checkpoint-group |  |  | section | Fan
checkpoint-status |  |  | checkpoint | Belts, pulleys, guards fitted.
checkpoint-status |  |  | checkpoint | Fan air flow direction.
checkpoint-status |  |  | checkpoint | Internal supports & spring mounts.
checkpoint-status |  |  | checkpoint | Flexible connections.
checkpoint-group |  |  | section | Electrical
checkpoint-status |  |  | checkpoint | Cable trays/ducts/conduits
checkpoint-status |  |  | checkpoint | Wiring
checkpoint-status |  |  | checkpoint | VSD installed (if Applicable)
checkpoint-status |  |  | checkpoint | Termination at equipment.
checkpoint-status |  |  | checkpoint | Tested rotation
checkpoint-group |  |  | section | Controls.
checkpoint-status |  |  | checkpoint | Sensors, controllers & switches fitted?
checkpoint-status |  |  | checkpoint | Wiring/Conduits to devices.
checkpoint-status |  |  | checkpoint | Termination at controllers.
checkpoint-status |  |  | checkpoint | Termination at device.
checkpoint-status |  |  | checkpoint | Point Tested
checklist-flat |  |  | checklist | Pipework Installation |  |  |  |  | Yes | Pipework Installation | 6d4f802b-405b-43bc-b630-040e0166e44a
checkpoint-status |  |  | checkpoint | Installed as per drawing
text | 5d7af0da-fb2b-54fb-af9d-dbd239141b31 |  | textbox | Drawing rev
text | 42fc5cf9-0e70-5d68-858a-670b3be569d6 |  | textbox | Area/Level/Zone.
text | 1199c728-6928-54e7-ad10-27ea1111efd4 |  | textbox | System Reference.
text | 5437304e-c7a4-597a-bbc3-09d306e7bbbe |  | textbox | Position
text | 6ef125f3-cdcc-5f8a-97d9-38fa3996bfc5 |  | textbox | Height
text | bb2e0aaf-9fdb-5ec3-a613-7399c354e703 |  | textbox | Sizing
checkpoint-status |  |  | checkpoint | Hangers & springs
checkpoint-status |  |  | checkpoint | Insulation blocks
checkpoint-status |  |  | checkpoint | Valves & tags
checkpoint-status |  |  | checkpoint | Provision for expansion
checkpoint-status |  |  | checkpoint | Anchors & Guides
checkpoint-status |  |  | checkpoint | Air Vents
checkpoint-status |  |  | checkpoint | Drain down
checkpoint-status |  |  | checkpoint | Pipe sleeves & fire seals
checkpoint-status |  |  | checkpoint | Service Access
checkpoint-status |  |  | checkpoint | Insulation & Sheathing
checkpoint-status |  |  | checkpoint | Installation clean & tidy
checklist-sectioned |  |  | checklist | Apartment Checklist |  |  |  |  | Yes | Apartment Checklist | 73a9f576-2314-43fb-8ebe-dd842e88100d
checkpoint-group |  |  | section | Hallway Fit-Off
checkpoint-status |  |  | checkpoint | Grille Fit-Off
checkpoint-group |  |  | section | Set Out
checkpoint-status |  |  | checkpoint | Area ready & accessible for work
checkpoint-status |  |  | checkpoint | Model: (Indoor/Outdoor) (Take a photo)
checkpoint-status |  |  | checkpoint | Serial No.: (Indoor/Outdoor) (Take a photo)
checkpoint-group |  |  | section | Installation
checkpoint-status |  |  | checkpoint | Secured
checkpoint-status |  |  | checkpoint | Vibration Pads
checkpoint-status |  |  | checkpoint | Filter
checkpoint-group |  |  | section | Electrical
checkpoint-status |  |  | checkpoint | Control Cable
checkpoint-status |  |  | checkpoint | Power
checkpoint-group |  |  | section | Refrigeration Lines
checkpoint-status |  |  | checkpoint | Connected in Unit
checkpoint-status |  |  | checkpoint | Connected Branch Box
checkpoint-status |  |  | checkpoint | Pressure Tested
checkpoint-status |  |  | checkpoint | Pipe Supported and Sealed
checkpoint-group |  |  | section | Drain Line
checkpoint-status |  |  | checkpoint | Correct Fall
checkpoint-status |  |  | checkpoint | Connected
checkpoint-status |  |  | checkpoint | Insulated and Sealed
checkpoint-status |  |  | checkpoint | Tested
checkpoint-status |  |  | checkpoint | Trapped
checklist-flat |  |  | checklist | Switchboard Installation |  |  |  |  | Yes | Switchboard Installation | 8e58f1a2-6bd6-40bf-ba95-28156f1ba0c3
checkpoint-status |  |  | checkpoint | Equipment installed in correct location
text | 1fb53b34-d791-5051-a71c-8eba6c013251 |  | textbox | SWBD designation
text | c5a6e827-f961-50cb-9036-652088ace470 |  | textbox | Drawing No.
text | c71dc402-530d-581e-b9cf-295b745d2c6a |  | textbox | Manufactured
text | 66966e92-d554-56ad-9258-cd0b3b399cd1 |  | textbox | Tested by
checkpoint-status |  |  | checkpoint | Test Equipment
text | 5c50f1f5-93d0-5d8b-b332-ca44798e8556 |  | textbox | Insulation Tester
text | c9814b97-a260-5de4-820e-1a5f8d5858c4 |  | textbox | RCD Tester
text | 7c1ef7db-9c14-5f55-b980-85b2e3f41d55 |  | textbox | Multimeter
checkpoint-status |  |  | checkpoint | Visually check panel is satisfactory, items such as correct coil voltages, all cables are terminated, transformers are terminated correctly, scratch washers on painted metal, earth straps on metal not fixed to main cubicle, protection against contact with live parts, condition of components (signs of damage), components secured properly, current carrying capacity of conductors and switchgear, check clearances – (phase to phase 20mm, phase to earth 20mm), check power wiring into three phase comb is correct.
checkpoint-status |  |  | checkpoint | Check all isolators and switches operate mechanically and electrically as per intended
checkpoint-status |  |  | checkpoint | Check continuity from earth link to all exposed metal is not more than 0.5Ω
text | 1427c615-c9ad-5c50-afba-6e97db3c7619 |  | textbox | Record Value
checkpoint-status |  |  | checkpoint | Insulation Resistance MAIN SWITCH AND DISTRIBUTION CHASSIS
label | e16e9bc5-9e1e-53c5-84ec-f038a7cea9d2 |  | note | Turn main switch ON and all circuit protection devices OFF. Select 500V scale on megger and test each phase to earth, each phase to neutral and phase to phase (A→B, A→C and B→C). Each test should result in readings not less than 1MΩ
text | 8f8800ec-100a-5ada-98c9-2a086dcbbd24 |  | textbox | A to B
text | 19beb2a0-ff6d-5ed4-8e9a-08b983b71e00 |  | textbox | A to C
text | c204cf77-f7b3-585a-92ff-cb8f1cee6b6e |  | textbox | B to C
text | 2df1dd93-9832-535a-abf2-b6fbb099dd4a |  | textbox | A to N
text | 60a4b5f5-e129-5138-8fa5-4cce8ba4798a |  | textbox | B to N
text | d88e86b8-185f-547c-885e-209c86683244 |  | textbox | C to N
text | 03d0b247-00f4-500f-8af8-4a32bce84fe6 |  | textbox | A to E
text | 865237c1-e87d-552c-8476-a856a2bd8227 |  | textbox | B to E
text | 4bd8d1c8-42f9-5dea-9f0f-37bbe6cb3a79 |  | textbox | C to E
text | ad4fbe21-891e-5c1e-9422-d4f16355eaee |  | textbox | N to E
checkpoint-status |  |  | checkpoint | Barricade area before live testing
text | 26cc2365-d09c-5d3b-9875-cf7f514228d6 |  | textbox | RCD Amps
text | c0503988-74cb-5b2e-bd28-1b2d098c980b |  | textbox | Milliamps
label | a1191704-33e5-5997-bc9b-701dd11adb30 |  | note | 0
text | 64bbf3fc-5fe5-5c99-90df-0f3442b3def4 |  | textbox | No Trip Test x 1/2 (No Trip
text | 0577efe8-9d8d-5a37-b59a-a9ceff228752 |  | textbox | Trip Test X 1 (1000 ms MAX)
text | f51d63e3-15ab-5d3a-b723-27c39a863cdc |  | textbox | Fast Trip Test x 5 (200ms MAX)
text | 7b68c774-194d-5d0e-9f8c-610a139a4584 |  | textbox | DC Test (1000 ms MAX)
text | ef5b870a-641e-5403-90dc-8a7a9c52f4d9 |  | textbox | Auto Ramp Test - 20% - 110% of rated trip current
text | e9f8777b-4eb6-5cf6-82ff-03002430582d |  | textbox | Auto Ramp Test - MAX 300 ms
label | 71430fbb-cf87-5119-b009-c755365d8ca9 |  | note | 180
text | 577561fd-92a5-5e49-a95f-4a22faff25da |  | textbox | No Trip Test x 1/2 (No Trip
text | fbdd57eb-f475-5644-aa83-cd6fe1997885 |  | textbox | Trip Test X 1 (1000 ms MAX)
text | 3997ca5e-7abd-5728-98bf-3536e3fdab32 |  | textbox | Fast Trip Test x 5 (200ms MAX)
text | f64be886-b13e-5bde-8360-088fe27c26cd |  | textbox | DC Test (1000 ms MAX)
text | 09ef328a-a2c8-5fea-9aed-c67cf5546498 |  | textbox | Auto Ramp Test - 20% - 110% of rated trip current
text | 06dce14c-8198-5c57-809b-10d70effe032 |  | textbox | Auto Ramp Test - MAX 300 ms
checkpoint-status |  |  | checkpoint | Ensure all power connections are tightened. Busbar connections and isolator connections to be witness marked where possible. Check circuit breaker sizes are correct and circuit breaker schedule is correct and installed in switchboard. Check contactor sizes and overload ratings and power wiring are correct.
label | 0748dadd-aee6-590b-ba4e-4e04c9fc8d16 |  | note | (3 phase – single phase, ensure single phase power wiring for overload is looped through each contact of overload).
checkpoint-status |  |  | checkpoint | Check circuit breaker sizes are correct as per drawings and circuit breaker schedule is correct and installed in switchboard.
checkpoint-status |  |  | checkpoint | Check overload and time delays are set correctly as per detailed on drawings.
checkpoint-status |  |  | checkpoint | Ensure all wires and terminals are numbered.
checkpoint-status |  |  | checkpoint | Ensure ALL labels are fitted and correct. Read each individual label and check it is consistent with the text on the drawings. CHECK RED WARNING STICKER is attached to appropriate sections of the switchboard.
checkpoint-status |  |  | checkpoint | Check that door seals and locks function correctly and keys are supplied in an accessible place.
checkpoint-status |  |  | checkpoint | Ensure that a copy of time switch, timer and other appropriate instructions are placed in Switchboard
checkpoint-status |  |  | checkpoint | Ensure site controls and switch plates are secured within the switchboard if applicable.
checkpoint-status |  |  | checkpoint | Ensure wall mounting brackets are placed and securely within the switchboard if required.
checkpoint-status |  |  | checkpoint | Ensure entire switchboard is vacuumed and wiped clean and all temporary labelling has been removed.
checkpoint-status |  |  | checkpoint | Check and record any damage to paint work both, internal or external.
checkpoint-status |  |  | checkpoint | Ensure Switchboard photos have been taken that clearly identify the,
checkpoint-status |  |  | checkpoint | Switchboard Designation / External of the switchboard / Internal of the switchboard / Switchboard Fascia/s.
checklist-flat |  |  | checklist | Fire Damper Installation Checklist |  |  |  |  | Yes | Fire Damper Installation Checklist | 94fd831b-75ba-4dbb-a571-48a517ce3c06
checkpoint-status |  |  | checkpoint | Damper installed as per drawing
text | 585d9fad-5698-5b29-96a9-c64d54cf393d |  | textbox | Drawing rev
text | 6602e049-1260-5bd1-9d4f-ed8e72cc9359 |  | textbox | Area/Level/Zone.
text | a771ecd6-f66c-5bfe-9d58-fa9d35f8abe7 |  | textbox | System Reference.
text | cbfc26e5-0813-55ea-b705-795188f2597a |  | textbox | Fire damper manufacturer.
checkpoint-status |  |  | checkpoint | Opening in fire rated construction built correctly (Signed by builder).
select | 238d01ad-a23a-5016-a005-1b494211bc05 |  | dropdown | Fire damper mechanism type | Curtain, Motorised, Slab, Intumescent
text | b6a057c6-bdea-5ef1-beca-7916058a7ca8 |  | textbox | Fire damper test report number (Refer to fire damper QA manual).
checkpoint-status |  |  | checkpoint | Does the structure match that for which damper was tested
checkpoint-status |  |  | checkpoint | Energy Air fire damper installation drawing number (Refer to fire damper QA manual).
checkpoint-status |  |  | checkpoint | Is the damper & penetration construction as per Energy Air fire damper installation drawing / an opinion
label | c80b03ef-4fb4-56f2-b9b7-ab50728b98fa |  | note | Check damper orientation (i.e. Upside down or not).
checkpoint-status |  |  | checkpoint | Check damper air flow direction.
checkpoint-status |  |  | checkpoint | Is the damper casing wholly within wall structure
checkpoint-status |  |  | checkpoint | Is damper expansion material fitted between damper and penetration
checkpoint-status |  |  | checkpoint | Check for minimum clearance between damper & penetration is as per standard.
checkpoint-status |  |  | checkpoint | Check that the fusible link is fitted and has the correct temperature rating.
checkpoint-status |  |  | checkpoint | Check damper blades are fully open.
checkpoint-status |  |  | checkpoint | Check damper closure is not impeded (drop test).
checkpoint-status |  |  | checkpoint | Confirm an access panel in the duct is provided and allows access to reset damper.
checkpoint-status |  |  | checkpoint | If motorised, is the actuator fixed to the damper body
checkpoint-status |  |  | checkpoint | Confirm break away bolts / fixings have been used (plastic or aluminium).
checkpoint-status |  |  | checkpoint | Are retaining angles fitted
checkpoint-status |  |  | checkpoint | Is the damper labelled with information as required
checklist-sectioned |  |  | checklist | Lobby Checklist |  |  |  |  | Yes | Lobby Checklist | 9fe61534-cb94-42e4-9247-734877d8ed59
checkpoint-group |  |  | section | Set Out
checkpoint-status |  |  | checkpoint | Installed as per drawing
checkpoint-status |  |  | checkpoint | Branch Box No. (Take a photo)
text | f08d0062-b631-522f-8262-08f2e7172836 |  | textbox | Make
checkpoint-group |  |  | section | Installation
checkpoint-status |  |  | checkpoint | All branch boxes installed
checkpoint-status |  |  | checkpoint | Refnets installed
checkpoint-group |  |  | section | Electrical
checkpoint-status |  |  | checkpoint | Control Cable
checkpoint-status |  |  | checkpoint | Power
checkpoint-group |  |  | section | Lobby Relief
checkpoint-status |  |  | checkpoint | Mesh cut out
checkpoint-status |  |  | checkpoint | Duct installed
checkpoint-status |  |  | checkpoint | Damper installed
checkpoint-status |  |  | checkpoint | Actuator installed
checkpoint-status |  |  | checkpoint | Actuator wired and tested for free operation
checkpoint-group |  |  | section | Refrigeration Lines
checkpoint-status |  |  | checkpoint | Connected to branch boxes/ refnets
checkpoint-status |  |  | checkpoint | Tested
checkpoint-group |  |  | section | Fire Rating
checkpoint-status |  |  | checkpoint | Photographed
checkpoint-status |  |  | checkpoint | On register
checkpoint-status |  |  | checkpoint | Submitted
checkpoint-group |  |  | section | Stair Pressurization
checkpoint-status |  |  | checkpoint | Copper pipework installed
checkpoint-status |  |  | checkpoint | Pressure transducers fitted
checkpoint-status |  |  | checkpoint | VSD installed
checkpoint-status |  |  | checkpoint | Grilles fitted
checkpoint-status |  |  | checkpoint | All door hardware installed (by others)
checkpoint-status |  |  | checkpoint | All penetration sealed
checklist-sectioned |  |  | checklist | Split AC Units Installation Checklist |  |  |  |  | Yes | Split AC Units Installation Checklist | e72ecb99-6ec5-40d7-8cab-1ea3a1ce02ac
checkpoint-group |  |  | section | Set Out
checkpoint-status |  |  | checkpoint | Equipment installed in correct location
checkpoint-status |  |  | checkpoint | Drawing No.
text | ecb75450-27b8-5907-9731-ba28d3888f76 |  | textbox | System reference
checkpoint-status |  |  | checkpoint | External springs and mounts
checkpoint-group |  |  | section | Fan Coil Unit
checkpoint-status |  |  | checkpoint | Traps & drains, flow from trays
checkpoint-status |  |  | checkpoint | Coil fins not damaged
checkpoint-status |  |  | checkpoint | Supports, spring mounts
checkpoint-status |  |  | checkpoint | Clearance and access
checkpoint-group |  |  | section | Condenser
checkpoint-status |  |  | checkpoint | Installed to manufacturers instructions
checkpoint-status |  |  | checkpoint | Fan/Coil guards fitted correctly.
checkpoint-status |  |  | checkpoint | Access covers in place, sealed, pipes connected.
checkpoint-status |  |  | checkpoint | Coil fins not damaged
checkpoint-status |  |  | checkpoint | Coil installed correctly
checkpoint-status |  |  | checkpoint | Air intake/discharge clearances adequate
checkpoint-status |  |  | checkpoint | Cleaning access
checkpoint-group |  |  | section | Fan
checkpoint-status |  |  | checkpoint | Belts, pulleys, guards fitted
checkpoint-status |  |  | checkpoint | Fan direction of airflow
checkpoint-status |  |  | checkpoint | Internal supports & spring mounts
checkpoint-group |  |  | section | Refrigerant Pipework
checkpoint-status |  |  | checkpoint | Line size
checkpoint-status |  |  | checkpoint | Pressure Tested
checkpoint-status |  |  | checkpoint | Pipe Supported
checkpoint-status |  |  | checkpoint | Gauges, test points & drain points
checkpoint-status |  |  | checkpoint | Valves - direction of flow & size
checkpoint-status |  |  | checkpoint | By-pass valve - direction of flow & size
checkpoint-status |  |  | checkpoint | Clearance and access
checkpoint-status |  |  | checkpoint | Pipework Lagging
checkpoint-group |  |  | section | Electrical
checkpoint-status |  |  | checkpoint | Termination at equipment
checkpoint-status |  |  | checkpoint | Tested
checkpoint-status |  |  | checkpoint | Controls
checkpoint-status |  |  | checkpoint | Sensors, controllers, switches fitted to pipes
checkpoint-status |  |  | checkpoint | Wiring/tubing to devices
checkpoint-status |  |  | checkpoint | Termination at controllers & devices
checkpoint-status |  |  | checkpoint | Tested
checkpoint-group |  |  | section | Painting/Labelling
checkpoint-status |  |  | checkpoint | Pipework – Is touch up required
checkpoint-status |  |  | checkpoint | Unit labelled
checkpoint-status |  |  | checkpoint | Pipe labelled
checkpoint-status |  |  | checkpoint | Control valves tags
checkpoint-status |  |  | checkpoint | VSD labelled
checkpoint-status |  |  | checkpoint | Installation left clean & tidy.
checklist-flat |  |  | checklist | Ductwork Installation Checklist |  |  |  |  | Yes | Ductwork Installation Checklist | f053a43a-eedf-4e6d-9fda-49e99cf57f91
checkpoint-status |  |  | checkpoint | Installed as per drawing
text | 6c63e898-9b47-5a36-a837-e88a7126b161 |  | textbox | Drawing rev
text | 87d4a38a-aaa8-5297-adfd-f79f21f5562f |  | textbox | Area/Level/Zone.
text | d3aa3f99-1d8d-56fb-9fd3-ec8e45f896a0 |  | textbox | System Reference.
text | 9a8dbb68-9075-51de-9654-76581e2f4eac |  | textbox | Position
text | a90a1e7c-ece0-5774-8f20-f62d805e3669 |  | textbox | Height
text | f01aedee-30f0-5f4c-a560-3a263fc473bc |  | textbox | Spigots
text | 5fc4eeb4-7da8-528e-9a99-78afab451a83 |  | textbox | Joining (including clips)
text | a12c336c-8541-5601-9fec-fb61069830d8 |  | textbox | Stiffening
text | 97d91f7a-46e3-5983-88a4-96fa08ac5e18 |  | textbox | Sealing
checkpoint-status |  |  | checkpoint | Hangers (including booker rod cut back and cold gal edges)
checkpoint-status |  |  | checkpoint | Canvas connection and emerclad where required
checkpoint-status |  |  | checkpoint | Equipment connection and emerclad where required
checkpoint-status |  |  | checkpoint | VCD’s & MVCD’s open & marked.
checkpoint-status |  |  | checkpoint | Actuators Installed
checkpoint-status |  |  | checkpoint | Flexible duct(s)
checkpoint-status |  |  | checkpoint | Grille / Plenum Box Installation
checkpoint-status |  |  | checkpoint | External insulation
checkpoint-status |  |  | checkpoint | Kitchen exhaust duct graded towards hood
checkpoint-status |  |  | checkpoint | Kitchen exhaust duct installed with access panels (every 3 meters & change in direction) and drains
checkpoint-status |  |  | checkpoint | Exposed ductwork to weather, top of ductwork cross broken, joints & flex connections weather proofed (flashings), Roof cowls secured and weather proofed
checkpoint-status |  |  | checkpoint | Installation left clean & tidy & Labels removed