## 1145-C200-FUL-QAC-ITP-0001
|  |  | Inspection and Test Plan - Stripping Topsoil, Clearing and Grubbing | [7 empty] | Document # 1145-C200-FUL-QAC-ITP-0001
[11 empty] | Revision : 00 | 2021-09-10
Client: | MRPV |  | Construction Process: | Stripping Topsoil, Clearing and Grubbing |  | Prepared by: |  | Reviewed by : |  |  | Approved by :
Project: | Craigieburn Road Upgrade |  |  |  |  | Name: | Johan Lau & Karim Hussein | Name: | Babak Rudd |  | Name: | Steve Felsinger
Contract No: | 1145 |  | Specifications: | Contract Specification Sections 1200 and 3020 VicRoads Sections 201 (Jan 2016) and 204 (Dec 2015) |  | Site Engineer |  | Quality Manager |  |  | Project Manager/Area Manager
|  |  | Structure / Component: | Stripping Topsoil, Clearing and Grubbing
Date: | 2021-02-11 |  | Location: | CRG Project wide |  | Date : | 22/04/2021 | Date : | 23/08/2021 |  | Date : | 10/09/2021
Lot No: |  |  | Lot Details: | [5 empty] | Lot Size/ Quantity:
Item | Task/Activity Description |  | Inspection / Controls and Verification Detail |  |  |  |  | HP/ WP/ AP/ IP/ TP/ SCP | Responsibility | Checked by:
No. |  |  | Frequency | Acceptance Criteria | Reference Documents | Inspection / Test Method | Record of conformity |  | Project Engineer Site Engineer Superintendent Surveyor Foreman | Superintendent | Fulton Hogan | FH's Sub-contractor | Date
1 | Preliminary Works
1.1 | Induction |  | Prior to Commencing Work | All personnel on site have been inducted to the CRG site | PMP Inductions Register | Document review | Site induction signed | AP | Site Engineer / Site Foreman | N/A
1.2 | Safety measures are in place, SWMS undertaken |  | Prior to Commencing Work | As per Fulton Hogan Safety Strategy. All personnel on site to have signed onto relevant SWMS before commencing work. | Health and Safety Coordination Plan | Document Review | SWMS(s) signed | HP | Site Engineer, Site Foreman & Superintendent
1.3 | Check that current revision drawings are being used |  | Prior to Commencing Work | Refer to latest drawings and latest available revision used | IFC Project Drawings/ Drawing Register | Document review | Latest revision drawings | AP | Site Engineer / Site Foreman | N/A |  | N/A
1.4 | Confirm understanding of current EMP related to the work area and that all prescribed environmental controls are in place |  | Prior to Commencing Work | All environmental measures to be implemented as per current EMP and local authorities. Sediment control measures to be installed and protected vegetation to be clearly identified | EMP, induction register Project Spec. Cl.1200.03 | Document review & Site inspection | Site induction signed This ITP signed | IP | Site Engineer | N/A
1.5 | Ground Penetration Permit (GPP) issued |  | Prior to Commencing Work | Current GPP signed and specific for the area where works will be executed. | GPP | Document review & Site inspection | GPP no. | HP* | Site Engineer | N/A |  | N/A
1.6 | Traffic Management (When required) |  | Prior to Commencing Work | Approved TMP and MOA | TMP | Document review & Site inspection | Approved TMP & MOA | AP | Site Engineer | N/A |  | N/A
1.7 | Vegetation Removal Permit (if required) |  | Prior to Commencing | Prior to removing any vegetation or habitat, FH shall: (a) arrange an on-site inspection with the Superintendent relevant authorities to confirm and clearly identify and mark trees, vegetation or habitat to be removed, consistent with the Design Documents and any relevant permits. (b) fence and sign all sites nominated as No-Go Zones. (c) Preclearance inspection by an ecologist to be completed not less than 7 days prior to the proposed clearing activity | Project Specs. Cl.1200.15 | Document review & Site inspection | Approved Veg Removal permit received. | HP | Site Engineer & Superintendent
1.8 | Extent of Clearing and Grubbing |  | Prior to Commencing Work | Extent of Clearing and Grubbing shall be reviewed jointly by Superintendent and FH representative prior commencement of the Works | Project Spec. Cl.3020.07(a)(ii) | Site Inspection | Extent of Clearing and Grubbing reviewed by Superintendent | HP | Site Engineer & Superintendent |  |  | N/A
2 | Construction Works
2.1 | Identification of Cultural Heritage sites and areas of Cultural Significance |  | Prior to Excavation | Areas determined to be No-Go Zones are securely fenced and clearly identified by signage installed in the fencing. Immediately stop work and notify the Superintendent if any Cultural Heritage is discovered or identified during construction. Works may recommence with the cultural heritage approval or if works can resume without risk to the discovered Cultural Heritage. | Relevant EMP Project Spec. Cl.1200.17 VicRoads Spec. Cl.201.10 | Document review & Site inspection | Cultural Heitage approval (when required) Signed ITP | AP | Site Engineer | N/A |  | N/A
2.2 | Stockpiling |  | Prior to Excavation | Where soil is stockepiled on Site, such stockpiles shall be located, where possible, to provide a clearance of not less than 10 metres from waterways. If this clearance is not possible,additional protection shall be provided. An area for stockpiling of topsoil has been designated and marked according Work Procedure WP-0009 | Project Spec. Cl.1200.09 (b)(i)(4) | Document review & Site inspection | Signed ITP | IP | Site Engineer | N/A |  | N/A
2.3 | Stripping of topsoil |  | Prior and after commencement of any ground disturbing activities | Topsoil shall be stripped for the full width of the formation. Declared noxious weeds, pests and pathogens shall be treated and monitored before stripping of topsoil, and after spreading, to prevent and/or minimise the spread of weeds and other pathogens throughout the site. Stockpiles shall be maintained in a neat, well shaped state capable of shedding water. Topsoil shall be re spread as soon as practicable. Unless there is an excess of topsoil to be removed from site, Topsoil shall remain on site where possible | Relevant EMP Project Spec. Cl.1200.16 VicRoads Spec. Cl.204.05 | Site Inspection | Signed ITP | IP | Site Engineer | N/A |  | N/A
2.4 | Removal of abandoned services |  | Prior to commencing this work | Removal and disposal of abandoned services and obsolete underground drainage lines which interfere with the execution of works has been done. Verify service is not likely to contain a hazardous material (sewage, asbestos pipe) Decommissioned services to be disposed of in a suitable manner. Decommissioned pits have been broken back to 0.3 metres below subgrade level. | Project Spec. Cl.3020.07(a)(i) VicRoads Spec. Cl.201.05 GPP # IFC Drawings | Site Inspection | Signed ITP | HP* | Site Engineer | N/A |  | N/A
2.5 | Clearing of Trees and Vegetation |  | During clearing works | Clearing work shall not be undertake outside of the specified limits of work. Tree branches extending over the carriageway shall be trimmed by a suitably qualified arborist to provide a clearance of at least 6 m above the carriageway surface. Where whole branches are to be removed, the three cut method shall be used. | VicRoads Spec. Cl.201.04 Project Spec. Cl | Site Inspection | Signed ITP | HP* | Site Engineer | N/A |  | N/A
2.6 | Clearing Process |  | During clearing works | Tree Clearing shall be done in a 2 stages: 1. only non-habitat trees as identified by the the ecologist are to be removed 2. the removal of habitat trees must occur not less than 24 hours after the removal of non-habitat trees in the area | Project Spec Cl. 1200.15.5.a | Site Inspection | Signed ITP | HP* | Site Engineer | N/A
2.7 | Grubbing of vegetation |  | Prior to commencing excavation | In areas where excavation will be made, all vegetation, refuse and obstructions shall be totally grubbed or grubbed to a depth of not less than 0.3 m below the subgrade and batters, whichever is the lesser treatment. In areas to be covered by embankments, to a depth of not less than 0.3 m below the stripped surface or not less than 0.6 m below the finished surface of the subgrade, whichever is the lesser treatment. Holes resulting from grubbing shall be backfilled with material similar to the surrounding material and compacted to the same degree as the surrounding material | Project Spec. Cl.3020.07(a) VicRoads Spec. Cl.201.05 | Site Inspection | Signed ITP | IP | Site Engineer | N/A |  | N/A
3 | Completion
3.1 | Disposal of vegetation |  | At completion of works | Tree trunks and large branches shall be removed from the site. Small tree branches, shrubs and leaves, excluding noxious weeds, shall be disposed of by chipping and mulching to form mulch. | VicRoads Spec. Cl.201.07 | Site Inspection | Delivery docket | IP | Site Engineer | N/A |  | N/A
3.2 | Topsoil Placement |  | At completion of works | All disturbed and/or not paved areas shall be topsoiled according to Section 204 of VicRoads Standard for Roadworks and Bridge works, to the following minimum depths - Batter slopes > 2:1 = 50mm -tree and shrub plantation bed areas= 100mm - Verge, 50mm outer edge / 20mm when within 100mm of the edge of seal or asphalt surface treatment - All other areas - 75mm Topsoil should be levelled and spread, but not compacted, except for verge areas. | Project Spec. Cl.3020.07(k) VicRoads Specification Cl.204.17 | Site Inspection | Signed ITP | IP | Site Engineer | N/A |  | N/A
Final Inspection
The signature below verifies that this ITP has been completed in accordance with the FH’s Quality system Procedures and verifies lot compliance with specifications.
| Print Name: |  | Position: |  | Signature: |  |  |  |  | Date: / /
Legend
HP | Hold Point | Work shall not proceed past the HP until released by the Superintendent |  |  | IP | Inspection point |  | Formal Inspection to be done and recorded
HP* | FH Hold Point | Work shall not proceed past the HP* until released by FH |  |  | TP | Test Point |  | Product compliance test to be undertaken and recorded/reported
WP | Witness Point | An inspection which must be witnessed by the Superintendent |  |  | SCP | Survey conformance point |  | A qualified surveyor to check product/section/structure and report
AP | Approval Point | Written or verbal approval given by the Superintendent