## Project Structure
Folder Structure |  |  |  |  | Checklists
Site QA
| FD Photos | Level | Zone | FD #
B4
Zone 24
|  |  |  | FD-B4-16 | FD Installation Photos Checklist
FD-B4-17
FD-B4-18
FD-B4-19
Zone 25
FD-B4-09
Zone 34
FD-B4-32
FD-B4-33
FD-B4-35
FD-B4-37
FD-B4-38
FD-B4-39
FD-B4-40
Zone 45
FD-B4-48
FD-B4-49
FD-B4-51
FD-B4-52
FD-B4-53
B3
Zone 24
FD-B3-54
FD-B3-55
Zone 25
FD-B3-50
FD-B3-51
FD-B3-52
Zone 34
FD-B3-60
FD-B3-61
Zone 45
FD-B3-62
FD-B3-63
FD-B3-64
B2
Zone 24
FD-B2-06
FD-B2-08
FD-B2-09
FD-B2-10
Zone 25
FD-B2-01
Zone34
FD-B2-02
FD-B2-07
FD-B2-12
Zone 45
FD-B2-03
FD-B2-04
FD-B2-05
B1
Zone 24
MFSD-B1-09
MFSD-B1-10
MFSD-B1-17
MFSD-B1-18
MFSD-B1-19
FD-B1-15
FD-B1-16
FD-B1-36
FD-B1-36A
Zone 25
FD-B1-08
FD-B1-08A
Zone 34
MFSD-B1-35
MFSD-B1-37
MFSD-B1-38
MFSD-B1-39
MFSD-B1-40
MFSD-B1-57
MFSD-B1-58
MFSD-B1-61
MFSD-B1-62
MFSD-B1-63
FD-B1-41
FD-B1-41B
FD-B1-59
FD-B1-64
FD-B1-65
FD-B1-66
FD-B1-75
FD-B1-76
Zone 44
MFSD-B1-54
Zone 45
MFSD-B1-53
MFSD-B1-56
FD-B1-46
FD-B1-47
FD-B1-48
FD-B1-49
FD-B1-50
FD-B1-79
FD-B1-80
FD-B1-81
FD-B1-83
FD-B1-84
FD-B1-85
FD-B1-86
FD-B1-87
B0
Zone 34
MFSD-B0-06
Zone 45
MFSD-B0-02
MFSD-B0-03
MFSD-B0-04
MFSD-B0-09
MFSD-B0-10

## Checklists
type | name | values
checklist-flat | FD Installation Checklist
checkpoint | FD Dimensions
Drawing #
label | Min Penetration = (1.01W + 10mm) x (1.01H + 10mm)
label | Max Penetration = (W+F) x (H+F)
label | F= Side of the angle against Fire Wall (mm)
label | AS.1682.2:2015
text | FD Size (W X H):
text | Flange Size (F):
text | Minimum Peno Size (W X H):
text | Maximum Peno Size (W X H):
text | Current Peno Size (W x H)
checkpoint | FD fully open; blades free to close and latch
checkpoint | FD orientation and air flow direction is correct
checkpoint | FD wholly within wall/ Slab; case is square
checkpoint | FD and Duct attached correctly/ Breakaway
checkpoint | Packing/expansion metal installed around casing
checkpoint | Opening in fire rated structure is correct
checkpoint | FD Flanges attached correctly
checkpoint | FD # corresponds to the one detailed on drawing
checkpoint | FD location corresponds to the one detailed on drawing
checkpoint | FD accessible for maintenance and service purposes
checkpoint | FD Installer Label complete
checkpoint | Fusible Link Fitted
checkpoint | Floor Mounted-2000 mm of Duct insulated above FD
checkpoint | Installation is approved
checkpoint | Corrective actions have been undertaken
checklist-flat | FD Installation Photos Checklist
checkpoint | Penetration Width
checkpoint | Penetration Height
checkpoint | Left and/or Rigth Gap
checkpoint | Top and/or Bottom Gap
checkpoint | FD c/w Retention Angles
checkpoint | FD Open
checkpoint | FD Close
checkpoint | FD Break Away Joint
checkpoint | FD with AP
checkpoint | Gaps Around FD Sealed
checkpoint | Sticker