## Table 1
| WORK AREA: |  |  | DESCRIPTION OF ACTIVITY: DN710, DN630 and DN450 PE Pipe and Welding |  | Key: P= PERFORM (Activity) R = REVIEW (Documents & Work) W = WITNESS (Activity) H = HOLD (Point for Acceptance)
[8 empty] | 1 | GvdLinde |  | 2024-06-19
| Kioreroa Road Sewer Rising Main | [6 empty] | 0 | GvdLinde |  | 2024-05-10
[8 empty] | Rev | Originator |  | Date |  |  | Approved |  |  | Date
Item No. |  | ITEM | ACTIVITY TASK |  | ACCEPTANCE CRITERIA |  | CERTIFING DOCUMENTATION AND FREQUENCY |  | Supervisor, Foreman or Subcontractor |  |  | Project Manager or Delegated Person |  |  | Engineer’s Representative
[9 empty] | Key | Sign / Date |  | Key | Sign / Date |  | Key | Sign / Date
1 |  | PE Pipe Jointing | Welding – Butt and EF Joints |  | As per T-WES 04110 – Fusion jointing of PE Pipes Specifications |  | Submit WMS as per T-WES 04110 Section 2.4 and 2.5 |  | P |  |  | R |  |  | H
2 |  | DN710 pipe material | Supply of Resin QA data |  | Certification from manufacturer that materials comply with the manufacturer’s specification as per project specs as per T-WES 00013 – Pressure Pipelines Supply, Installation and Testing Specification Section 2.4 |  | QA Documents As per Section 2.4.2.3 – submit prior to procurement. |  |  |  |  | P |  |  | H
3 |  | DN710 Pipe Welding | Construction |  | All weld parameters are to be recorded for each separate weld as well as the welder, weld number, location, date and time of weld and air temperature All butt welds to be undertaken in accordance with the manufacturer’s recommendations. Welder to have qualification certificates. As per T-WES 04110 – Fusion Jointing of PE Pipes |  | EF Weld Inspection joints Approved WMS Welding machine certified and calibrated with data logging capacity – submit calibration certs prior to start. Welder to supply Data Logger Information etc for butt-welding. Supply info as per Section 2.2 and 2.3- Welder qualifications and info. Maintain site records as per Section 3 |  | P |  |  | R |  |  | R
4 |  | DN710 -Testing of butt Welds | Butt Welding Test |  | Tests to be carried out to see Ductile or Tensile Failure as per WDCEES specifications. T-WES 04110 Section 3. |  | Test Results Butt Welding information to be provided with test weld, copy of information to be kept on site in QA folder, Results / Feedback to be supplied to WDC. Frequency as per T-WES 04110 - Section 3.1.4 Perform pre-construction test as per Section 3.1.1 Test 2 welds from first 50 welds as per Section 3.1.4 Maintain site records as per Section 3 |  | P |  |  | P |  |  | R
5 |  | DN710 - Testing of EF Welds | Joining of Strings |  | Tests to be carried out to see Ductile or Tensile Failure as per WDCEES specifications. T-WES 04110 Section 3.2 |  | Test Results EF Welding information to be provided with test weld, copy of information to be kept on site in QA folder, Results / Feedback to be supplied to WDC. Frequency as per T-WES 04110 - Section 3.1.4 |  | P |  |  | P |  |  | R
6 |  | DN630 - Pipe material | Supply of Resin QA data |  | Certification from manufacturer that materials comply with the manufacturer’s specification as per project specs. As per T-WES 00013 – Pressure Pipelines Supply, Installation and Testing Specification Section 2.4 |  | QA Documents As per section 2.4.2.3 – submit prior to procurement. |  |  |  |  | P |  |  | R
7 |  | DN630 Pipe Welding | Construction |  | All weld parameters are to be recorded for each separate weld as well as the welder, weld number, location, date and time of weld and air temperature All butt welds to be undertaken in accordance with the manufacturer’s recommendations. Welder to have qualification certificates As per T-WES 04110 – Fusion Jointing of PE Pipes |  | EF Weld Inspection joints Approved WMS Welding machine certified and calibrated with data logging capacity – submit calibration certs prior to start. Welder to supply Data Logger Information etc for butt-welding. Supply info as per Section 2.2 and 2.3- Welder qualifications and info. Maintain site records as per Section 3 |  | P |  |  | P |  |  | R
8 |  | DN630 - Testing of butt Welds | Butt Welding Test |  | Tests to be carried out to see Ductile or Tensile Failure as per WDCEES specifications. T-WES 04110 Section 3 |  | Test Results Butt Welding information to be provided with test weld, copy of information to be kept on site in QA folder, Results / Feedback to be supplied to WDC. Frequency as per T-WES 04110 - Section 3.1.4 Perform pre-construction test as per Section 3.1.1 Test 2 welds from first 50 welds as per Section 3.1.4 |  | P |  |  | P |  |  | R
9 |  | DN630 - Testing of EF Welds | Joining of Strings |  | Tests to be carried out to see Ductile or Tensile Failure as per WDCEES specifications. T-WES 04110 Section 3.2 |  | Test Results EF Welding information to be provided with test weld, copy of information to be kept on site in QA folder, Results / Feedback to be supplied to WDC. Frequency as per T-WES 04110 - Section 3.1.4 |  | P |  |  | P |  |  | R
10 |  | DN450 - Pipe material | Supply of Resin QA data |  | Certification from manufacturer that materials comply with the manufacturer’s specification as per project specs. As per T-WES 00013 – Pressure Pipelines Supply, Installation and Testing Specification Section 2.4 |  | QA Documents As per section 2.4.2.3 – submit prior to procurement. |  |  |  |  | P |  |  | R
11 |  | DN450 Pipe Welding | Construction |  | All weld parameters are to be recorded for each separate weld as well as the welder, weld number, location, date and time of weld and air temperature All butt welds to be undertaken in accordance with the manufacturer’s recommendations. Welder to have qualification certificates As per T-WES 04110 – Fusion Jointing of PE Pipes |  | EF Weld Inspection joints Approved WMS Welding machine certified and calibrated with data logging capacity – submit calibration certs prior to start. Welder to supply Data Logger Information etc for butt-welding. Supply info as per Section 2.2 and 2.3- Welder qualifications and info. Maintain site records as per Section 3 |  | P |  |  | P |  |  | R
12 |  | DN450 - Testing of butt Welds | Butt Welding Test |  | Tests to be carried out to see Ductile or Tensile Failure as per WDCEES specifications. T-WES 04110 Section 3 |  | Test Results Butt Welding information to be provided with test weld, copy of information to be kept on site in QA folder, Results / Feedback to be supplied to WDC. Frequency as per T-WES 04110 - Section 3.1.4 Perform pre-construction test as per Section 3.1.1 Test 2 welds from first 50 welds as per Section 3.1.4 |  | P |  |  | P |  |  | R
13 |  | DN450 - Testing of EF Welds | Joining of Strings |  | Tests to be carried out to see Ductile or Tensile Failure as per WDCEES specifications. T-WES 04110 Section 3.2 |  | Test Results EF Welding information to be provided with test weld, copy of information to be kept on site in QA folder, Results / Feedback to be supplied to WDC. Frequency as per T-WES 04110 - Section 3.1.4 |  | P |  |  | P |  |  | R
1
INSPECTION & TEST PLAN
INSPECTION & TEST PLAN (ITP) The ITP defines the required inspections during various stages of fabrication, construction & installation work. It is also a method of communicating these requirements to those doing the work & a verifying record that they have been carried out.
The ITP defines four different levels of inspection according to the following criteria:  Perform (P) The person(s) performing the work inspects his/her own work and the Foreman/Supervisor or Subcontractors Representative is to verify/check the work as correct. The Foreman/Supervisor or Subcontractors Representative is required to sign the Inspection & Test Checklist.  Review (R) – Documents When applied to documents this can indicate review & approval before fabrication commences e.g. weld procedures or after completion e.g. QC Package.  Review (R) –Work Performed Fabrication may proceed past the points indicated on the ITP. This type of inspection performed on a random basis. If corrective action is necessary, the frequency of inspections may be increased.  Witness (W) This type of inspection is performed when critical activities are undertaken & verification of work done is required by a third party, or internally by a supervisor or QA Personnel. It is the responsibility of the Foreman/Supervisor or Subcontractors Representative to notify whoever is identified as the Witness initiator that the (W) stage of inspection has been reached.  Hold (H) This type of inspection requires the Foreman/ Supervisor or Subcontractors Representative to notify the United Civil Project Manager that the (H) stage of inspection has been reached. Fabrication shall not proceed past this point unless the inspection has been carried out or approval to proceed is given in writing & signed by the Engineer’s Representative.
NOTE REGARDING INSPECTION AUTHORITIES NOT SIGNING OFF WITNESS OR HOLD POINTS
On occasion there are situations where the required Inspection Authority (normally the Engineer or Contractor’s Representative) at the witness or hold points has not for whatever reason signed the required documentation such ITP or Check Sheet where the given verifications points are clearly and evidently completed to the required standard. The Inspection Authority normally signifies verification by other means such as email sign off or other formal correspondence. Where this occurs, in lieu of a signature, a note to this effect shall be made on the relevant document by the Project Manager and reference to the said correspondence. The correspondence shall be kept on the company file for the project concerned.