## Insitu Concrete
|  |  |  | Process & Control Plan |  | MWTP-QA-6006 | Approved |  | Signature
|  |  |  | Contract Name: | Luggate Water Upgrade |  | FH Engineer
|  |  |  | Procedure: | Zone 1 foundations |  | FH Quality Manager
Inspection & Test Plan / Checklist
Lot No: |  |  |  | Corresponding Work Instruction: |  |  |  | Compliance with Work Instructions and Specifications
Detailed Location: 116 Church Road
Revision: 1
No: | Inspection / Test Point | ACTION (Hold, Monitor, Witness) | Detail | Frequency | Inspection / Test Method submission, visual inspection, testing, measure, review | Conformance Criteria | Records | FH Initials | Design Engineer Initials (Grey if not required) | Date(s)
1 | Design | H | IFC Drawings | Prior to commencement | Document Review | Ensure that Design is approved and Drawings are of the latest revision | Check Drawing Register | Site Engineer
2 | Set Out Survey | H | Arrange for a survey of extents to be carried out | Prior to Commencement | Survey | As per construction drawings. | Survey receipt | Site Engineer
3 | Material Supply (1) | H | Steel supply | Ongoing | Inspection/Review | Detailed and Delivered in accordance with drawings. Check delivery dockets when steel is delivered to site ensure that the correct materials have been delivered. On delivery to the site, steel reinforcement shall be stored on supports clear of the ground. | Delivery Dockets | Site Engineer
3 | Material Supply (2) | H | Steel strength | During construction | Inspection/Review | D & R reinforcing shall be grade 300 E bars, HD & HR Reinforcing shall be grade 500 E bars unless otherwise shown. Wire mesh shall be in accordance with AS/NZS 4671, to a minimum grade of 500 MPa. | Delivery Dockets | Site Engineer
3 | Material Supply (3) | H | Concrete mix | Once | Review | Concrete mix & compessive strength | Concrete docket | Site Engineer
4 | Subgrade | W | Confirm subgrade has adequate bearing capacity under foundtions | Once | Geotechnical Engineer Inspection & testing | Geotechnical Engineer visual inspection of subgrade. SPT to be undertaken on subgrade along footings. Test results shall be >150 kPa bearing capacity unless otherwise approved by the design engineer. | Inspection & test results | Site Engineer | Geotechnical Engineer
5 | Fill (1) | H | Fill material compliance | Throughout construction | The contractor is to confirm the material with Design Engineer | 150 mm minimum of AP40 hardfill. | Lab test report | Site Engineer
5 | Fill (2) | H | Fill placement | Once per foundation | NDM Testing | Each layer of fill shall be uniformly compacted in layers not exceeding 225mm prior to compaction. Each layer shall be compacted to 95% MDD as determined by NZS 4402. | Test results | Site Engineer | Geotechnical Engineer
6 | Sand | H | Site concrete placement under footings & floor slab | Prior to foundation construction | Visual Inspection | — | Photos | Site Engineer
7 | Formwork | H | Formwork installation on site for all structural concrete pours | Per pour | Inspection | Formwork installation shall be done in accordance with NZS3109:1997 Concrete Construction and the Project Specification. The grade of finish required will be constructed in accordance with project specification. | Photographs & Pre-pour inspections | Site Engineer
8 | Steel Reinforcing | H | Fabrication and placement of Reinforcing Steel for reinforced concrete works | During construction | Visual Inspection | Reinforcing shall be bent and placed in accordance with NZS 3109, NZS 3101, NZS 4671 and the Project Specification. Reinforcement shall be adequately tied and supported to maintain correct position and cover. Covers to reinforcement shall be as shown on structural drawings and as per NZS 3101. | Photographs & Pre-pour inspections | Site Engineer
9 | Notice of Pours | H | Engineer to check the form work, waterproofing and steel before the concrete is poured. | Per pour | Notice | Engineer shall be given a minimum of 24 hours notice in advance for inspections | Email | Site Engineer
10 | Pre Pour Inspection | W | Pre pour check sheets | Per pour | Inspection | Structural engineer inspection to confirm steel placement, construction joints, formwork, embedded items and surface finishes, in accordance with structural design. | Pre-pour inspection form | Site Engineer | Design Engineer/QLDC Representative
11 | As-builts | H | Final record of works undertaken/completed | During and at completion of work. | Survey / Drawings | Any works outside Construction tolerance and signed off on OFI or similar. As Built by Surveyor. Red pen mark up drawings to be included in QA file | Survey receipts, As-built plans | Site Engineer
QA Compiled By : |  |  | Maddie Irving |  | Signature: |  |  | Date:
QA checked By Quality Manager: |  |  | Kurt Beeton |  | Signature: |  |  | Date:
Accepted By Design Engineer: |  |  | Wanida Van Houtte |  | Signature: |  |  | Date: