## res
type | name | values | prefix | postfix | usage count | user addable | template name | Resource Id
checklist | MWTP-QA-6006 - PCP Foundation Pads | itp |  |  |  |  | MWTP-QA-6006 - PCP Foundation Pads Rev 1
section | PCP Foundation Pads
checkpoint | 1 - Design
label | ACTION (Hold, Monitor, Witness) - H
label | Detail - IFC Drawings
label | Frequency - Prior to commencement
label | Inspection / Test Method submission, visual inspection, testing, measure, review - Document Review
label | Conformance Criteria - Ensure that Design is approved and Drawings are of the latest revision
label | Records - Check Drawing Register
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 2 - Set Out Survey
label | ACTION (Hold, Monitor, Witness) - H
label | Detail - Arrange for a survey of extents to be carried out
label | Frequency - Prior to Commencement
label | Inspection / Test Method submission, visual inspection, testing, measure, review - Survey
label | Conformance Criteria - As per construction drawings.
label | Records - Survey receipt
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 3 - Material Supply (1)
label | ACTION (Hold, Monitor, Witness) - H
label | Detail - Steel supply
label | Frequency - Ongoing
label | Inspection / Test Method submission, visual inspection, testing, measure, review - Inspection/Review
label | Conformance Criteria - Detailed and Delivered in accordance with drawings. Check delivery dockets when steel is delivered to site ensure that the correct materials have been delivered. On delivery to the site, steel reinforcement shall be stored on supports clear of the ground.
label | Records - Delivery Dockets
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 3 - Material Supply (2)
label | ACTION (Hold, Monitor, Witness) - H
label | Detail - Steel strength
label | Frequency - During construction
label | Inspection / Test Method submission, visual inspection, testing, measure, review - Inspection/Review
label | Conformance Criteria - D & R reinforcing shall be grade 300 E bars, HD & HR Reinforcing shall be grade 500 E bars unless otherwise shown. Wire mesh shall be in accordance with AS/NZS 4671, to a minimum grade of 500 MPa.
label | Records - Delivery Dockets
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 3 - Material Supply (3)
label | ACTION (Hold, Monitor, Witness) - H
label | Detail - Concrete mix
label | Frequency - Once
label | Inspection / Test Method submission, visual inspection, testing, measure, review - Review
label | Conformance Criteria - Concrete mix & compessive strength
label | Records - Concrete docket
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 4 - Subgrade
label | ACTION (Hold, Monitor, Witness) - W
label | Detail - Confirm subgrade has adequate bearing capacity under foundtions
label | Frequency - Once
label | Inspection / Test Method submission, visual inspection, testing, measure, review - Geotechnical Engineer Inspection & testing
label | Conformance Criteria - Geotechnical Engineer visual inspection of subgrade.
label | ○ SPT to be undertaken on subgrade along footings. Test results shall be >150 kPa bearing capacity unless otherwise approved by the design engineer.
label | Records - Inspection & test results
checkpoint | 5 - Fill (1)
label | ACTION (Hold, Monitor, Witness) - H
label | Detail - Fill material compliance
label | Frequency - Throughout construction
label | Inspection / Test Method submission, visual inspection, testing, measure, review - The contractor is to confirm the material with Design Engineer
label | Conformance Criteria - 150 mm minimum of AP40 hardfill.
label | Records - Lab test report
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 5 - Fill (2)
label | ACTION (Hold, Monitor, Witness) - H
label | Detail - Fill placement
label | Frequency - Once per foundation
label | Inspection / Test Method submission, visual inspection, testing, measure, review - NDM Testing
label | Conformance Criteria - Each layer of fill shall be uniformly compacted in layers not exceeding 225mm prior to compaction. Each layer shall be compacted to 95% MDD as determined by NZS 4402.
label | Records - Test results
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 6 - Sand
label | ACTION (Hold, Monitor, Witness) - H
label | Detail - Site concrete placement under footings & floor slab
label | Frequency - Prior to foundation construction
label | Inspection / Test Method submission, visual inspection, testing, measure, review - Visual Inspection
label | Records - Photos
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 7 - Formwork
label | ACTION (Hold, Monitor, Witness) - H
label | Detail - Formwork installation on site for all structural concrete pours
label | Frequency - Per pour
label | Inspection / Test Method submission, visual inspection, testing, measure, review - Inspection
label | Conformance Criteria - Formwork installation shall be done in accordance with NZS3109:1997 Concrete Construction and the Project Specification. The grade of finish required will be constructed in accordance with project specification.
label | Records - Photographs & Pre-pour inspections
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 8 - Steel Reinforcing
label | ACTION (Hold, Monitor, Witness) - H
label | Detail - Fabrication and placement of Reinforcing Steel for reinforced concrete works
label | Frequency - During construction
label | Inspection / Test Method submission, visual inspection, testing, measure, review - Visual Inspection
label | Conformance Criteria - Reinforcing shall be bent and placed in accordance with NZS 3109, NZS 3101, NZS 4671 and the Project Specification. Reinforcement shall be adequately tied and supported to maintain correct position and cover. Covers to reinforcement shall be as shown on structural drawings and as per NZS 3101.
label | Records - Photographs & Pre-pour inspections
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 9 - Notice of Pours
label | ACTION (Hold, Monitor, Witness) - H
label | Detail - Engineer to check the form work, waterproofing and steel before the concrete is poured.
label | Frequency - Per pour
label | Inspection / Test Method submission, visual inspection, testing, measure, review - Notice
label | Conformance Criteria - Engineer shall be given a minimum of 24 hours notice in advance for inspections
label | Records - Email
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 10 - Pre Pour Inspection
label | ACTION (Hold, Monitor, Witness) - W
label | Detail - Pre pour check sheets
label | Frequency - Per pour
label | Inspection / Test Method submission, visual inspection, testing, measure, review - Inspection
label | Conformance Criteria - Structural engineer inspection to confirm steel placement, construction joints, formwork, embedded items and surface finishes, in accordance with structural design.
label | Records - Pre-pour inspection form
checkpoint | 11 - As-builts
label | ACTION (Hold, Monitor, Witness) - H
label | Detail - Final record of works undertaken/completed
label | Frequency - During and at completion of work.
label | Inspection / Test Method submission, visual inspection, testing, measure, review - Survey / Drawings
label | Conformance Criteria - Any works outside Construction tolerance and signed off on OFI or similar. As Built by Surveyor. Red pen mark up drawings to be included in QA file
label | Records - Survey receipts, As-built plans
holdpoint | AUTHORITY HOLDPOINT
checkpoint | Final Inspection
label | QA Compiled By: Maddie Irving
label | QA checked By Quality Manager: Kurt Beeton
label | Accepted By Design Engineer: Wanida Van Houtte
signoff | Sign ITP